## TOC
SDG&E Post-Event Report Data
Public Safety Power Shutoff Post-Event Report: JANUARY 20 – JANUARY 24, 2025
FILE DESCRIPTION
This file includes all tables and appendices that exceed five (5) rows from the Post Event Report submitted following the De-energization Event.
TABLE OF CONTENTS
SECTION 2: Decision Making Process
Table 2: Factors Considered in the Decision to Shut Off Power
SECTION 3: De-energized Time, Place, Duration and Customers
Table 3: Circuits De-energized
SECTION 4: Damage and Hazards to Overhead Facilities
Table 4: Damages and Hazards
SECTION 5: Notifications
Table 5: Positive Notification
Table 6: Notification Failure
SECTION 6: Local and State Public Safety Partner Engagement
Table 7: Public Safety Partners Contacted
Table 8: Services Provides to Customers with AFN
Table 9: Backup Power – Description, Capacity and Estimated Maximum Duration
Table 10: Community Generator Program Sites
Table 11: Total Number of Backup Generators and Mobile Batteries
Table 12: Critical Facility and Infrastructure Customers
Table 13: Community Generator Program Sites
SECTION 7: Complaints and Claims
Table 14: Number and Nature of Complaints Received
Table 15: Claims Filed Against SDG&E Due to De-energization
SECTION 8: Power Restoration
Table 16: Circuits requiring more than 24 hours to restore
SECTION 9: Community Resource Centers
Table 17: Community Resource Centers
SECTION 10: Mitigations to Reduce Impact
Table 18: Summary of Avoided Customer Impacts
Table 19: Summary of Avoided Customer Impacts by Circuit
Table 20: Summary of Customers Served by Microgrids
SECTION 11: Lessons Learned from this Event
Table 21: Lessons Learned from PSPS Event
APPENDIX
Appendix 1 – Customer Notifications: Descriptions, Dates, Times, and Scripts of Notifications
Appendix 2 – Public Safety Partner Notifications: Descriptions, Dates, Times, and Copies of Notifications
Appendix 3 – CPUC Notifications: Descriptions, Dates, Times, and Copies of Notifications
Appendix 4 – AFN Community Based Organization (CBO) Notifications: Descriptions, Dates, Times, and Copies of Notifications

## Table 2
Public Safety Power Shutoff Post-Event Report: JANUARY 20 – JANUARY 24, 2025
Appendix 5: PSPS Event Data Workbook
Table 2: Factors Considered in the Decision to Shut Off Power
# | Circuit/Device Name | Sustained Wind Speeds (mph) | Gust Wind Speeds (mph) | Peak Gust Speed (mph) | Temperature (°F) | Humidity (%) | Moisture | Fire Potential Index1 (FPI) | Temp Config2 (Y/N) | Vegetation Risk Index3 (VRI) | Circuit Risk Index3 (CRI) | Alert Speed4 (mph) | WiNGS Ops5 (mph) | Wildfire Consequence Score | PSPS Consequence Score | Wildfire/ PSPS Ratio6 | Ok to De-energize Date/Time
1 | 79-799R | 37 | 52 | 102 | 49 | 25% | 15% | 15 | N | Low | Low | 45 | 55.4813 | 0.045316 | 0.00018656 | 242.9021 | 2025-01-20 07:59
2 | 445-1325F | 30 | 40 | 77 | 45 | 31% | 10% | 15 | Y | Low | Low | 35 | 43.3246 | 0.024044 | 0.00054616 | 44.0239 | 2025-01-20 08:38
3 | 445-897R | 30 | 40 | 77 | 45 | 31% | 10% | 15 | Y | Low | Low | 35 | 35.4737 | 0.50148 | 0.0031283 | 160.3026 | 2025-01-20 08:38
4 | 212-1177R | 22 | 38 | 45 | 53 | 19% | 9% | 15 | N | Low | Medium | 36 | --- | --- | --- | --- | 2025-01-20 12:18
5 | CW-12.47KV-1215 | 27 | 44 | 77 | 46 | 24% | 7% | 15 | N | Low | Low | 45 | 36.7561 | 1.1973 | 0.0014747 | 811.8746 | 2025-01-20 13:50
6 | 79-685R | 23 | 47 | 73 | 39 | 22% | 8% | 15 | N | Low | Low | 45 | 47.3417 | 0.01215 | 6.4663e-05 | 187.903 | 2025-01-20 17:45
7 | 442-16R | 16 | 42 | 49 | 41 | 12% | 7% | 15 | N | Medium | Low | 41 | 34.1465 | 0.0092498 | 0.00026433 | 34.9936 | 2025-01-20 18:04
8 | 449-683 | 32 | 45 | 62 | 46 | 22% | 7% | 15 | N | Low | High | 45 | 32.7721 | 0.45529 | 0.0051923 | 87.6843 | 2025-01-20 18:04
9 | 597-595 | 27 | 41 | 41 | 60 | 6% | 7% | 15 | N | Medium | High | 35 | 29.9722 | 0.025834 | 0.011564 | 2.2339 | 2025-01-20 18:04
10 | TM1-10R | 14 | 35 | 39 | 57 | 12% | 8% | 15 | N | Low | Low | 38 | 39.6628 | 0.0015504 | 0.00032685 | 4.7435 | 2025-01-20 18:04
11 | 1030-1823F | 16 | 33 | 40 | 55 | 12% | 8% | 15 | Y | Medium | Medium | 35 | 42.2652 | 0.0006572 | 0.0001689 | 3.8911 | 2025-01-20 18:14
12 | 217-835R | 18 | 42 | 47 | 60 | 11% | 8% | 16 | N | Low | Low | 45 | 21.6383 | 0.21474 | 0.0017441 | 123.1219 | 2025-01-20 18:43
13 | 79-679R | 18 | 31 | 67 | 45 | 18% | 8% | 16 | N | Medium | Low | 45 | 46.0759 | 0.037829 | 0.0015856 | 23.8586 | 2025-01-20 18:43
14 | 73-678R | 29 | 47 | 49 | 49 | 15% | 8% | 16 | Y | Medium | Low | 35 | 34.8073 | 0.076325 | 0.0031267 | 24.4106 | 2025-01-20 18:51
15 | 221-1230F | 35 | 49 | 79 | 44 | 18% | 8% | 16 | Y | Medium | Low | 35 | --- | --- | --- | --- | 2025-01-20 19:15
16 | STY-12KV-222 | 35 | 49 | 79 | 44 | 18% | 8% | 16 | Y | Medium | Low | 35 | 28.0434 | 2.6275 | 0.012403 | 211.8549 | 2025-01-20 19:16
17 | 442-728R | 15 | 38 | 56 | 44 | 19% | 7% | 16 | N | Medium | Low | 35 | 40.6597 | 0.082837 | 0.0074103 | 11.1787 | 2025-01-20 19:18
18 | BUE-12.47KV-444 | 31 | 45 | 59 | 42 | 23% | 5% | 16 | N | Low | Low | 45 | --- | --- | --- | --- | 2025-01-20 19:48
19 | BUE-12.47KV-445 | 31 | 45 | 59 | 42 | 23% | 5% | 16 | N | Low | Low | 42 | 31.6515 | 0.28227 | 0.0081881 | 34.4732 | 2025-01-20 19:49
20 | 441-23R | 36 | 46 | 71 | 40 | 27% | 7% | 16 | N | Low | Low | 45 | 29.0933 | 1.6509 | 0.0010889 | 1516.068 | 2025-01-20 19:49
21 | 79-658R | 24 | 45 | 55 | 41 | 20% | 7% | 16 | N | Low | Low | 39 | 32.8317 | 0.038917 | 0.0024507 | 15.8798 | 2025-01-20 19:49
22 | 211-312R | 29 | 40 | 48 | 41 | 20% | 5% | 16 | N | Low | Low | 35 | 38.3168 | 0.0041138 | 0.0013153 | 3.1277 | 2025-01-20 19:49
23 | 79-785 | 31 | 51 | 54 | 44 | 18% | 7% | 16 | N | Medium | Low | 45 | 31.958 | 0.038267 | 0.0055175 | 6.9355 | 2025-01-20 20:00
24 | GC-12.47KV-442 | 19 | 48 | 65 | 41 | 18% | 7% | 16 | N | Low | Low | 45 | 40.9512 | 0.091861 | 0.0098635 | 9.3132 | 2025-01-20 20:12
25 | VC-12KV-907 | 32 | 43 | 50 | 57 | 10% | 8% | 16 | N | Medium | Medium | 45 | --- | --- | --- | --- | 2025-01-20 20:15
26 | GC-12.47KV-441 | 22 | 49 | 78 | 46 | 15% | 7% | 16 | N | Low | Low | 45 | 27.7497 | 0.41732 | 0.0012755 | 327.1911 | 2025-01-20 20:30
27 | 73-1163 | 19 | 54 | 57 | 43 | 18% | 7% | 16 | Y | Medium | Low | 35 | 35.879 | 0.11416 | 0.006191 | 18.4395 | 2025-01-20 20:35
28 | 79-1215F | 19 | 54 | 57 | 43 | 18% | 7% | 16 | N | Medium | Low | 45 | 33.5785 | 0.023419 | 0.0077536 | 3.0203 | 2025-01-20 20:35
29 | DE-12KV-78 | 19 | 54 | 57 | 43 | 18% | 7% | 16 | N | Medium | Low | 45 | 44.459 | 0.032553 | 0.0010053 | 32.3808 | 2025-01-20 20:44
30 | RIN-12KV-215 | 23 | 50 | 50 | 57 | 9% | 8% | 16 | N | Low | Medium | 45 | 29.3024 | 0.010077 | 0.004314 | 2.3358 | 2025-01-20 20:44
31 | 220-298R | 23 | 43 | 59 | 44 | 15% | 8% | 16 | N | Medium | Low | 45 | 41.9354 | 0.049118 | 0.0015528 | 31.6317 | 2025-01-20 20:53
32 | 221-36 | 27 | 40 | 43 | 39 | 20% | 8% | 16 | N | High | Low | 35 | 27.5239 | 0.00057014 | 0.011877 | 0.048003 | 2025-01-20 21:05
33 | 448-744R | 24 | 46 | 60 | 45 | 13% | 8% | 16 | Y | Low | Low | 35 | 44.8057 | 0.014903 | 0.0028954 | 5.147 | 2025-01-20 21:07
34 | 448-714R | 24 | 46 | 60 | 45 | 13% | 8% | 16 | N | Low | Low | 45 | 48.7133 | 0.012985 | 0.0046476 | 2.7939 | 2025-01-20 21:07
35 | 448-735R | 24 | 46 | 60 | 45 | 13% | 8% | 16 | N | Low | Low | 50 | --- | --- | --- | --- | 2025-01-20 21:08
36 | 448-1196F | 24 | 46 | 60 | 45 | 13% | 8% | 16 | N | Low | Medium | 35 | 34.7377 | 0.30164 | 0.0089351 | 33.7589 | 2025-01-20 21:08
37 | STY-12KV-220 | 25 | 46 | 59 | 46 | 15% | 8% | 16 | N | Low | Low | 42 | 35.6145 | 0.063039 | 0.003106 | 20.2962 | 2025-01-20 21:10
38 | 448-47R | 30 | 45 | 59 | 47 | 11% | 8% | 16 | N | Low | Low | 50 | --- | --- | --- | --- | 2025-01-20 21:07
39 | 448-724R | 13 | 27 | 53 | 46 | 19% | 7% | 16 | N | Low | Low | 43 | --- | --- | --- | --- | 2025-01-20 21:16
40 | CN-12.47KV-449 | 12 | 27 | 41 | 44 | 13% | 7% | 16 | N | Medium | Medium | 42 | 32.7721 | 0.45529 | 0.0051923 | 87.6843 | 2025-01-20 21:17
41 | 220-294R | 39 | 50 | 68 | 40 | 14% | 8% | 16 | N | Low | Low | 45 | 38.6948 | 0.082739 | 0.0027895 | 29.6613 | 2025-01-20 21:31
42 | 176-1834R | 23 | 43 | 53 | 55 | 9% | 8% | 16 | N | Medium | Medium | 40 | 23.1148 | 0.13987 | 0.0098326 | 14.2253 | 2025-01-20 21:37
43 | WR-12KV-211 | 25 | 39 | 51 | 48 | 9% | 6% | 16 | N | Low | Medium | 45 | 31.8219 | 0.10014 | 0.0025433 | 39.3751 | 2025-01-20 22:35
44 | 212-638R | 29 | 44 | 50 | 47 | 11% | 6% | 16 | N | Medium | Low | 45 | 27.3701 | 0.064537 | 0.0010261 | 62.8972 | 2025-01-20 22:36
45 | 1090-639R | 31 | 49 | 59 | 41 | 12% | 5% | 16 | N | Low | Low | 45 | 44.882 | 0.035248 | 0.00024499 | 143.8714 | 2025-01-21 04:51
46 | 1030-989R | 35 | 44 | 63 | 50 | 6% | 8% | 16 | N | Low | Low | 40 | 29.2572 | 0.12426 | 0.0013849 | 89.7263 | 2025-01-21 07:48
47 | 176-1836R | 33 | 48 | 51 | 54 | 7% | 7% | 16 | N | Medium | Medium | 45 | 22.9253 | 0.016087 | 0.0114 | 1.4111 | 2025-01-21 07:56
48 | 450-50R | 31 | 45 | 50 | 59 | 5% | 8% | 16 | Y | Medium | Low | 35 | 40.1219 | 0.023284 | 0.0089727 | 2.5949 | 2025-01-21 09:15
49 | 454-48F | 31 | 45 | 50 | 59 | 5% | 8% | 16 | N | Medium | Low | 39 | 20.2417 | 0.084675 | 0.00018849 | 449.221 | 2025-01-21 09:15
50 | 454-1814 | 31 | 45 | 50 | 59 | 5% | 8% | 16 | N | Medium | Low | 45 | 45 | 3.8111e-05 | 1.5664e-05 | 2.433 | 2025-01-21 09:15
51 | 175-24R | 28 | 45 | 48 | 61 | 6% | 6% | 16 | N | Low | Medium | 45 | 19.2789 | 0.85792 | 0.010577 | 81.1096 | 2025-01-21 09:34
52 | WC-12KV-327 | 28 | 45 | 48 | 61 | 6% | 6% | 16 | N | Low | Low | 45 | 25.2576 | 0.007856 | 1.111e-05 | 707.1291 | 2025-01-21 09:34
53 | 358-682F | 29 | 45 | 61 | 69 | 7% | 5% | 15 | N | Low | Low | 45 | 40.6094 | 0.075642 | 0.001557 | 48.5821 | 2025-01-22 09:58
54 | 1458-519 | 25 | 38 | 59 | 60 | 7% | 4% | 15 | Y | Medium | Medium | 35 | 36.9457 | 0.16597 | 0.0041429 | 40.0606 | 2025-01-23 04:54
55 | 217-983R | 35 | 47 | 71 | 64 | 6% | 5% | 15 | N | Low | Low | 45 | 28.3514 | 0.28814 | 0.00063962 | 450.4807 | 2025-01-23 05:04
56 | 157-232R | 34 | 50 | 63 | 58 | 9% | 5% | 15 | N | Low | Low | 45 | 35.319 | 0.075863 | 0.0032403 | 23.4125 | 2025-01-23 05:11
57 | 237-1765R | 39 | 56 | 56 | 58 | 9% | 4% | 15 | N | Low | Low | 45 | 40.5462 | 0.011285 | 0.001138 | 9.9163 | 2025-01-23 05:54
58 | 1030-1777 | 24 | 42 | 55 | 67 | 6% | 6% | 15 | Y | Medium | Medium | 35 | 27.5366 | 0.32665 | 0.0073562 | 44.4043 | 2025-01-23 05:57
59 | 214-1122R | 31 | 52 | 62 | 62 | 5% | 6% | 15 | N | Medium | Low | 45 | 24.2264 | 0.7777 | 0.0033563 | 231.7115 | 2025-01-23 05:58
60 | OV-12KV-1250 | 36 | 41 | 57 | 65 | 7% | 6% | 15 | Y | Medium | Low | 35 | 25.3642 | 1.0445 | 0.014741 | 70.8535 | 2025-01-23 07:48
61 | LL-12KV-283 | 32 | 50 | 61 | 66 | 4% | 4% | 15 | N | Low | Medium | 45 | --- | --- | --- | --- | 2025-01-23 08:49
62 | LL-12KV-1166 | 32 | 50 | 61 | 66 | 4% | 4% | 15 | N | Low | Medium | 45 | 20.3211 | 0.0049283 | 0.0014116 | 3.4912 | 2025-01-23 08:49
63 | PA-12KV-1233 | 24 | 38 | 48 | 68 | 5% | 4% | 15 | N | Medium | Low | 36 | --- | --- | --- | --- | 2025-01-23 09:01
64 | RB1-433R | 17 | 51 | 51 | 69 | 4% | 4% | 15 | N | Medium | Low | 39 | 37.5578 | 0.0058003 | 0.00044192 | 13.1253 | 2025-01-23 09:40
65 | 521-14R | 30 | 48 | 48 | 69 | 4% | 4% | 15 | N | Medium | Medium | 43 | 31.25 | 0.036959 | 0.0021258 | 17.3858 | 2025-01-23 09:40
66 | 520-1527R | 30 | 48 | 48 | 69 | 4% | 4% | 15 | N | Medium | High | 35 | 20.7499 | 0.52236 | 0.0048138 | 108.513 | 2025-01-23 09:41
67 | 972-1582R | 32 | 44 | 48 | 67 | 5% | 4% | 15 | N | Medium | Medium | 38 | 38.2005 | 0.025068 | 0.0024356 | 10.2923 | 2025-01-23 09:45
68 | 971-1973R | 32 | 44 | 48 | 67 | 5% | 4% | 15 | Y | Medium | Medium | 35 | 38.6285 | 0.0048439 | 0.0017621 | 2.749 | 2025-01-23 09:45
69 | VC-12KV-909 | 24 | 55 | 55 | 68 | 6% | 5% | 15 | N | Medium | Medium | 35 | 25.9095 | 0.010816 | 0.0038152 | 2.8351 | 2025-01-23 09:57
70 | 175-64R | 31 | 39 | 48 | 67 | 5% | 4% | 15 | N | Medium | Medium | 40 | 36.2481 | 0.0098735 | 0.00099383 | 9.9348 | 2025-01-23 10:09
71 | 176-197F | 31 | 39 | 48 | 67 | 5% | 4% | 15 | N | Medium | Medium | 40 | 35.9915 | 0.023282 | 0.0043957 | 5.2965 | 2025-01-23 10:27
72 | ARR-12KV-1101 | 39 | 49 | 54 | 72 | 5% | 8% | 15 | Y | Low | Low | 35 | 19.1163 | 3.6647 | 0.0049938 | 733.846 | 2025-01-23 10:34
73 | 358-1193F | 34 | 47 | 59 | 63 | 6% | 4% | 15 | N | Medium | Low | 45 | 43.1172 | 0.0040394 | 0.0026098 | 1.5478 | 2025-01-23 10:53
74 | WR-12KV-210 | 41 | 52 | 53 | 54 | 12% | 3% | 15 | N | Low | Low | 35 | 34.0602 | 0.053209 | 0.0019192 | 27.7247 | 2025-01-23 11:53
75 | WR-12KV-212 | 41 | 52 | 53 | 54 | 12% | 3% | 15 | N | Low | Medium | 43 | 26.5379 | 0.15274 | 0.0059956 | 25.4757 | 2025-01-23 11:53
76 | 157-273R | 29 | 45 | 51 | 67 | 7% | 4% | 15 | Y | Medium | Medium | 35 | 23.7855 | 0.17478 | 0.0027753 | 62.9754 | 2025-01-23 13:03
77 | 214-613R | 28 | 44 | 44 | 44 | 8% | 1% | 15 | N | High | Low | 36 | 33.8781 | 0.02211 | 0.00080297 | 27.5356 | 2025-01-23 19:17
78 | 357-2049F | 25 | 46 | 47 | 60 | 5% | 4% | 15 | Y | Medium | Low | 35 | 40.792 | 0.0078003 | 0.0017749 | 4.3947 | 2025-01-23 19:39
79 | TL50003 | 55 | 67 | 83 | 51 | 11% | 4% | 15 | N | Low | High | 70 | NA | NA | NA | NA | 2025-01-23 07:32
80 | TL686 | 41 | 52 | 53 | 54 | 12% | 3% | 15 | Y | Medium | High | 45 | NA | NA | NA | NA | 2025-01-23 11:58
81 | TL6958 | 45 | 65 | 70 | 38 | 16% | 7% | 16 | N | Low | High | 55 | NA | NA | NA | NA | 2025-01-20 21:18
82 | TL6923 | 48 | 75 | 88 | 44 | 16% | 7% | 16 | N | Low | High | 65 | NA | NA | NA | NA | 2025-01-20 20:57
83 | TL625 | 15 | 36 | 48 | 42 | 14% | 7% | 16 | N | Low | High | 65 | NA | NA | NA | NA | 2025-01-20 20:53
Note: Missing values are indicated by '---'. SDG&E will integrate these Circuit Breakers into the WiNGS-Ops tool.
1 Fire Potential Index is described in Section 2.2
2 Temporary Construction and Compliance Poles (TCC) are assessed by Electrical Distribution and Transmission engineering teams before a PSPS activation. They evaluate compliance risks, considering factors like wire distances from objects and pole capacities, and may lower wind gust speed thresholds based on the severity of their findings. Legend (Y*) indicates the presence of one or more TCC poles downstream of the SCADA sectionalizing device, with no change in alert speed due to this TCC condition. Legend (Y**) signifies that the TCC pole(s) downstream of the SCADA sectionalizing device meet the criteria to lower wind gust thresholds.
3 VRI and CRI provide a relative assessment of vegetation as well as conductor risk for each segment. Methodologies reported in SDG&E's 2021 WMP, Section 4.5.1.
4 This Alert Speed is the recommended wind gust threshold for initiating de-energization during this specific PSPS activation.
5 WiNGS Ops provides an estimated wind gust threshold at which the expected wildfire risk exceeds the PSPS risk at each feeder segment. This output incorporates both an estimate of likelihood of the risk as well as consequence. Calculations described in Section 2.4
6 This ratio depicts the comparison between wildfire consequence score using historical weather events and PSPS consequence score (excludes likelihood of risk). A value greater than 1 means the wildfire risk exceeds the PSPS risk.

## Table 3
Public Safety Power Shutoff Post-Event Report: JANUARY 20 – JANUARY 24, 2025
Appendix 5: PSPS Event Data Workbook
Table 3: Circuits De-energized
Distribution/ Transmission | Circuit/ Device Name | County | De-energization Date and Time | Restoration Date/Time | Duration | All clear Date/Time | HFTD Tier | Total Customers | Residential Customers | Commercial/ Industrial Customers | MBL Customers | AFN other than MBL Customers1 | Other Customers
Distribution | LBE.23234 | San Diego | 2025-01-20 17:27 | 2025-01-20 19:29 | 0.084722 | 2025-01-20 19:28 | Tier-3 | 1 | 0 | 1 | 0 | 0 | N/A
Distribution | LBE.30429 | San Diego | 2025-01-20 17:27 | 2025-01-20 19:29 | 0.084722 | 2025-01-20 19:28 | Tier-3 | 1 | 0 | 1 | 0 | 0 | N/A
Distribution | 221-1251R | San Diego | 2025-01-20 21:37 | 2025-01-21 01:01 | 0.14167 | 2025-01-21 01:00 | Tier-3 | 116 | 99 | 17 | 4 | 31 | N/A
Distribution | 448-1204 | San Diego | 2025-01-20 21:44 | 2025-01-21 04:04 | 0.26389 | 2025-01-21 04:03 | Tier-3 | 18 | 0 | 18 | 0 | 0 | N/A
Distribution | F2251624 | San Diego | 2025-01-20 23:11 | 2025-01-21 08:30 | 0.38819 | 2025-01-21 06:38 | Tier-2 | 22 | 3 | 19 | 1 | 1 | N/A
Distribution | F2590037 | San Diego | 2025-01-21 10:45 | 2025-01-21 14:55 | 0.17361 | 2025-01-21 14:37 | Tier-3 | 5 | 4 | 1 | 0 | 0 | N/A
Distribution | 454-48F | San Diego | 2025-01-21 09:21 | 2025-01-21 15:21 | 0.25 | 2025-01-21 14:02 | Tier-2 | 17 | 9 | 8 | 1 | 1 | N/A
Distribution | 454-1814 | San Diego | 2025-01-21 09:23 | 2025-01-21 15:28 | 0.25347 | 2025-01-21 14:02 | Tier-2 | 2 | 2 | 0 | 0 | 0 | N/A
Distribution | 450-50R | San Diego | 2025-01-21 09:22 | 2025-01-21 15:44 | 0.26528 | 2025-01-21 14:02 | Non HFTD | 1111 | 1061 | 50 | 92 | 292 | N/A
Distribution | 217-983R | Riverside, San Diego | 2025-01-20 17:31 | 2025-01-21 16:05 | 0.94028 | 2025-01-21 14:04 | Tier-3 | 82 | 76 | 6 | 4 | 16 | N/A
Distribution | SCE-218 | Riverside, San Diego | 2025-01-21 09:45 | 2025-01-22 02:37 | 0.70278 | 2025-01-22 02:37 | Non HFTD | 1 | 0 | 1 | 0 | 0 | N/A
Distribution | 1090-639R | San Diego | 2025-01-21 04:54 | 2025-01-22 08:39 | 1899-12-31 03:45 | 2025-01-22 07:22 | Tier-2 | 16 | 0 | 16 | 0 | 0 | N/A
Distribution | 157-232R | San Diego | 2025-01-20 18:50 | 2025-01-22 09:16 | 1899-12-31 14:26 | 2025-01-22 07:20 | Tier-3 | 94 | 87 | 7 | 9 | 38 | N/A
Distribution | 157-189R | San Diego | 2025-01-20 18:50 | 2025-01-22 09:21 | 1899-12-31 14:31 | 2025-01-22 07:20 | Tier-3 | 248 | 177 | 71 | 4 | 101 | N/A
Distribution | VC-12KV-907 | San Diego | 2025-01-20 20:23 | 2025-01-22 09:21 | 1899-12-31 12:58 | 2025-01-22 07:20 | Tier-2 | 746 | 621 | 125 | 29 | 124 | N/A
Distribution | 907-1716R | San Diego | 2025-01-20 20:23 | 2025-01-22 09:26 | 1899-12-31 13:03 | 2025-01-22 07:20 | Tier-2 | 708 | 653 | 55 | 80 | 151 | N/A
Distribution | 907-2820R | San Diego | 2025-01-20 20:23 | 2025-01-22 09:46 | 1899-12-31 13:23 | 2025-01-22 07:20 | Tier-2 | 1 | 1 | 0 | 0 | 0 | N/A
Distribution | WC-12KV-327 | San Diego | 2025-01-21 10:08 | 2025-01-22 09:51 | 0.98819 | 2025-01-22 07:22 | Tier-3 | 4 | 0 | 4 | 0 | 0 | N/A
Distribution | 175-24R | San Diego | 2025-01-21 09:39 | 2025-01-22 09:56 | 1899-12-31 00:17 | 2025-01-22 07:36 | Tier-3 | 788 | 741 | 47 | 53 | 80 | N/A
Distribution | 175-94R | San Diego | 2025-01-21 09:39 | 2025-01-22 10:12 | 1899-12-31 00:33 | 2025-01-22 07:36 | Tier-3 | 176 | 136 | 40 | 4 | 6 | N/A
Distribution | 175-2024R | San Diego | 2025-01-21 09:39 | 2025-01-22 10:16 | 1899-12-31 00:37 | 2025-01-22 07:36 | Tier-3 | 30 | 8 | 22 | 0 | 0 | N/A
Distribution | 907-1702R | San Diego | 2025-01-20 20:23 | 2025-01-22 10:24 | 1899-12-31 14:01 | 2025-01-22 07:20 | Tier-2 | 73 | 66 | 7 | 7 | 21 | N/A
Distribution | 175-90R | San Diego | 2025-01-21 09:39 | 2025-01-22 10:28 | 1899-12-31 00:49 | 2025-01-22 07:36 | Tier-3 | 166 | 106 | 60 | 11 | 23 | N/A
Distribution | BUE-12.47KV-444 | San Diego | 2025-01-20 19:51 | 2025-01-22 10:28 | 1899-12-31 14:37 | 2025-01-22 08:44 | Tier-2 | 4 | 3 | 1 | 1 | 3 | N/A
Distribution | 444-43R | San Diego | 2025-01-20 19:51 | 2025-01-22 10:33 | 1899-12-31 14:42 | 2025-01-22 08:44 | Tier-2 | 123 | 93 | 30 | 11 | 36 | N/A
Distribution | 175-64R | San Diego | 2025-01-21 09:39 | 2025-01-22 10:42 | 1899-12-31 01:03 | 2025-01-22 07:36 | Tier-3 | 108 | 74 | 34 | 4 | 8 | N/A
Distribution | 176-1836R | San Diego | 2025-01-21 08:01 | 2025-01-22 10:46 | 1899-12-31 02:45 | 2025-01-22 07:20 | Tier-2 | 196 | 183 | 13 | 13 | 25 | N/A
Transmission | TL682 | San Diego | 2025-01-21 09:59 | 2025-01-22 10:51 | 1899-12-31 00:52 | 2025-01-22 07:19 | Tier-2/Tier-3 | 0 | 0 | 0 | 0 | 0 | N/A
Distribution | 1030-989R | San Diego | 2025-01-21 07:53 | 2025-01-22 11:08 | 1899-12-31 03:15 | 2025-01-22 07:21 | Tier-3 | 153 | 102 | 51 | 5 | 25 | N/A
Distribution | 176-1834R | San Diego | 2025-01-20 21:49 | 2025-01-22 11:11 | 1899-12-31 13:22 | 2025-01-22 07:20 | Tier-2 | 267 | 238 | 29 | 24 | 22 | N/A
Distribution | 176-194R | San Diego | 2025-01-20 21:49 | 2025-01-22 11:16 | 1899-12-31 13:27 | 2025-01-22 07:20 | Tier-2 | 99 | 72 | 27 | 7 | 12 | N/A
Distribution | 176-161R | San Diego | 2025-01-20 21:49 | 2025-01-22 11:20 | 1899-12-31 13:31 | 2025-01-22 07:20 | Tier-2 | 657 | 578 | 79 | 69 | 88 | N/A
Distribution | 1233-587R | San Diego | 2025-01-21 01:46 | 2025-01-22 11:23 | 1899-12-31 09:37 | 2025-01-22 07:20 | Tier-3 | 91 | 78 | 13 | 2 | 13 | N/A
Distribution | 176-164R | San Diego | 2025-01-20 21:49 | 2025-01-22 11:25 | 1899-12-31 13:36 | 2025-01-22 07:20 | Tier-2 | 69 | 43 | 26 | 5 | 5 | N/A
Transmission | TL50003 | San Diego | 2025-01-21 07:35 | 2025-01-22 11:30 | 1899-12-31 03:55 | 2025-01-22 07:19 | Tier-3 | 0 | 0 | 0 | 0 | 0 | N/A
Distribution | 176-1845R | San Diego | 2025-01-20 21:49 | 2025-01-22 11:38 | 1899-12-31 13:49 | 2025-01-22 07:20 | Tier-2 | 70 | 52 | 18 | 4 | 5 | N/A
Distribution | 221-1249R | San Diego | 2025-01-20 21:37 | 2025-01-22 11:43 | 1899-12-31 14:06 | 2025-01-22 07:22 | Tier-3 | 196 | 158 | 38 | 7 | 43 | N/A
Distribution | 221-37AE | San Diego | 2025-01-20 21:37 | 2025-01-22 11:43 | 1899-12-31 14:06 | 2025-01-22 07:22 | Tier-3 | 222 | 195 | 27 | 17 | 92 | N/A
Distribution | 1233-589R | San Diego | 2025-01-21 01:46 | 2025-01-22 11:45 | 1899-12-31 09:59 | 2025-01-22 07:20 | Tier-3 | 17 | 8 | 9 | 0 | 1 | N/A
Distribution | 221-344R | San Diego | 2025-01-20 21:37 | 2025-01-22 11:49 | 1899-12-31 14:12 | 2025-01-22 07:22 | Tier-3 | 99 | 77 | 22 | 0 | 14 | N/A
Distribution | 1233-585R | San Diego | 2025-01-21 01:46 | 2025-01-22 11:59 | 1899-12-31 10:13 | 2025-01-22 07:20 | Tier-3 | 80 | 69 | 11 | 2 | 17 | N/A
Distribution | 1233-591R | San Diego | 2025-01-21 01:46 | 2025-01-22 12:05 | 1899-12-31 10:19 | 2025-01-22 07:20 | Tier-3 | 76 | 63 | 13 | 4 | 6 | N/A
Distribution | 221-824 | San Diego | 2025-01-20 21:34 | 2025-01-22 12:09 | 1899-12-31 14:35 | 2025-01-22 07:22 | Tier-3 | 150 | 137 | 13 | 10 | 38 | N/A
Distribution | 221-23R | San Diego | 2025-01-20 21:37 | 2025-01-22 12:21 | 1899-12-31 14:44 | 2025-01-22 07:22 | Tier-3 | 267 | 249 | 18 | 19 | 77 | N/A
Distribution | 210-172R | San Diego | 2025-01-20 20:39 | 2025-01-22 12:28 | 1899-12-31 15:49 | 2025-01-22 07:21 | Tier-2 | 24 | 2 | 22 | 0 | 0 | N/A
Distribution | 210-9R | San Diego | 2025-01-20 20:39 | 2025-01-22 12:32 | 1899-12-31 15:53 | 2025-01-22 07:21 | Tier-2 | 85 | 84 | 1 | 7 | 16 | N/A
Distribution | 221-782R | San Diego | 2025-01-20 21:37 | 2025-01-22 12:38 | 1899-12-31 15:01 | 2025-01-22 07:22 | Tier-3 | 3 | 0 | 3 | 0 | 0 | N/A
Distribution | 221-6R | San Diego | 2025-01-20 21:37 | 2025-01-22 12:48 | 1899-12-31 15:11 | 2025-01-22 07:22 | Tier-3 | 1 | 0 | 1 | 0 | 0 | N/A
Distribution | 210-394R | San Diego | 2025-01-20 20:39 | 2025-01-22 12:50 | 1899-12-31 16:11 | 2025-01-22 07:21 | Tier-2 | 23 | 2 | 21 | 0 | 0 | N/A
Distribution | 221-675R | San Diego | 2025-01-20 21:37 | 2025-01-22 12:50 | 1899-12-31 15:13 | 2025-01-22 07:22 | Tier-3 | 7 | 5 | 2 | 0 | 2 | N/A
Distribution | 210-392R | San Diego | 2025-01-20 20:39 | 2025-01-22 12:55 | 1899-12-31 16:16 | 2025-01-22 07:21 | Tier-2 | 79 | 67 | 12 | 6 | 38 | N/A
Distribution | LBE.246 | San Diego | 2025-01-20 21:24 | 2025-01-22 13:02 | 1899-12-31 15:38 | 2025-01-22 07:22 | Tier-3 | 83 | 68 | 15 | 2 | 20 | N/A
Distribution | 212-734R | San Diego | 2025-01-20 23:11 | 2025-01-22 13:20 | 1899-12-31 14:09 | 2025-01-22 07:20 | Tier-2 | 23 | 0 | 23 | 0 | 0 | N/A
Distribution | 212-638R | San Diego | 2025-01-20 23:11 | 2025-01-22 13:22 | 1899-12-31 14:11 | 2025-01-22 07:20 | Tier-2 | 7 | 7 | 0 | 0 | 3 | N/A
Distribution | LBE.782 | San Diego | 2025-01-20 10:39 | 2025-01-22 13:29 | 1900-01-01 02:50 | 2025-01-22 07:20 | Tier-2 | 111 | 77 | 34 | 3 | 33 | N/A
Distribution | 212-743R | San Diego | 2025-01-20 23:11 | 2025-01-22 13:33 | 1899-12-31 14:22 | 2025-01-22 07:20 | Tier-2 | 10 | 8 | 2 | 0 | 1 | N/A
Distribution | 212-880R | San Diego | 2025-01-20 23:11 | 2025-01-22 13:38 | 1899-12-31 14:27 | 2025-01-22 07:20 | Tier-2 | 3 | 3 | 0 | 0 | 0 | N/A
Distribution | 214-1122R | San Diego | 2025-01-20 18:23 | 2025-01-22 13:39 | 1899-12-31 19:16 | 2025-01-22 12:00 | Tier-3 | 236 | 185 | 51 | 8 | 64 | N/A
Distribution | 212-739R | San Diego | 2025-01-20 23:11 | 2025-01-22 13:47 | 1899-12-31 14:36 | 2025-01-22 07:20 | Tier-2 | 46 | 31 | 15 | 2 | 9 | N/A
Distribution | 214-647R | San Diego | 2025-01-20 18:23 | 2025-01-22 13:48 | 1899-12-31 19:25 | 2025-01-22 12:00 | Tier-3 | 137 | 116 | 21 | 8 | 59 | N/A
Distribution | 212-758R | San Diego | 2025-01-20 10:39 | 2025-01-22 13:55 | 1900-01-01 03:16 | 2025-01-22 07:20 | Tier-2 | 54 | 37 | 17 | 0 | 15 | N/A
Distribution | 212-1204R | San Diego | 2025-01-20 10:39 | 2025-01-22 13:57 | 1900-01-01 03:18 | 2025-01-22 07:20 | Tier-2 | 77 | 59 | 18 | 1 | 22 | N/A
Distribution | 214-613R | San Diego | 2025-01-20 18:14 | 2025-01-22 13:58 | 1899-12-31 19:44 | 2025-01-22 12:00 | Tier-3 | 100 | 82 | 18 | 3 | 7 | N/A
Distribution | 212-725R | San Diego | 2025-01-20 23:11 | 2025-01-22 14:00 | 1899-12-31 14:49 | 2025-01-22 07:20 | Tier-2 | 57 | 31 | 26 | 1 | 6 | N/A
Distribution | 212-799R | San Diego | 2025-01-20 10:39 | 2025-01-22 14:12 | 1900-01-01 03:33 | 2025-01-22 07:20 | Tier-2 | 40 | 28 | 12 | 1 | 6 | N/A
Distribution | CTL1-3R | San Diego | 2025-01-20 18:14 | 2025-01-22 14:14 | 1899-12-31 20:00 | 2025-01-22 12:00 | Tier-3 | 193 | 174 | 19 | 3 | 31 | N/A
Distribution | 212-773R | San Diego | 2025-01-20 10:39 | 2025-01-22 14:25 | 1900-01-01 03:46 | 2025-01-22 07:20 | Tier-2 | 125 | 109 | 16 | 3 | 35 | N/A
Distribution | 212-888R | Riverside, San Diego | 2025-01-20 10:39 | 2025-01-22 14:28 | 1900-01-01 03:49 | 2025-01-22 07:20 | Tier-2 | 48 | 32 | 16 | 0 | 7 | N/A
Distribution | 444-9R | San Diego | 2025-01-20 19:51 | 2025-01-22 14:42 | 1899-12-31 18:51 | 2025-01-22 08:47 | Tier-2 | 282 | 236 | 46 | 15 | 133 | N/A
Distribution | 212-886R | San Diego | 2025-01-20 10:39 | 2025-01-22 14:44 | 1900-01-01 04:05 | 2025-01-22 07:20 | Tier-2 | 21 | 9 | 12 | 1 | 3 | N/A
Distribution | 444-15R | Imperial, San Diego | 2025-01-20 19:51 | 2025-01-22 14:58 | 1899-12-31 19:07 | 2025-01-22 08:44 | Tier-2 | 16 | 9 | 7 | 2 | 5 | N/A
Distribution | 1101-590 | San Diego | 2025-01-23 10:37 | 2025-01-23 11:00 | 0.015972 | 2025-01-23 10:59 | Tier-2 | 614 | 578 | 36 | 33 | 138 | N/A
Distribution | ARR-12KV-1101 | San Diego | 2025-01-23 10:37 | 2025-01-24 08:03 | 0.89306 | 2025-01-24 05:39 | Tier-2 | 3 | 0 | 3 | 0 | 0 | N/A
Distribution | 357-2049F | San Diego | 2025-01-23 19:48 | 2025-01-24 08:11 | 0.51597 | 2025-01-24 05:39 | Tier-2 | 206 | 198 | 8 | 12 | 34 | N/A
Distribution | 357-1299R | San Diego | 2025-01-23 19:48 | 2025-01-24 08:16 | 0.51944 | 2025-01-24 05:39 | Tier-2 | 10 | 9 | 1 | 2 | 4 | N/A
Transmission | TL50003 | San Diego | 2025-01-23 07:43 | 2025-01-24 08:52 | 1899-12-31 01:09 | 2025-01-24 05:39 | Tier-3 | 0 | 0 | 0 | 0 | 0 | N/A
Transmission | TL625 | San Diego | 2025-01-20 21:33 | 2025-01-24 08:52 | 1900-01-02 11:19 | 2025-01-24 05:39 | Tier-3 | 0 | 0 | 0 | 0 | 0 | N/A
Transmission | TL686 | San Diego | 2025-01-23 12:17 | 2025-01-24 08:52 | 0.85764 | 2025-01-24 05:39 | Tier-2 | 0 | 0 | 0 | 0 | 0 | N/A
Distribution | 358-1193F | San Diego | 2025-01-23 11:04 | 2025-01-24 08:57 | 0.91181 | 2025-01-24 05:39 | Tier-3 | 65 | 1 | 64 | 0 | 1 | N/A
Distribution | 358-682F | San Diego | 2025-01-22 10:02 | 2025-01-24 09:02 | 1899-12-31 23:00 | 2025-01-24 05:39 | Tier-3 | 187 | 168 | 19 | 11 | 53 | N/A
Transmission | TL6923 | San Diego | 2025-01-20 21:49 | 2025-01-24 09:13 | 1900-01-02 11:24 | 2025-01-24 05:39 | Tier-3 | 0 | 0 | 0 | 0 | 0 | N/A
Distribution | 217-983R | Riverside, San Diego | 2025-01-23 05:13 | 2025-01-24 09:15 | 1899-12-31 04:02 | 2025-01-24 05:39 | Tier-3 | 82 | 76 | 6 | 4 | 16 | N/A
Distribution | 1458-519 | San Diego | 2025-01-23 05:00 | 2025-01-24 09:17 | 1899-12-31 04:17 | 2025-01-24 05:39 | Tier-3 | 1 | 0 | 1 | 0 | 0 | N/A
Distribution | BR-12KV-170 | San Diego | 2025-01-23 12:17 | 2025-01-24 09:19 | 0.87639 | 2025-01-24 05:39 | Non HFTD | 603 | 520 | 83 | 16 | 78 | N/A
Distribution | 1166-15R | San Diego | 2025-01-23 09:00 | 2025-01-24 09:20 | 1899-12-31 00:20 | 2025-01-24 05:39 | Tier-3 | 61 | 56 | 5 | 6 | 18 | N/A
Distribution | BR-12KV-171 | San Diego | 2025-01-23 12:17 | 2025-01-24 09:20 | 0.87708 | 2025-01-24 05:39 | Non HFTD | 765 | 594 | 171 | 34 | 207 | N/A
Distribution | 171-704R | San Diego | 2025-01-23 12:17 | 2025-01-24 09:21 | 0.87778 | 2025-01-24 05:39 | Non HFTD | 135 | 109 | 26 | 2 | 16 | N/A
Distribution | DE-12KV-73 | San Diego | 2025-01-20 21:01 | 2025-01-24 09:22 | 1900-01-02 12:21 | 2025-01-24 05:39 | Tier-3 | 256 | 220 | 36 | 13 | 64 | N/A
Distribution | 1166-18R | San Diego | 2025-01-23 09:00 | 2025-01-24 09:23 | 1899-12-31 00:23 | 2025-01-24 05:39 | Tier-3 | 17 | 13 | 4 | 2 | 3 | N/A
Distribution | 171-708R | San Diego | 2025-01-23 12:17 | 2025-01-24 09:24 | 0.87986 | 2025-01-24 05:39 | Non HFTD | 219 | 206 | 13 | 13 | 44 | N/A
Distribution | BR-12KV-172 | San Diego | 2025-01-23 12:17 | 2025-01-24 09:26 | 0.88125 | 2025-01-24 05:39 | Non HFTD | 24 | 6 | 18 | 0 | 1 | N/A
Distribution | 171-6R | San Diego | 2025-01-23 12:17 | 2025-01-24 09:27 | 0.88194 | 2025-01-24 05:39 | Non HFTD | 84 | 83 | 1 | 5 | 46 | N/A
Distribution | 172-615R | San Diego | 2025-01-23 12:17 | 2025-01-24 09:28 | 0.88264 | 2025-01-24 05:39 | Non HFTD | 212 | 183 | 29 | 1 | 37 | N/A
Distribution | BR-12KV-173 | San Diego | 2025-01-23 12:17 | 2025-01-24 09:29 | 0.88333 | 2025-01-24 05:39 | Non HFTD | 2 | 0 | 2 | 0 | 0 | N/A
Distribution | OV-12KV-1250 | San Diego | 2025-01-23 07:54 | 2025-01-24 09:29 | 1899-12-31 01:35 | 2025-01-24 05:39 | Tier-2 | 3 | 3 | 0 | 0 | 0 | N/A
Distribution | 157-232R | San Diego | 2025-01-23 05:30 | 2025-01-24 09:31 | 1899-12-31 04:01 | 2025-01-24 05:39 | Tier-3 | 94 | 87 | 7 | 9 | 38 | N/A
Distribution | 73-683R | San Diego | 2025-01-20 21:01 | 2025-01-24 09:31 | 1900-01-02 12:30 | 2025-01-24 05:39 | Tier-3 | 126 | 98 | 28 | 10 | 22 | N/A
Distribution | 1250-677R | San Diego | 2025-01-23 07:54 | 2025-01-24 09:32 | 1899-12-31 01:38 | 2025-01-24 05:39 | Tier-2 | 148 | 125 | 23 | 4 | 17 | N/A
Distribution | 1166-342R | San Diego | 2025-01-23 09:00 | 2025-01-24 09:34 | 1899-12-31 00:34 | 2025-01-24 05:39 | Tier-3 | 84 | 72 | 12 | 4 | 16 | N/A
Distribution | 1458-601R | San Diego | 2025-01-23 05:00 | 2025-01-24 09:34 | 1899-12-31 04:34 | 2025-01-24 05:39 | Tier-3 | 287 | 227 | 60 | 38 | 93 | N/A
Distribution | 172-567R | San Diego | 2025-01-23 12:17 | 2025-01-24 09:35 | 0.8875 | 2025-01-24 05:39 | Non HFTD | 244 | 238 | 6 | 7 | 92 | N/A
Distribution | 172-569R | San Diego | 2025-01-23 12:17 | 2025-01-24 09:35 | 0.8875 | 2025-01-24 05:39 | Non HFTD | 216 | 162 | 54 | 6 | 36 | N/A
Distribution | 971-1973R | San Diego | 2025-01-23 10:02 | 2025-01-24 09:35 | 0.98125 | 2025-01-24 05:39 | Tier-3 | 303 | 269 | 34 | 38 | 62 | N/A
Distribution | 1250-8R | San Diego | 2025-01-23 07:54 | 2025-01-24 09:36 | 1899-12-31 01:42 | 2025-01-24 05:39 | Tier-2 | 128 | 116 | 12 | 6 | 18 | N/A
Distribution | 157-273R | San Diego | 2025-01-23 13:15 | 2025-01-24 09:37 | 0.84861 | 2025-01-24 05:39 | Tier-3 | 53 | 44 | 9 | 8 | 24 | N/A
Distribution | 1250-671R | San Diego | 2025-01-23 07:54 | 2025-01-24 09:40 | 1899-12-31 01:46 | 2025-01-24 05:39 | Tier-2 | 709 | 692 | 17 | 48 | 107 | N/A
Transmission | TL629 | San Diego | 2025-01-20 20:38 | 2025-01-24 09:41 | 1900-01-02 13:03 | 2025-01-24 05:39 | Tier-3 | 0 | 0 | 0 | 0 | 0 | N/A
Distribution | 1250-27R | San Diego | 2025-01-23 07:54 | 2025-01-24 09:43 | 1899-12-31 01:49 | 2025-01-24 05:39 | Tier-2 | 840 | 812 | 28 | 62 | 211 | N/A
Distribution | 172-630R | San Diego | 2025-01-23 12:17 | 2025-01-24 09:45 | 0.89444 | 2025-01-24 05:39 | Non HFTD | 298 | 274 | 24 | 4 | 31 | N/A
Transmission | TL6958 | San Diego | 2025-01-20 21:39 | 2025-01-24 09:45 | 1900-01-02 12:06 | 2025-01-24 05:39 | Tier-3 | 0 | 0 | 0 | 0 | 0 | N/A
Distribution | DE-12KV-78 | San Diego | 2025-01-20 21:02 | 2025-01-24 09:46 | 1900-01-02 12:44 | 2025-01-24 05:39 | Tier-3 | 106 | 98 | 8 | 15 | 27 | N/A
Transmission | TL6931 | San Diego | 2025-01-20 20:27 | 2025-01-24 09:46 | 1900-01-02 13:19 | 2025-01-24 05:39 | Tier-2 | 0 | 0 | 0 | 0 | 0 | N/A
Distribution | 157-165R | San Diego | 2025-01-23 13:15 | 2025-01-24 09:52 | 0.85903 | 2025-01-24 05:39 | Tier-3 | 35 | 26 | 9 | 0 | 7 | N/A
Distribution | 73-678R | San Diego | 2025-01-20 18:58 | 2025-01-24 09:55 | 1900-01-02 14:57 | 2025-01-24 05:39 | Tier-3 | 149 | 129 | 20 | 14 | 33 | N/A
Distribution | 157-257R | San Diego | 2025-01-23 13:15 | 2025-01-24 10:03 | 0.86667 | 2025-01-24 05:39 | Tier-3 | 228 | 189 | 39 | 10 | 80 | N/A
Distribution | STY-12KV-222 | San Diego | 2025-01-20 19:35 | 2025-01-24 10:04 | 1900-01-02 14:29 | 2025-01-24 05:39 | Tier-3 | 535 | 428 | 107 | 31 | 80 | N/A
Distribution | 73-23R | San Diego | 2025-01-20 18:58 | 2025-01-24 10:08 | 1900-01-02 15:10 | 2025-01-24 05:39 | Tier-3 | 75 | 56 | 19 | 8 | 14 | N/A
Distribution | 222-1523R | San Diego | 2025-01-20 19:35 | 2025-01-24 10:13 | 1900-01-02 14:38 | 2025-01-24 05:39 | Tier-3 | 197 | 161 | 36 | 17 | 35 | N/A
Distribution | 222-1992R | San Diego | 2025-01-20 19:35 | 2025-01-24 10:14 | 1900-01-02 14:39 | 2025-01-24 05:39 | Tier-3 | 27 | 12 | 15 | 2 | 4 | N/A
Distribution | 283-55R | San Diego | 2025-01-23 08:53 | 2025-01-24 10:14 | 1899-12-31 01:21 | 2025-01-24 05:39 | Tier-3 | 316 | 230 | 86 | 18 | 48 | N/A
Distribution | 1233-259R | San Diego | 2025-01-23 09:13 | 2025-01-24 10:15 | 1899-12-31 01:02 | 2025-01-24 05:39 | Tier-3 | 29 | 8 | 21 | 0 | 0 | N/A
Distribution | 73-1130R | San Diego | 2025-01-20 18:58 | 2025-01-24 10:15 | 1900-01-02 15:17 | 2025-01-24 05:39 | Tier-3 | 145 | 137 | 8 | 11 | 47 | N/A
Distribution | 78-782R | San Diego | 2025-01-20 21:02 | 2025-01-24 10:19 | 1900-01-02 13:17 | 2025-01-24 05:39 | Tier-3 | 17 | 14 | 3 | 1 | 4 | N/A
Distribution | DV1-3R | San Diego | 2025-01-23 08:53 | 2025-01-24 10:25 | 1899-12-31 01:32 | 2025-01-24 05:39 | Tier-3 | 171 | 151 | 20 | 11 | 35 | N/A
Distribution | 157-189R | San Diego | 2025-01-23 05:29 | 2025-01-24 10:27 | 1899-12-31 04:58 | 2025-01-24 05:39 | Tier-3 | 248 | 177 | 71 | 4 | 101 | N/A
Distribution | 222-1990R | San Diego | 2025-01-20 19:35 | 2025-01-24 10:27 | 1900-01-02 14:52 | 2025-01-24 05:39 | Tier-3 | 78 | 42 | 36 | 3 | 9 | N/A
Distribution | 222-1433R | San Diego | 2025-01-20 19:35 | 2025-01-24 10:30 | 1900-01-02 14:55 | 2025-01-24 05:39 | Tier-3 | 16 | 13 | 3 | 1 | 5 | N/A
Distribution | 222-1503R | San Diego | 2025-01-20 19:35 | 2025-01-24 10:38 | 1900-01-02 15:03 | 2025-01-24 05:39 | Tier-3 | 46 | 38 | 8 | 2 | 5 | N/A
Distribution | 449-6R | San Diego | 2025-01-20 21:44 | 2025-01-24 10:40 | 1900-01-02 12:56 | 2025-01-24 05:39 | Tier-3 | 75 | 72 | 3 | 5 | 35 | N/A
Distribution | 222-1988R | San Diego | 2025-01-20 19:35 | 2025-01-24 10:41 | 1900-01-02 15:06 | 2025-01-24 05:39 | Tier-3 | 10 | 8 | 2 | 0 | 3 | N/A
Distribution | CN-12.47KV-448 | San Diego | 2025-01-20 21:44 | 2025-01-24 10:44 | 1900-01-02 13:00 | 2025-01-24 05:39 | Tier-3 | 5 | 2 | 3 | 1 | 1 | N/A
Distribution | 222-1986R | San Diego | 2025-01-20 19:35 | 2025-01-24 10:47 | 1900-01-02 15:12 | 2025-01-24 05:39 | Tier-3 | 307 | 220 | 87 | 17 | 52 | N/A
Distribution | 449-13R | San Diego | 2025-01-20 21:44 | 2025-01-24 10:49 | 1900-01-02 13:05 | 2025-01-24 05:39 | Tier-3 | 477 | 423 | 54 | 47 | 211 | N/A
Distribution | 449-16R | San Diego | 2025-01-20 21:44 | 2025-01-24 10:50 | 1900-01-02 13:06 | 2025-01-24 05:39 | Tier-3 | 33 | 32 | 1 | 0 | 10 | N/A
Distribution | 449-693R | San Diego | 2025-01-20 21:44 | 2025-01-24 10:51 | 1900-01-02 13:07 | 2025-01-24 05:39 | Tier-3 | 42 | 36 | 6 | 3 | 14 | N/A
Distribution | 222-2013R | San Diego | 2025-01-20 19:35 | 2025-01-24 10:52 | 1900-01-02 15:17 | 2025-01-24 05:39 | Tier-3 | 247 | 199 | 48 | 10 | 41 | N/A
Distribution | 1233-587R | San Diego | 2025-01-23 09:13 | 2025-01-24 10:55 | 1899-12-31 01:42 | 2025-01-24 05:39 | Tier-3 | 91 | 78 | 13 | 2 | 13 | N/A
Distribution | 448-9R | San Diego | 2025-01-20 21:44 | 2025-01-24 10:55 | 1900-01-02 13:11 | 2025-01-24 05:39 | Tier-3 | 139 | 118 | 21 | 9 | 64 | N/A
Distribution | 972-1582R | San Diego | 2025-01-23 09:52 | 2025-01-24 10:58 | 1899-12-31 01:06 | 2025-01-24 05:39 | Tier-3 | 162 | 116 | 46 | 12 | 20 | N/A
Distribution | 972-942R | San Diego | 2025-01-23 09:52 | 2025-01-24 11:01 | 1899-12-31 01:09 | 2025-01-24 05:39 | Tier-3 | 118 | 92 | 26 | 7 | 12 | N/A
Distribution | 448-744R | San Diego | 2025-01-20 21:44 | 2025-01-24 11:03 | 1900-01-02 13:19 | 2025-01-24 05:39 | Tier-3 | 340 | 301 | 39 | 27 | 137 | N/A
Distribution | 1233-589R | San Diego | 2025-01-23 09:13 | 2025-01-24 11:05 | 1899-12-31 01:52 | 2025-01-24 05:39 | Tier-3 | 17 | 8 | 9 | 0 | 1 | N/A
Distribution | 1030-1777 | San Diego | 2025-01-23 06:03 | 2025-01-24 11:06 | 1899-12-31 05:03 | 2025-01-24 05:39 | Tier-2 | 121 | 111 | 10 | 6 | 48 | N/A
Distribution | 448-714R | San Diego | 2025-01-20 21:44 | 2025-01-24 11:09 | 1900-01-02 13:25 | 2025-01-24 05:39 | Tier-3 | 369 | 303 | 66 | 31 | 162 | N/A
Distribution | 1458-1131R | San Diego | 2025-01-23 05:00 | 2025-01-24 11:10 | 1899-12-31 06:10 | 2025-01-24 05:39 | Tier-3 | 160 | 139 | 21 | 8 | 44 | N/A
Distribution | GC-12.47KV-441 | San Diego | 2025-01-20 20:29 | 2025-01-24 11:10 | 1900-01-02 14:41 | 2025-01-24 05:39 | Tier-3 | 18 | 5 | 13 | 0 | 0 | N/A
Distribution | 1030-42R | San Diego | 2025-01-23 06:03 | 2025-01-24 11:11 | 1899-12-31 05:08 | 2025-01-24 05:39 | Tier-2 | 308 | 264 | 44 | 25 | 85 | N/A
Distribution | 441-23R | San Diego | 2025-01-20 17:27 | 2025-01-24 11:12 | 1900-01-02 17:45 | 2025-01-24 05:39 | Tier-3 | 25 | 7 | 18 | 0 | 2 | N/A
Distribution | 441-279R | San Diego | 2025-01-20 17:27 | 2025-01-24 11:13 | 1900-01-02 17:46 | 2025-01-24 05:39 | Tier-3 | 11 | 3 | 8 | 0 | 0 | N/A
Distribution | 1030-1728R | San Diego | 2025-01-23 06:03 | 2025-01-24 11:15 | 1899-12-31 05:12 | 2025-01-24 05:39 | Tier-2 | 66 | 64 | 2 | 3 | 26 | N/A
Distribution | RB1-433R | Riverside, San Diego | 2025-01-23 11:04 | 2025-01-24 11:15 | 1899-12-31 00:11 | 2025-01-24 05:39 | Tier-3 | 44 | 31 | 13 | 1 | 5 | N/A
Distribution | 448-724R | San Diego | 2025-01-20 21:44 | 2025-01-24 11:16 | 1900-01-02 13:32 | 2025-01-24 05:39 | Tier-3 | 43 | 29 | 14 | 2 | 14 | N/A
Distribution | 1030-20R | San Diego | 2025-01-23 06:03 | 2025-01-24 11:22 | 1899-12-31 05:19 | 2025-01-24 05:39 | Tier-2 | 149 | 109 | 40 | 4 | 29 | N/A
Distribution | BUE-12.47KV-445 | San Diego | 2025-01-20 19:58 | 2025-01-24 11:23 | 1900-01-02 15:25 | 2025-01-24 05:39 | Tier-2 | 28 | 16 | 12 | 1 | 7 | N/A
Distribution | 1030-18R | San Diego | 2025-01-23 06:03 | 2025-01-24 11:25 | 1899-12-31 05:22 | 2025-01-24 05:39 | Tier-2 | 61 | 58 | 3 | 0 | 18 | N/A
Distribution | 1233-585R | San Diego | 2025-01-23 09:13 | 2025-01-24 11:26 | 1899-12-31 02:13 | 2025-01-24 05:39 | Tier-3 | 80 | 69 | 11 | 2 | 17 | N/A
Distribution | 441-27R | San Diego | 2025-01-20 17:27 | 2025-01-24 11:27 | 1900-01-02 18:00 | 2025-01-24 05:39 | Tier-3 | 30 | 22 | 8 | 1 | 5 | N/A
Distribution | 441-30R | San Diego | 2025-01-20 17:27 | 2025-01-24 11:28 | 1900-01-02 18:01 | 2025-01-24 05:39 | Tier-3 | 24 | 18 | 6 | 2 | 8 | N/A
Distribution | 1030-989R | San Diego | 2025-01-23 06:03 | 2025-01-24 11:29 | 1899-12-31 05:26 | 2025-01-24 05:39 | Tier-2 | 153 | 102 | 51 | 5 | 25 | N/A
Distribution | 448-735R | San Diego | 2025-01-20 21:44 | 2025-01-24 11:29 | 1900-01-02 13:45 | 2025-01-24 05:39 | Tier-3 | 45 | 31 | 14 | 0 | 20 | N/A
Distribution | 445-39R | San Diego | 2025-01-20 19:58 | 2025-01-24 11:36 | 1900-01-02 15:38 | 2025-01-24 05:39 | Tier-2 | 177 | 150 | 27 | 12 | 59 | N/A
Distribution | 211-279R | San Diego | 2025-01-20 22:50 | 2025-01-24 11:37 | 1900-01-02 12:47 | 2025-01-24 05:39 | Tier-2 | 66 | 58 | 8 | 7 | 17 | N/A
Distribution | 448-47R | San Diego | 2025-01-20 21:44 | 2025-01-24 11:37 | 1900-01-02 13:53 | 2025-01-24 05:39 | Tier-3 | 56 | 48 | 8 | 3 | 31 | N/A
Distribution | 448-1234R | San Diego | 2025-01-20 21:44 | 2025-01-24 11:39 | 1900-01-02 13:55 | 2025-01-24 05:39 | Tier-3 | 8 | 8 | 0 | 2 | 2 | N/A
Distribution | 445-19R | San Diego | 2025-01-20 19:58 | 2025-01-24 11:41 | 1900-01-02 15:43 | 2025-01-24 05:39 | Tier-2 | 84 | 71 | 13 | 9 | 34 | N/A
Distribution | 445-17R | San Diego | 2025-01-20 19:58 | 2025-01-24 11:42 | 1900-01-02 15:44 | 2025-01-24 05:39 | Tier-2 | 58 | 47 | 11 | 6 | 26 | N/A
Distribution | 1233-591R | San Diego | 2025-01-23 09:13 | 2025-01-24 11:47 | 1899-12-31 02:34 | 2025-01-24 05:39 | Tier-3 | 76 | 63 | 13 | 4 | 6 | N/A
Distribution | 211-771R | San Diego | 2025-01-20 22:50 | 2025-01-24 11:47 | 1900-01-02 12:57 | 2025-01-24 05:39 | Tier-2 | 80 | 52 | 28 | 0 | 17 | N/A
Distribution | 445-1325F | San Diego | 2025-01-20 08:44 | 2025-01-24 11:48 | 1900-01-03 03:04 | 2025-01-24 05:39 | Tier-2 | 90 | 73 | 17 | 8 | 23 | N/A
Distribution | GC-12.47KV-442 | San Diego | 2025-01-20 20:16 | 2025-01-24 11:51 | 1900-01-02 15:35 | 2025-01-24 05:39 | Tier-3 | 10 | 2 | 8 | 0 | 0 | N/A
Distribution | 237-1765R | San Diego | 2025-01-23 06:04 | 2025-01-24 12:02 | 1899-12-31 05:58 | 2025-01-24 05:39 | Tier-2 | 134 | 117 | 17 | 6 | 37 | N/A
Distribution | 211-312R | San Diego | 2025-01-20 19:50 | 2025-01-24 12:03 | 1900-01-02 16:13 | 2025-01-24 05:39 | Tier-2 | 151 | 130 | 21 | 12 | 54 | N/A
Distribution | 445-894R | San Diego | 2025-01-20 19:58 | 2025-01-24 12:03 | 1900-01-02 16:05 | 2025-01-24 05:39 | Tier-2 | 179 | 149 | 30 | 9 | 72 | N/A
Distribution | 445-897R | San Diego | 2025-01-20 08:41 | 2025-01-24 12:04 | 1900-01-03 03:23 | 2025-01-24 05:39 | Tier-2 | 8 | 8 |  | 1 | 4 | N/A
Distribution | 220-288R | San Diego | 2025-01-20 21:34 | 2025-01-24 12:08 | 1900-01-02 14:34 | 2025-01-24 05:39 | Tier-3 | 34 | 19 | 15 | 0 | 2 | N/A
Distribution | 442-728R | San Diego | 2025-01-20 19:23 | 2025-01-24 12:10 | 1900-01-02 16:47 | 2025-01-24 05:39 | Tier-3 | 869 | 765 | 104 | 66 | 186 | N/A
Distribution | 176-197F | San Diego | 2025-01-23 10:44 | 2025-01-24 12:11 | 1899-12-31 01:27 | 2025-01-24 05:39 | Tier-3 | 374 | 334 | 40 | 46 | 53 | N/A
Distribution | 445-1311R | San Diego | 2025-01-20 08:41 | 2025-01-24 12:13 | 1900-01-03 03:32 | 2025-01-24 05:39 | Tier-2 | 175 | 149 | 26 | 11 | 73 | N/A
Distribution | 220-294R | San Diego | 2025-01-20 21:34 | 2025-01-24 12:18 | 1900-01-02 14:44 | 2025-01-24 05:39 | Tier-3 | 129 | 101 | 28 | 10 | 54 | N/A
Distribution | TM1-10R | San Diego | 2025-01-23 09:35 | 2025-01-24 12:18 | 1899-12-31 02:43 | 2025-01-24 09:24 | Tier-3 | 36 | 30 | 6 | 0 | 5 | N/A
Distribution | 445-18R | San Diego | 2025-01-20 08:41 | 2025-01-24 12:19 | 1900-01-03 03:38 | 2025-01-24 05:39 | Tier-2 | 164 | 134 | 30 | 8 | 75 | N/A
Distribution | 521-14R | San Diego | 2025-01-23 09:55 | 2025-01-24 12:22 | 1899-12-31 02:27 | 2025-01-24 05:39 | Tier-2 | 266 | 252 | 14 | 18 | 45 | N/A
Distribution | 176-164R | San Diego | 2025-01-23 10:44 | 2025-01-24 12:23 | 1899-12-31 01:39 | 2025-01-24 05:39 | Tier-3 | 69 | 43 | 26 | 5 | 5 | N/A
Distribution | 220-298R | San Diego | 2025-01-20 21:00 | 2025-01-24 12:23 | 1900-01-02 15:23 | 2025-01-24 05:39 | Tier-3 | 171 | 119 | 52 | 1 | 30 | N/A
Distribution | 442-28R | San Diego | 2025-01-20 20:16 | 2025-01-24 12:29 | 1900-01-02 16:13 | 2025-01-24 05:39 | Tier-3 | 4 | 1 | 3 | 0 | 0 | N/A
Distribution | DE-12KV-79 | San Diego | 2025-01-20 21:04 | 2025-01-24 12:31 | 1900-01-02 15:27 | 2025-01-24 05:39 | Tier-3 | 18 | 10 | 8 | 0 | 3 | N/A
Distribution | 79-676R | San Diego | 2025-01-20 21:04 | 2025-01-24 12:33 | 1900-01-02 15:29 | 2025-01-24 05:39 | Tier-3 | 75 | 67 | 8 | 0 | 17 | N/A
Distribution | 176-1845R | San Diego | 2025-01-23 10:44 | 2025-01-24 12:34 | 1899-12-31 01:50 | 2025-01-24 05:39 | Tier-3 | 70 | 52 | 18 | 4 | 5 | N/A
Distribution | 175-64R | San Diego | 2025-01-23 10:16 | 2025-01-24 12:35 | 1899-12-31 02:19 | 2025-01-24 05:39 | Tier-3 | 106 | 73 | 33 | 4 | 8 | N/A
Distribution | 79-785 | San Diego | 2025-01-20 20:05 | 2025-01-24 12:36 | 1900-01-02 16:31 | 2025-01-24 05:39 | Tier-3 | 270 | 239 | 31 | 23 | 74 | N/A
Distribution | 79-714R | San Diego | 2025-01-20 20:05 | 2025-01-24 12:43 | 1900-01-02 16:38 | 2025-01-24 05:39 | Tier-3 | 94 | 78 | 16 | 6 | 21 | N/A
Distribution | 909-453R | San Diego | 2025-01-23 10:02 | 2025-01-24 12:44 | 1899-12-31 02:42 | 2025-01-24 05:39 | Tier-2 | 282 | 226 | 56 | 12 | 74 | N/A
Distribution | 442-764R | San Diego | 2025-01-20 20:16 | 2025-01-24 12:46 | 1900-01-02 16:30 | 2025-01-24 05:39 | Tier-3 | 19 | 17 | 2 | 1 | 1 | N/A
Distribution | 909-458R | San Diego | 2025-01-23 10:02 | 2025-01-24 12:46 | 1899-12-31 02:44 | 2025-01-24 05:39 | Tier-2 | 2 | 0 | 2 | 0 | 0 | N/A
Distribution | 442-32R | San Diego | 2025-01-20 20:16 | 2025-01-24 12:47 | 1900-01-02 16:31 | 2025-01-24 05:39 | Tier-3 | 2 | 0 | 2 | 0 | 0 | N/A
Distribution | 79-658R | San Diego | 2025-01-20 19:49 | 2025-01-24 12:48 | 1900-01-02 16:59 | 2025-01-24 05:39 | Tier-3 | 33 | 13 | 20 | 1 | 2 | N/A
Distribution | 1215-10R | San Diego | 2025-01-20 13:53 | 2025-01-24 12:52 | 1900-01-02 22:59 | 2025-01-24 05:39 | Tier-3 | 10 | 0 | 10 | 0 | 0 | N/A
Distribution | 442-46R | San Diego | 2025-01-20 20:16 | 2025-01-24 12:54 | 1900-01-02 16:38 | 2025-01-24 05:39 | Tier-3 | 171 | 141 | 30 | 2 | 10 | N/A
Distribution | 1215-12R | San Diego | 2025-01-20 13:53 | 2025-01-24 12:56 | 1900-01-02 23:03 | 2025-01-24 05:39 | Tier-3 | 35 | 33 | 2 | 5 | 15 | N/A
Distribution | 442-509R | San Diego | 2025-01-20 20:16 | 2025-01-24 12:56 | 1900-01-02 16:40 | 2025-01-24 05:39 | Tier-3 | 58 | 48 | 10 | 0 | 2 | N/A
Distribution | 79-679R | San Diego | 2025-01-20 21:04 | 2025-01-24 12:58 | 1900-01-02 15:54 | 2025-01-24 05:39 | Tier-3 | 96 | 89 | 7 | 10 | 11 | N/A
Distribution | 79-660R | San Diego | 2025-01-20 19:49 | 2025-01-24 13:03 | 1900-01-02 17:14 | 2025-01-24 05:39 | Tier-3 | 18 | 4 | 14 | 0 | 0 | N/A
Distribution | 909-805R | San Diego | 2025-01-23 10:02 | 2025-01-24 13:05 | 1899-12-31 03:03 | 2025-01-24 05:39 | Tier-2 | 150 | 105 | 45 | 4 | 30 | N/A
Distribution | 79-685R | San Diego | 2025-01-20 17:52 | 2025-01-24 13:06 | 1900-01-02 19:14 | 2025-01-24 05:39 | Tier-3 | 5 | 3 | 2 | 0 | 0 | N/A
Distribution | 79-808R | San Diego | 2025-01-20 21:04 | 2025-01-24 13:09 | 1900-01-02 16:05 | 2025-01-24 05:39 | Tier-3 | 70 | 54 | 16 | 2 | 14 | N/A
Distribution | 1215-28R | San Diego | 2025-01-20 13:53 | 2025-01-24 13:12 | 1900-01-02 23:19 | 2025-01-24 05:39 | Tier-3 | 33 | 19 | 14 | 2 | 13 | N/A
Distribution | 79-799R | San Diego | 2025-01-20 08:04 | 2025-01-24 13:15 | 1900-01-03 05:11 | 2025-01-24 05:39 | Tier-3 | 18 | 14 | 4 | 1 | 4 | N/A
Distribution | 79-782R | San Diego | 2025-01-20 19:49 | 2025-01-24 13:18 | 1900-01-02 17:29 | 2025-01-24 05:39 | Tier-3 | 1 | 0 | 1 | 0 | 0 | N/A
Distribution | 1215-32R | San Diego | 2025-01-20 13:53 | 2025-01-24 13:24 | 1900-01-02 23:31 | 2025-01-24 05:39 | Tier-3 | 76 | 58 | 18 | 1 | 24 | N/A
Distribution | 79-668R | San Diego | 2025-01-20 19:49 | 2025-01-24 13:26 | 1900-01-02 17:37 | 2025-01-24 05:39 | Tier-3 | 194 | 154 | 40 | 3 | 18 | N/A
Distribution | 214-1122R | San Diego | 2025-01-23 06:17 | 2025-01-24 13:49 | 1899-12-31 07:32 | 2025-01-24 05:39 | Tier-3 | 236 | 185 | 51 | 8 | 64 | N/A
Distribution | 214-647R | San Diego | 2025-01-23 06:17 | 2025-01-24 13:51 | 1899-12-31 07:34 | 2025-01-24 05:39 | Tier-3 | 137 | 116 | 21 | 8 | 59 | N/A
Distribution | 212-638R | San Diego | 2025-01-23 12:07 | 2025-01-24 14:04 | 1899-12-31 01:57 | 2025-01-24 05:39 | Tier-2 | 7 | 7 | 0 | 0 | 3 | N/A
Distribution | 212-739R | San Diego | 2025-01-23 12:07 | 2025-01-24 14:06 | 1899-12-31 01:59 | 2025-01-24 05:39 | Tier-2 | 46 | 31 | 15 | 2 | 9 | N/A
Distribution | 212-734R | San Diego | 2025-01-23 12:07 | 2025-01-24 14:14 | 1899-12-31 02:07 | 2025-01-24 05:39 | Tier-2 | 23 | 0 | 23 | 0 | 0 | N/A
Distribution | 212-725R | San Diego | 2025-01-23 12:07 | 2025-01-24 14:18 | 1899-12-31 02:11 | 2025-01-24 05:39 | Tier-2 | 57 | 31 | 26 | 1 | 6 | N/A
Distribution | 210-50 | San Diego | 2025-01-23 12:25 | 2025-01-24 14:30 | 1899-12-31 02:05 | 2025-01-24 05:39 | Tier-2 | 24 | 2 | 22 | 0 | 0 | N/A
Distribution | 210-9R | San Diego | 2025-01-23 12:25 | 2025-01-24 14:34 | 1899-12-31 02:09 | 2025-01-24 05:39 | Tier-2 | 85 | 84 | 1 | 7 | 16 | N/A
Distribution | 520-1527R | San Diego | 2025-01-23 09:59 | 2025-01-24 14:36 | 1899-12-31 04:37 | 2025-01-24 05:39 | Tier-2 | 168 | 146 | 22 | 16 | 31 | N/A
Distribution | 520-35R | Riverside, San Diego | 2025-01-23 09:59 | 2025-01-24 14:39 | 1899-12-31 04:40 | 2025-01-24 05:39 | Tier-2 | 134 | 86 | 48 | 5 | 16 | N/A
Distribution | 214-613R | San Diego | 2025-01-23 19:26 | 2025-01-24 14:40 | 0.80139 | 2025-01-24 05:39 | Tier-3 | 100 | 82 | 18 | 3 | 7 | N/A
Distribution | 520-1045R | Riverside, San Diego | 2025-01-23 09:59 | 2025-01-24 14:44 | 1899-12-31 04:45 | 2025-01-24 05:39 | Tier-2 | 59 | 29 | 30 | 1 | 4 | N/A
Distribution | 520-1509R | San Diego | 2025-01-23 09:59 | 2025-01-24 14:47 | 1899-12-31 04:48 | 2025-01-24 05:39 | Tier-2 | 185 | 142 | 43 | 12 | 39 | N/A
Distribution | SCE-218 | Riverside, San Diego | 2025-01-23 10:39 | 2025-01-24 14:50 | 1899-12-31 04:11 | 2025-01-24 05:39 | Non HFTD | 1 | 0 | 1 | 0 | 0 | N/A
Distribution | CTL1-3R | San Diego | 2025-01-23 19:26 | 2025-01-24 14:51 | 0.80903 | 2025-01-24 05:39 | Tier-3 | 193 | 174 | 19 | 3 | 31 | N/A
Distribution | 212-880R | San Diego | 2025-01-23 12:07 | 2025-01-24 14:54 | 1899-12-31 02:47 | 2025-01-24 05:39 | Tier-2 | 3 | 3 | 0 | 0 | 0 | N/A
Distribution | 210-394R | San Diego | 2025-01-23 12:25 | 2025-01-24 14:57 | 1899-12-31 02:32 | 2025-01-24 05:39 | Tier-2 | 23 | 2 | 21 | 0 | 0 | N/A
Distribution | 210-392R | San Diego | 2025-01-23 12:25 | 2025-01-24 14:59 | 1899-12-31 02:34 | 2025-01-24 05:39 | Tier-2 | 79 | 67 | 12 | 6 | 38 | N/A
Distribution | 212-1177R | San Diego | 2025-01-23 12:07 | 2025-01-24 15:06 | 1899-12-31 02:59 | 2025-01-24 05:39 | Tier-2 | 111 | 77 | 34 | 3 | 33 | N/A
Distribution | 212-758R | San Diego | 2025-01-23 12:07 | 2025-01-24 15:11 | 1899-12-31 03:04 | 2025-01-24 05:39 | Tier-2 | 54 | 37 | 17 | 0 | 15 | N/A
Distribution | 212-743R | San Diego | 2025-01-23 12:07 | 2025-01-24 15:12 | 1899-12-31 03:05 | 2025-01-24 05:39 | Tier-2 | 10 | 8 | 2 | 0 | 1 | N/A
Distribution | 212-799R | San Diego | 2025-01-23 12:07 | 2025-01-24 15:23 | 1899-12-31 03:16 | 2025-01-24 05:39 | Tier-2 | 40 | 28 | 12 | 1 | 6 | N/A
Distribution | 212-1204R | San Diego | 2025-01-23 12:07 | 2025-01-24 15:26 | 1899-12-31 03:19 | 2025-01-24 05:39 | Tier-2 | 77 | 59 | 18 | 1 | 22 | N/A
Distribution | 212-888R | Riverside, San Diego | 2025-01-23 12:07 | 2025-01-24 15:33 | 1899-12-31 03:26 | 2025-01-24 05:39 | Tier-2 | 48 | 32 | 16 | 0 | 7 | N/A
Distribution | 212-773R | San Diego | 2025-01-23 12:07 | 2025-01-24 15:35 | 1899-12-31 03:28 | 2025-01-24 05:39 | Tier-2 | 125 | 109 | 16 | 3 | 35 | N/A
Distribution | 212-886R | San Diego | 2025-01-23 12:07 | 2025-01-24 15:48 | 1899-12-31 03:41 | 2025-01-24 05:39 | Tier-2 | 21 | 9 | 12 | 1 | 3 | N/A
Distribution | 441-570 | San Diego | 2025-01-20 17:27 | 2025-01-24 16:33 | 1900-01-02 23:06 | 2025-01-24 05:39 | Tier-3 | 2 | 0 | 2 | 0 | 0 | N/A
Distribution | 175-285 | San Diego | 2025-01-23 10:16 | 2025-01-24 17:06 | 1899-12-31 06:50 | 2025-01-24 05:39 | Tier-3 | 2 | 1 | 1 | 0 | 0 | N/A
1Includes all customers that meet any of the 12 AFN conditions flagged in SDG&E’s customer information system as long as MBL is not the only condition.
Formulas:
Duration = [Restoration Date/Time]-[De-energization Date and Time]

## Table 4
Public Safety Power Shutoff Post-Event Report: JANUARY 20 – JANUARY 24, 2025
Appendix 5: PSPS Event Data Workbook
Table 4: Damages and Hazards
Circuit/ Device Name | County | Structure Identifier | HFTD Tier | Type of Damage/Hazard
449 | San Diego | P42621J | 3 | Broken Pole
476 | San Diego | P108167 | Non-HFTD | Broken Pole
175 | San Diego | P133349 | 3 | Broken Pole
Average customer duration calculation
22:00
5:05
27:40
25:58
29:23
26:58
27:02
25:45
27:52
26:25
30:05
29:55
18:45
30:02
29:47
29:29
31:32
31:41
9:25
8:34
32:11
32:20
33:01
12:56
12:31
10:25
41:48
41:25
41:12
42:09
41:20
41:16
42:11
41:12

## Table 5
Public Safety Power Shutoff Post-Event Report: JANUARY 20 – JANUARY 24, 2025
Appendix 5: PSPS Event Data Workbook
Table 5: Positive Notification
Designation | Total Number of Customers | Notification Attempts Made | Timing of Attempts | Who made the Notification Attempt | Successful Positive Notification
MBL | 5927 | 14044 | 1/18 13:28 PDT - 1/21 09:48 PDT | SDGE | 5927
MBL behind a master meter | 235 | 494 | 1/18 13:28 PDT - 1/21 09:48 PDT | SDGE | N/A

## Table 6
Public Safety Power Shutoff Post-Event Report: JANUARY 20 – JANUARY 24, 2025
Appendix 5: PSPS Event Data Workbook
Table 6: Notification Failure
Notifications Sent To | Notification Failure Description | Number of Entities or Customer Accouunts | Explanation
Public Safety Partners excluding Critical Facilities and Infrastructure | Entities who did not receive 48- to 72-hour advance notification. | 0
| Entities who did not receive 1–4-hour imminent notification. | 0
| Entities who did not receive any notifications before de-energization | 0
| Entities who were not notified immediately before re-energization | 0
| Entities who did not receive cancellation notification within two hours of the decision to cancel | 0
Critical Facilities and Infrastructure | Facilities who did not receive 48–72-hour advance notification. | 0 | 5 Customers with no Contact Data
| Facilities who did not receive 1-4 hour of imminent notifications. | 0 | 4 Customers with no Contact Data
| Facilities who did not receive any notifications before de-energization. | 0 | 4 Customers with no Contact Data
| Facilities who were not notified at de-energization initiation. | 0 | 4 Customers with no Contact Data
| Facilities who were not notified immediately before re-energization. | 0 | 4 Customers with no Contact Data
| Facilities who were not notified when re-energization is complete. | 0 | 4 Customers with no Contact Data
| Facilities who did not receive cancellation notification within two hours of the decision to cancel | 0 | 1 Customer with no Contact Data
All Other Affected Customers | Customers who did not receive 24–48-hour advance notifications. | 190 | 190 customers did not receive the 48-24 hour notification because they were added to scope after the 24 hour period as a result of rapidly changing weather conditions. Of these 190 customers, there were 2 MBL customers. 1,137 customers with no contact data
| Customers who did not receive 1–4-hour imminent notifications. | 2261 | The 2,261 customers who did not receive the 1-4 hour notification is due to rapidly changing winds, allowing no time for the message prior to the immediate need to deenergize for safety. 520 customers with no contact data
| Customers who did not receive any notifications before de-energization. | 0 | 539 customers with no contact data
| Customers who were not notified at de-energization initiation. | 0 | 539 customers with no contact data
| Customers who were not notified immediately before re-energization. | 586 | 586 missed notifications due to special underground configuration to minimize de-energized customers. 536 customers with no contact data
| Customers who were not notified when re-energization is complete. | 2 | 2 missed notifications due to special underground configuration to minimize de-energized customers. 539 customers with no contact data
| Customers who did not receive cancellation notification within two hours of the decision to cancel | 105 | 105 shared customers with Edison missed the cancellation notification due to an internal miscommunication. Of these 105 customers, there were 11 MBL customers. 598 customers with no contact data

## Table 7
Public Safety Power Shutoff Post-Event Report: JANUARY 20 – JANUARY 24, 2025
Appendix 5: PSPS Event Data Workbook
Table 7: Public Safety Partners Contacted
Jurisdiction/Organization | Title | HFTD Tier | Date/Time Contacted
2-1-1 Orange County | Director of Community Programs | Non-HFTD¦Tier-2¦Zone-1 | See Appendix 2
2-1-1 San Diego | Duty Officer | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Alvarado Hospital | Building Engineer | Tier-2¦Tier-3 | See Appendix 2
Alvarado Hospital | Director Plant Operations | Tier-2¦Tier-3 | See Appendix 2
Alvarado Hospital | NA | Tier-2¦Tier-3 | See Appendix 2
Alvarado Hospital | NOT UNDER AHMC/ASSISTANT PROPERTY MANAGER | Tier-2¦Tier-3 | See Appendix 2
Alvarado Hospital | NOT UNDER AHMC/PROPERTY MANAGER | Tier-2¦Tier-3 | See Appendix 2
American Red Cross of Orange County | Regional Disaster Officer | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
American Red Cross San Diego Region | Disaster Program Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
American Red Cross San Diego Region | Disaster Program Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
AT&T | Area Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
AT&T | Client Director | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
AT&T | Director - Construction & Engineering | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
AT&T | Director - Government & Legislative Affairs | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
AT&T | Director - Regulatory Affairs | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
AT&T | Director - Technology Operations | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
AT&T | Director of External Affairs | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
AT&T | Director of External Affairs - Tertiary | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
AT&T | Distribution List | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
AT&T | Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
AT&T | Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
AT&T | Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
AT&T | Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
AT&T | Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
AT&T | Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
AT&T | Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
AT&T | Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
AT&T | Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
AT&T | Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
AT&T | Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
AT&T | Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
AT&T | Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
AT&T | Mobility Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
AT&T | Regulatory Relations | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
AT&T | Sr. Program Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
AT&T | Sr. Technology Service Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Barona Band of Mission Indians | Barona Fire Chief | Tier-3¦Zone-1 | See Appendix 2
Barona Band of Mission Indians | Chairman | Tier-3¦Zone-1 | See Appendix 2
Barona Band of Mission Indians | Councilman | Tier-3¦Zone-1 | See Appendix 2
Barona Band of Mission Indians | Councilman | Tier-3¦Zone-1 | See Appendix 2
Barona Band of Mission Indians | Councilwoman | Tier-3¦Zone-1 | See Appendix 2
Barona Band of Mission Indians | Councilwoman | Tier-3¦Zone-1 | See Appendix 2
Barona Band of Mission Indians | Director of Government Affairs | Tier-3¦Zone-1 | See Appendix 2
Barona Band of Mission Indians | Vice Chair | Tier-3¦Zone-1 | See Appendix 2
Cal Fire | Battalion Chief | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Cal Fire | Chief | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Cal Fire | Chief | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Cal Fire | Deputy Chief | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Cal OES Office of Tribal Affairs | Distribution List | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Cal OES Office of Tribal Affairs | Senior Emergency Services Coordinator | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Cal OES Office of Tribal Affairs | Tribal Coordinator | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Cal OES | Cal OES | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Cal OES | Cal OES | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Cal OES | California State Warning Center | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Cal OES | Emergency Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Cal OES | Emergency Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Cal OES | Emergency Services Coordinator | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Cal OES | Sr. Emergency Services Coordinator | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
California Highway Patrol | Otay Mesa CVEF | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
California Highway Patrol | Otay Mesa CVEF | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
California Highway Patrol | Otay Mesa CVEF | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
California Highway Patrol | Sergeant | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Caltrans | Associate Transportation Planner | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Caltrans | Caltrans D11 SSM II | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Caltrans | Caltrans Electric Supervisor | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Caltrans | Caltrans Electrical Supervisor | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Caltrans | Caltrans Electrician ll | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Caltrans | Caltrans Electrician ll | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Caltrans | Caltrans Electrician ll | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Caltrans | D11 EOC Coordinator | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Caltrans | District Director | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Caltrans | GIS Specialist | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Caltrans | PIO, Communications | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Caltrans | PIO, Communications | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Caltrans | PIO, Communications | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Caltrans | PIO, Communications | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Caltrans | PIO, Communications | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Caltrans | PIO, Communications | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Caltrans | PIO, Communications | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Caltrans | PIO, Communications | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Caltrans | Research Data Analyst | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Caltrans | Research Data Specialist 1 | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Caltrans | TMC Operations Engineer | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Caltrans | Traffic Management Center | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Caltrans | Traffic Operations Chief/Senior Transportation Electrical Engineer | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Caltrans | Transportation Electrical Engineer | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Caltrans | Transportation Electrical Engineer | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Caltrans | Transportation Electrical Engineer | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Caltrans | Transportation Electrical Engineer | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Campo Band of Kumeyaay Indians | Chairman | Tier-3¦Tier-2¦Zone-1 | See Appendix 2
Campo Band of Kumeyaay Indians | Environmental Data Technician/Administrator | Tier-3¦Tier-2¦Zone-1 | See Appendix 2
Campo Band of Kumeyaay Indians | Fire Chief | Tier-3¦Tier-2¦Zone-1 | See Appendix 2
Campo Band of Kumeyaay Indians | Muht Hei Board Chair | Tier-3¦Tier-2¦Zone-1 | See Appendix 2
Carlsbad Fire Department | Assistant Director of Emergency Services | Tier-2 | See Appendix 2
Carlsbad Water | Supervisor | Tier-2 | See Appendix 2
Carlsbad Water | Supervisor | Tier-2 | See Appendix 2
Carlsbad Water | Supervisor | Tier-2 | See Appendix 2
Charter | Charter | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Charter | Director | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Charter | Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
City of Aliso Viejo | CEO | Non-HFTD | See Appendix 2
City of Aliso Viejo | City Clerk | Non-HFTD | See Appendix 2
City of Aliso Viejo | City Manager | Non-HFTD | See Appendix 2
City of Aliso Viejo | Councilmember | Non-HFTD | See Appendix 2
City of Aliso Viejo | Councilmember | Non-HFTD | See Appendix 2
City of Aliso Viejo | Councilmember | Non-HFTD | See Appendix 2
City of Aliso Viejo | Councilmember | Non-HFTD | See Appendix 2
City of Aliso Viejo | Director of Public Works | Non-HFTD | See Appendix 2
City of Aliso Viejo | Emergency Manager | Non-HFTD | See Appendix 2
City of Aliso Viejo | Executive Assistant | Non-HFTD | See Appendix 2
City of Aliso Viejo | IT Manager | Non-HFTD | See Appendix 2
City of Aliso Viejo | Mayor | Non-HFTD | See Appendix 2
City of Aliso Viejo | Planning Director | Non-HFTD | See Appendix 2
City of Carlsbad | City Manager | Tier-2 | See Appendix 2
City of Carlsbad | Council Secretary | Tier-2 | See Appendix 2
City of Carlsbad | Councilmember | Tier-2 | See Appendix 2
City of Carlsbad | Councilmember | Tier-2 | See Appendix 2
City of Carlsbad | Councilmember | Tier-2 | See Appendix 2
City of Carlsbad | Councilmember | Tier-2 | See Appendix 2
City of Carlsbad | Deputy City Manager | Tier-2 | See Appendix 2
City of Carlsbad | Intergovernmental Affairs Director | Tier-2 | See Appendix 2
City of Carlsbad | Mayor | Tier-2 | See Appendix 2
City of Chula Vista | Battalion 51 | Tier-2 | See Appendix 2
City of Chula Vista | Battalion 52 | Tier-2 | See Appendix 2
City of Chula Vista | City Manager | Tier-2 | See Appendix 2
City of Chula Vista | Councilmember | Tier-2 | See Appendix 2
City of Chula Vista | Councilmember | Tier-2 | See Appendix 2
City of Chula Vista | Councilmember | Tier-2 | See Appendix 2
City of Chula Vista | Deputy City Manager Development Services | Tier-2 | See Appendix 2
City of Chula Vista | Emergency Manager | Tier-2 | See Appendix 2
City of Chula Vista | Environmmental Sustainability Manager | Tier-2 | See Appendix 2
City of Chula Vista | Inform ation Techonogy | Tier-2 | See Appendix 2
City of Chula Vista | Mayor | Tier-2 | See Appendix 2
City of Chula Vista | Public Works Director | Tier-2 | See Appendix 2
City of Coronado | Assistant City Manager | Non-HFTD | See Appendix 2
City of Coronado | City Manager | Non-HFTD | See Appendix 2
City of Coronado | Councilmember | Non-HFTD | See Appendix 2
City of Coronado | Councilmember | Non-HFTD | See Appendix 2
City of Coronado | Councilmember | Non-HFTD | See Appendix 2
City of Coronado | Councilmember | Non-HFTD | See Appendix 2
City of Coronado | Emergency Management Coordinator | Non-HFTD | See Appendix 2
City of Coronado | Mayor | Non-HFTD | See Appendix 2
City of Coronado | Police Dispatch Supv. | Non-HFTD | See Appendix 2
City of Coronado | Public Services Director | Non-HFTD | See Appendix 2
City of Dana Point | CEO | Tier-2 | See Appendix 2
City of Dana Point | City Attorney | Tier-2 | See Appendix 2
City of Dana Point | City Clerk | Tier-2 | See Appendix 2
City of Dana Point | City Manager | Tier-2 | See Appendix 2
City of Dana Point | Community Development Director | Tier-2 | See Appendix 2
City of Dana Point | Councilmember | Tier-2 | See Appendix 2
City of Dana Point | Councilmember | Tier-2 | See Appendix 2
City of Dana Point | Councilmember | Tier-2 | See Appendix 2
City of Dana Point | Councilmember | Tier-2 | See Appendix 2
City of Dana Point | Deputy Public Works Director/City Engineer | Tier-2 | See Appendix 2
City of Dana Point | Economic Development | Tier-2 | See Appendix 2
City of Dana Point | Emergency Manager | Tier-2 | See Appendix 2
City of Dana Point | Emergency Services Coordinator | Tier-2 | See Appendix 2
City of Dana Point | Executive Assistant | Tier-2 | See Appendix 2
City of Dana Point | Mayor | Tier-2 | See Appendix 2
City of Dana Point | Unknown | Tier-2 | See Appendix 2
City of Dana Point | Unknown | Tier-2 | See Appendix 2
City of Del Mar | Assistant City Manager | Non-HFTD | See Appendix 2
City of Del Mar | City Manager | Non-HFTD | See Appendix 2
City of Del Mar | Councilmember | Non-HFTD | See Appendix 2
City of Del Mar | Councilmember | Non-HFTD | See Appendix 2
City of Del Mar | Councilmember | Non-HFTD | See Appendix 2
City of Del Mar | Emergency Manager | Non-HFTD | See Appendix 2
City of Del Mar | Mayor | Non-HFTD | See Appendix 2
City of Del Mar | Public Works Director | Non-HFTD | See Appendix 2
City of El Cajon | Acting Director of Public Works/City Engineer | Tier-2 | See Appendix 2
City of El Cajon | After Hours | Tier-2 | See Appendix 2
City of El Cajon | Assistant to City Manager | Tier-2 | See Appendix 2
City of El Cajon | City Manager | Tier-2 | See Appendix 2
City of El Cajon | Communications Manager | Tier-2 | See Appendix 2
City of El Cajon | Councilmember | Tier-2 | See Appendix 2
City of El Cajon | Councilmember | Tier-2 | See Appendix 2
City of El Cajon | Councilmember | Tier-2 | See Appendix 2
City of El Cajon | Councilmember | Tier-2 | See Appendix 2
City of El Cajon | Director | Tier-2 | See Appendix 2
City of El Cajon | Mayor | Tier-2 | See Appendix 2
City of El Cajon | Officer | Tier-2 | See Appendix 2
City of El Cajon | Public Works | Tier-2 | See Appendix 2
City of El Cajon | Senior Management Analyst | Tier-2 | See Appendix 2
City of El Cajon | Unknown | Tier-2 | See Appendix 2
City of Encinitas | City Clerk | Tier-2 | See Appendix 2
City of Encinitas | City Manager | Tier-2 | See Appendix 2
City of Encinitas | Councilmember | Tier-2 | See Appendix 2
City of Encinitas | Councilmember | Tier-2 | See Appendix 2
City of Encinitas | Councilmember | Tier-2 | See Appendix 2
City of Encinitas | Development Services Director | Tier-2 | See Appendix 2
City of Encinitas | Director of Engineering | Tier-2 | See Appendix 2
City of Encinitas | Emergency Manager | Tier-2 | See Appendix 2
City of Encinitas | Emergency Manager | Tier-2 | See Appendix 2
City of Encinitas | Fire Chief Encinitas, Del Mar, Solana Beach | Tier-2 | See Appendix 2
City of Encinitas | Mayor | Tier-2 | See Appendix 2
City of Encinitas | Risk Manager | Tier-2 | See Appendix 2
City of Escondido | City Manager | Tier-3¦Tier-2 | See Appendix 2
City of Escondido | Communications Manager | Tier-3¦Tier-2 | See Appendix 2
City of Escondido | Councilmember | Tier-3¦Tier-2 | See Appendix 2
City of Escondido | Councilmember | Tier-3¦Tier-2 | See Appendix 2
City of Escondido | Councilmember | Tier-3¦Tier-2 | See Appendix 2
City of Escondido | Councilmember | Tier-3¦Tier-2 | See Appendix 2
City of Escondido | Deputy Director of Utilities | Tier-3¦Tier-2 | See Appendix 2
City of Escondido | Dispatch | Tier-3¦Tier-2 | See Appendix 2
City of Escondido | Fire Chief | Tier-3¦Tier-2 | See Appendix 2
City of Escondido | Mayor | Tier-3¦Tier-2 | See Appendix 2
City of Escondido | Public Information Officer | Tier-3¦Tier-2 | See Appendix 2
City of Escondido | Utilities Supervisor | Tier-3¦Tier-2 | See Appendix 2
City of Escondido | Utilities Supervisor | Tier-3¦Tier-2 | See Appendix 2
City of Escondido | Wastewater Supervisor | Tier-3¦Tier-2 | See Appendix 2
City of Escondido | Water Treatment Plant Supervisor | Tier-3¦Tier-2 | See Appendix 2
City of Imperial Beach | Chief Administrative Officer | Non-HFTD | See Appendix 2
City of Imperial Beach | City Manager | Non-HFTD | See Appendix 2
City of Imperial Beach | Community Dev Dept Director | Non-HFTD | See Appendix 2
City of Imperial Beach | Councilmember | Non-HFTD | See Appendix 2
City of Imperial Beach | Councilmember | Non-HFTD | See Appendix 2
City of Imperial Beach | Councilmember | Non-HFTD | See Appendix 2
City of Imperial Beach | Councilmember | Non-HFTD | See Appendix 2
City of Imperial Beach | Fire Chief | Non-HFTD | See Appendix 2
City of Imperial Beach | Mayor | Non-HFTD | See Appendix 2
City of Imperial Beach | Public Works Director | Non-HFTD | See Appendix 2
City of La Mesa | City Manager | Non-HFTD | See Appendix 2
City of La Mesa | Councilmember | Non-HFTD | See Appendix 2
City of La Mesa | Councilmember | Non-HFTD | See Appendix 2
City of La Mesa | Councilmember | Non-HFTD | See Appendix 2
City of La Mesa | Councilmember | Non-HFTD | See Appendix 2
City of La Mesa | Director of Public Works | Non-HFTD | See Appendix 2
City of La Mesa | Mayor | Non-HFTD | See Appendix 2
City of Laguna Beach | CEO | Tier-2 | See Appendix 2
City of Laguna Beach | City Attorney | Tier-2 | See Appendix 2
City of Laguna Beach | City Clerk | Tier-2 | See Appendix 2
City of Laguna Beach | City Manager | Tier-2 | See Appendix 2
City of Laguna Beach | Community Development | Tier-2 | See Appendix 2
City of Laguna Beach | Community Development | Tier-2 | See Appendix 2
City of Laguna Beach | Councilmember | Tier-2 | See Appendix 2
City of Laguna Beach | Councilmember | Tier-2 | See Appendix 2
City of Laguna Beach | Councilmember | Tier-2 | See Appendix 2
City of Laguna Beach | Councilmember | Tier-2 | See Appendix 2
City of Laguna Beach | Executive Assistant | Tier-2 | See Appendix 2
City of Laguna Beach | Mayor | Tier-2 | See Appendix 2
City of Laguna Hills | City Atty – Woodruff, Spadlin & Smart | Non-HFTD | See Appendix 2
City of Laguna Hills | City Clerk | Non-HFTD | See Appendix 2
City of Laguna Hills | City Manager | Non-HFTD | See Appendix 2
City of Laguna Hills | Community Development Director/Planning Director | Non-HFTD | See Appendix 2
City of Laguna Hills | Councilmember | Non-HFTD | See Appendix 2
City of Laguna Hills | Councilmember | Non-HFTD | See Appendix 2
City of Laguna Hills | Councilmember | Non-HFTD | See Appendix 2
City of Laguna Hills | Councilmember | Non-HFTD | See Appendix 2
City of Laguna Hills | Deputy City Manager/Comm Services | Non-HFTD | See Appendix 2
City of Laguna Hills | Mayor | Non-HFTD | See Appendix 2
City of Laguna Hills | Public Works Director | Non-HFTD | See Appendix 2
City of Laguna Niguel | Chief of Police Services | Tier-2 | See Appendix 2
City of Laguna Niguel | City Clerk | Tier-2 | See Appendix 2
City of Laguna Niguel | City Manager | Tier-2 | See Appendix 2
City of Laguna Niguel | Community Development Director/Planning Director | Tier-2 | See Appendix 2
City of Laguna Niguel | Councilmember | Tier-2 | See Appendix 2
City of Laguna Niguel | Councilmember | Tier-2 | See Appendix 2
City of Laguna Niguel | Councilmember | Tier-2 | See Appendix 2
City of Laguna Niguel | Councilmember | Tier-2 | See Appendix 2
City of Laguna Niguel | Mayor | Tier-2 | See Appendix 2
City of Laguna Niguel | Public Works Director | Tier-2 | See Appendix 2
City of Lemon Grove | Assistant City Manager/Public Works Director/Superintendent | Non-HFTD | See Appendix 2
City of Lemon Grove | City Manager | Non-HFTD | See Appendix 2
City of Lemon Grove | Councilmember | Non-HFTD | See Appendix 2
City of Lemon Grove | Councilmember | Non-HFTD | See Appendix 2
City of Lemon Grove | Councilmember | Non-HFTD | See Appendix 2
City of Lemon Grove | Mayor | Non-HFTD | See Appendix 2
City of Mission Viejo | CEO | Tier-2 | See Appendix 2
City of Mission Viejo | City Attorney | Tier-2 | See Appendix 2
City of Mission Viejo | City Clerk/Director of Community Relations | Tier-2 | See Appendix 2
City of Mission Viejo | City Engineer | Tier-2 | See Appendix 2
City of Mission Viejo | City Manager | Tier-2 | See Appendix 2
City of Mission Viejo | Councilmember | Tier-2 | See Appendix 2
City of Mission Viejo | Councilmember | Tier-2 | See Appendix 2
City of Mission Viejo | Councilmember | Tier-2 | See Appendix 2
City of Mission Viejo | Councilmember | Tier-2 | See Appendix 2
City of Mission Viejo | Dir of Community Dvlpmnt | Tier-2 | See Appendix 2
City of Mission Viejo | Director of Finance | Tier-2 | See Appendix 2
City of Mission Viejo | Director of Public Works | Tier-2 | See Appendix 2
City of Mission Viejo | Emergency Manager | Tier-2 | See Appendix 2
City of Mission Viejo | Exec Asst to City Manager | Tier-2 | See Appendix 2
City of Mission Viejo | Mayor | Tier-2 | See Appendix 2
City of National City | Assistant City Manager | Non-HFTD | See Appendix 2
City of National City | City Manager | Non-HFTD | See Appendix 2
City of National City | City Manager | Non-HFTD | See Appendix 2
City of National City | Councilmember | Non-HFTD | See Appendix 2
City of National City | Councilmember | Non-HFTD | See Appendix 2
City of National City | Councilmember | Non-HFTD | See Appendix 2
City of National City | Councilmember | Non-HFTD | See Appendix 2
City of National City | Emergency Manager | Non-HFTD | See Appendix 2
City of National City | Mayor | Non-HFTD | See Appendix 2
City of National City | Public Works & Engineering Director | Non-HFTD | See Appendix 2
City of Oceanside | Assistant City Manager | Tier-2 | See Appendix 2
City of Oceanside | Battalion Chief | Tier-2 | See Appendix 2
City of Oceanside | City Manager | Tier-2 | See Appendix 2
City of Oceanside | Communications | Tier-2 | See Appendix 2
City of Oceanside | Councilmember | Tier-2 | See Appendix 2
City of Oceanside | Councilmember | Tier-2 | See Appendix 2
City of Oceanside | Councilmember | Tier-2 | See Appendix 2
City of Oceanside | Councilmember | Tier-2 | See Appendix 2
City of Oceanside | Mayor | Tier-2 | See Appendix 2
City of Poway | Assistant City Manager | Tier-3¦Tier-2 | See Appendix 2
City of Poway | Assistant Director of Public Works for Utilities | Tier-3¦Tier-2 | See Appendix 2
City of Poway | City Manager | Tier-3¦Tier-2 | See Appendix 2
City of Poway | Councilmember | Tier-3¦Tier-2 | See Appendix 2
City of Poway | Councilmember | Tier-3¦Tier-2 | See Appendix 2
City of Poway | Councilmember | Tier-3¦Tier-2 | See Appendix 2
City of Poway | Councilmember | Tier-3¦Tier-2 | See Appendix 2
City of Poway | Director of Public Works | Tier-3¦Tier-2 | See Appendix 2
City of Poway | Emergency Preparedness Coordinator | Tier-3¦Tier-2 | See Appendix 2
City of Poway | Fire Chief | Tier-3¦Tier-2 | See Appendix 2
City of Poway | Mayor | Tier-3¦Tier-2 | See Appendix 2
City of Poway | Public Works | Tier-3¦Tier-2 | See Appendix 2
City of Poway | Public Works | Tier-3¦Tier-2 | See Appendix 2
City of Poway | Public Works | Tier-3¦Tier-2 | See Appendix 2
City of Poway | Public Works Operations Manager | Tier-3¦Tier-2 | See Appendix 2
City of Poway | Wastewater Utilities Supervisor | Tier-3¦Tier-2 | See Appendix 2
City of Rancho Santa Margarita | City Clerk | Tier-2 | See Appendix 2
City of Rancho Santa Margarita | City Engineer/Director of Public Works | Tier-2 | See Appendix 2
City of Rancho Santa Margarita | City Manager | Tier-2 | See Appendix 2
City of Rancho Santa Margarita | Councilmember | Tier-2 | See Appendix 2
City of Rancho Santa Margarita | Councilmember | Tier-2 | See Appendix 2
City of Rancho Santa Margarita | Councilmember | Tier-2 | See Appendix 2
City of Rancho Santa Margarita | Councilmember | Tier-2 | See Appendix 2
City of Rancho Santa Margarita | Director of Finance | Tier-2 | See Appendix 2
City of Rancho Santa Margarita | Director of Planning | Tier-2 | See Appendix 2
City of Rancho Santa Margarita | Mayor | Tier-2 | See Appendix 2
City of Rancho Santa Margarita | PIO - Emergency Manager | Tier-2 | See Appendix 2
City of Rancho Santa Margarita | Principal Engineer | Tier-2 | See Appendix 2
City of Rancho Santa Margarita | Public Works Director/City Engineer | Tier-2 | See Appendix 2
City of Rancho Santa Margarita | Traffic Engineer | Tier-2 | See Appendix 2
City of San Clemente | CEO | Tier-2 | See Appendix 2
City of San Clemente | City Clerk | Tier-2 | See Appendix 2
City of San Clemente | City Clerk | Tier-2 | See Appendix 2
City of San Clemente | City Manager | Tier-2 | See Appendix 2
City of San Clemente | City Treasurer | Tier-2 | See Appendix 2
City of San Clemente | Councilmember | Tier-2 | See Appendix 2
City of San Clemente | Councilmember | Tier-2 | See Appendix 2
City of San Clemente | Councilmember | Tier-2 | See Appendix 2
City of San Clemente | Councilmember | Tier-2 | See Appendix 2
City of San Clemente | Director - Community Development | Tier-2 | See Appendix 2
City of San Clemente | Electrician | Tier-2 | See Appendix 2
City of San Clemente | Emergency Manager | Tier-2 | See Appendix 2
City of San Clemente | Maintenance Manager | Tier-2 | See Appendix 2
City of San Clemente | Mayor | Tier-2 | See Appendix 2
City of San Diego Office of Emergency Services | Emergency Management | Tier-2¦Tier-3 | See Appendix 2
City of San Diego Office of Emergency Services | Interim Program Manager | Tier-2¦Tier-3 | See Appendix 2
City of San Diego Water Department | Manager | Tier-2¦Tier-3 | See Appendix 2
City of San Diego Water Department | Manager | Tier-2¦Tier-3 | See Appendix 2
City of San Diego Water Department | Manager | Tier-2¦Tier-3 | See Appendix 2
City of San Diego | Active Transportation & Infrastructure Commitee Consultant | Tier-2¦Tier-3 | See Appendix 2
City of San Diego | Assistant Director of Development Services Department | Tier-2¦Tier-3 | See Appendix 2
City of San Diego | CFO | Tier-2¦Tier-3 | See Appendix 2
City of San Diego | Chief Building Official, Deputy Director | Tier-2¦Tier-3 | See Appendix 2
City of San Diego | Chief Deputy Engineer | Tier-2¦Tier-3 | See Appendix 2
City of San Diego | Chief Deputy Engineer - Secondary | Tier-2¦Tier-3 | See Appendix 2
City of San Diego | Chief of Staff | Tier-2¦Tier-3 | See Appendix 2
City of San Diego | Chief of Staff - District 8 | Tier-2¦Tier-3 | See Appendix 2
City of San Diego | Chief of Staff District 1 | Tier-2¦Tier-3 | See Appendix 2
City of San Diego | Chief of Staff District 3 | Tier-2¦Tier-3 | See Appendix 2
City of San Diego | Chief of Staff District 5 | Tier-2¦Tier-3 | See Appendix 2
City of San Diego | Chief of Staff District 6 | Tier-2¦Tier-3 | See Appendix 2
City of San Diego | Chief of Staff District 7 | Tier-2¦Tier-3 | See Appendix 2
City of San Diego | Chief of Staff District 9 | Tier-2¦Tier-3 | See Appendix 2
City of San Diego | CIO Performance + Analytics | Tier-2¦Tier-3 | See Appendix 2
City of San Diego | COO | Tier-2¦Tier-3 | See Appendix 2
City of San Diego | Councilmember | Tier-2¦Tier-3 | See Appendix 2
City of San Diego | Councilmember | Tier-2¦Tier-3 | See Appendix 2
City of San Diego | Councilmember | Tier-2¦Tier-3 | See Appendix 2
City of San Diego | Councilmember | Tier-2¦Tier-3 | See Appendix 2
City of San Diego | Councilmember | Tier-2¦Tier-3 | See Appendix 2
City of San Diego | Councilmember | Tier-2¦Tier-3 | See Appendix 2
City of San Diego | Councilmember | Tier-2¦Tier-3 | See Appendix 2
City of San Diego | Councilmember | Tier-2¦Tier-3 | See Appendix 2
City of San Diego | DCOO | Tier-2¦Tier-3 | See Appendix 2
City of San Diego | Deputy Chief of Staff | Tier-2¦Tier-3 | See Appendix 2
City of San Diego | Deputy Chief of Staff District 3 | Tier-2¦Tier-3 | See Appendix 2
City of San Diego | Deputy COO, General Services | Tier-2¦Tier-3 | See Appendix 2
City of San Diego | Deputy COO, Infrastructure and Public Works | Tier-2¦Tier-3 | See Appendix 2
City of San Diego | Deputy Director of Sustainability and Mobility Department | Tier-2¦Tier-3 | See Appendix 2
City of San Diego | Deputy Director Public Works / Chief Deputy Engineer - Tertiary | Tier-2¦Tier-3 | See Appendix 2
City of San Diego | Development Services Department, Director | Tier-2¦Tier-3 | See Appendix 2
City of San Diego | Director of Communications | Tier-2¦Tier-3 | See Appendix 2
City of San Diego | Director of Policy | Tier-2¦Tier-3 | See Appendix 2
City of San Diego | Economic Development Director, Office of the Mayor | Tier-2¦Tier-3 | See Appendix 2
City of San Diego | Emergency Services Program Coordinator | Tier-2¦Tier-3 | See Appendix 2
City of San Diego | Energy Policy and Council Affairs Manager | Tier-2¦Tier-3 | See Appendix 2
City of San Diego | Executive Assistant | Tier-2¦Tier-3 | See Appendix 2
City of San Diego | Fire Chief | Tier-2¦Tier-3 | See Appendix 2
City of San Diego | Interim Deputy Director | Tier-2¦Tier-3 | See Appendix 2
City of San Diego | Land Use and Housing Committee Consultant | Tier-2¦Tier-3 | See Appendix 2
City of San Diego | Mayor | Tier-2¦Tier-3 | See Appendix 2
City of San Diego | Police Chief | Tier-2¦Tier-3 | See Appendix 2
City of San Diego | Public Utilities Department, Director | Tier-2¦Tier-3 | See Appendix 2
City of San Diego | Rules Committe Consultant | Tier-2¦Tier-3 | See Appendix 2
City of San Diego | Rules Committee Consultant | Tier-2¦Tier-3 | See Appendix 2
City of San Diego | Strategic Capital Projects | Tier-2¦Tier-3 | See Appendix 2
City of San Diego | Strategic Energy Initiatives Manager | Tier-2¦Tier-3 | See Appendix 2
City of San Juan Capistrano | CFO/ Finance Director | Tier-2 | See Appendix 2
City of San Juan Capistrano | City Clerk | Tier-2 | See Appendix 2
City of San Juan Capistrano | City Manager | Tier-2 | See Appendix 2
City of San Juan Capistrano | Councilmember | Tier-2 | See Appendix 2
City of San Juan Capistrano | Councilmember | Tier-2 | See Appendix 2
City of San Juan Capistrano | Councilmember | Tier-2 | See Appendix 2
City of San Juan Capistrano | Councilmember | Tier-2 | See Appendix 2
City of San Juan Capistrano | Director of Public Works | Tier-2 | See Appendix 2
City of San Juan Capistrano | Director of Utilites/ Public Works | Tier-2 | See Appendix 2
City of San Juan Capistrano | Emergency Management Consultant | Tier-2 | See Appendix 2
City of San Juan Capistrano | Emergency Operations Center Manager - Tertiary | Tier-2 | See Appendix 2
City of San Juan Capistrano | HR/Risk Manager | Tier-2 | See Appendix 2
City of San Juan Capistrano | Mayor | Tier-2 | See Appendix 2
City of San Juan Capistrano | Senior Management Analyst | Tier-2 | See Appendix 2
City of San Marcos | City Manager | Tier-2 | See Appendix 2
City of San Marcos | Councilmember | Tier-2 | See Appendix 2
City of San Marcos | Councilmember | Tier-2 | See Appendix 2
City of San Marcos | Councilmember | Tier-2 | See Appendix 2
City of San Marcos | Councilmember | Tier-2 | See Appendix 2
City of San Marcos | Mayor | Tier-2 | See Appendix 2
City of San Marcos | Public Information officer | Tier-2 | See Appendix 2
City of Santee | City Manager | Tier-3¦Tier-2 | See Appendix 2
City of Santee | Councilmember | Tier-3¦Tier-2 | See Appendix 2
City of Santee | Councilmember | Tier-3¦Tier-2 | See Appendix 2
City of Santee | Councilmember | Tier-3¦Tier-2 | See Appendix 2
City of Santee | Councilmember | Tier-3¦Tier-2 | See Appendix 2
City of Santee | Fire Captain | Tier-3¦Tier-2 | See Appendix 2
City of Santee | Fire Chief | Tier-3¦Tier-2 | See Appendix 2
City of Santee | Marketing Manager | Tier-3¦Tier-2 | See Appendix 2
City of Santee | Mayor | Tier-3¦Tier-2 | See Appendix 2
City of Solana Beach | Asst. City Manager | Non-HFTD | See Appendix 2
City of Solana Beach | City Manager | Non-HFTD | See Appendix 2
City of Solana Beach | Councilmember | Non-HFTD | See Appendix 2
City of Solana Beach | Councilmember | Non-HFTD | See Appendix 2
City of Solana Beach | Councilmember | Non-HFTD | See Appendix 2
City of Solana Beach | Deputy Mayor | Non-HFTD | See Appendix 2
City of Solana Beach | Management Analyst/Emerg Coordinator | Non-HFTD | See Appendix 2
City of Solana Beach | Mayor | Non-HFTD | See Appendix 2
City of Vista | Asst. City Manager | Non-HFTD¦Tier-2 | See Appendix 2
City of Vista | City Manager | Non-HFTD¦Tier-2 | See Appendix 2
City of Vista | Communications Officer | Non-HFTD¦Tier-2 | See Appendix 2
City of Vista | Councilmember | Non-HFTD¦Tier-2 | See Appendix 2
City of Vista | Councilmember | Non-HFTD¦Tier-2 | See Appendix 2
City of Vista | Councilmember | Non-HFTD¦Tier-2 | See Appendix 2
City of Vista | Councilmember | Non-HFTD¦Tier-2 | See Appendix 2
City of Vista | Deputy Chief | Non-HFTD¦Tier-2 | See Appendix 2
City of Vista | Emergency Manager | Non-HFTD¦Tier-2 | See Appendix 2
City of Vista | Mayor | Non-HFTD¦Tier-2 | See Appendix 2
City of Vista | Public Works Director | Non-HFTD¦Tier-2 | See Appendix 2
Clean Energy Alliance | Board Secretary | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Clean Energy Alliance | CEO | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Clean Energy Alliance | Key Accounts Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Clean Energy Alliance | Local Affairs Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Clean Energy Alliance | Procurement Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Clean Energy Alliance | Regulatory Analyst | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Coronado Fire Department | Division Chief Emergency Manager / Fire Prevention | Non-HFTD | See Appendix 2
Coronado Fire Department | Fire Chief | Non-HFTD | See Appendix 2
Coronado Police Department | Captain | Non-HFTD | See Appendix 2
Coronado Police Department | Dispatcher | Non-HFTD | See Appendix 2
Coronado Police Department | Interim Chief of Police | Non-HFTD | See Appendix 2
County of Orange | Chief of Staff | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
County of Orange | Deputy Chief of Staff | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
County of San Diego Office of Emergency Services | Back Up Duty Officer | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
County of San Diego Office of Emergency Services | Emergency Management Coordinator | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
County of San Diego Office of Emergency Services | Emergency Management Coordinator | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
County of San Diego Office of Emergency Services | Emergency Services | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
County of San Diego Office of Emergency Services | Emergency Services Coordinator | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
County of San Diego Office of Emergency Services | Staff Duty Officer | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
County of San Diego | Acting LUEG Deputy CAO | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
County of San Diego | Assessor/Recorder/County Clerk | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
County of San Diego | Chief Administrative Officer | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
County of San Diego | Chief of County Operations | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
County of San Diego | Chief of County Operations | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
County of San Diego | Chief of Energy and Sustainability | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
County of San Diego | Chief of Staff | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
County of San Diego | Chief of Staff | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
County of San Diego | Chief of Staff | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
County of San Diego | Chief of Staff - District 4 | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
County of San Diego | Chief of Staff District 1 | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
County of San Diego | Chief of Staff District 2 | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
County of San Diego | Chief of Staff District 4 | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
County of San Diego | Chief of Staff/Senior Policy Advisor | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
County of San Diego | County of San Diego | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
County of San Diego | County Supervisor | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
County of San Diego | Deputy Chief Administrative Officer | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
County of San Diego | Director of Policy - D2 | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
County of San Diego | EMS Coordinator, PHPR | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
County of San Diego | General Services | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
County of San Diego | GIS Analyst | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
County of San Diego | Group Program Manager, LUEG | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
County of San Diego | Media & Public Relations | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
County of San Diego | Parks & Recreation | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
County of San Diego | Policy Advisor / Community Liason | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
County of San Diego | Policy Aide | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
County of San Diego | Program Coordinator | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
County of San Diego | Public Works | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
County of San Diego | Supervisor | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
County of San Diego | Supervisor | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
County of San Diego | Supervisor | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
County of San Diego | Supervisor | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
County of San Diego | Supervisor | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
County of San Diego | Supportive Services Program Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Cox Communications | Business Continuity Specialist | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Cox Communications | Communications Security | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Cox Communications | Cox Communications | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Cox Communications | Director | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Cox Communications | Director | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Cox Communications | Director, State Regulatory Affairs | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Cox Communications | Engineer | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Cox Communications | Field Operations Supervisor | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Cox Communications | Network Operations | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Cox Communications | Network Operations Supervisor | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Cox Communications | Sr. Director - Energy, Carbon & Innovation | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Cox Communications | Supervisor | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Cox Communications | Supervisor, Network Engineering | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
CPUC | CPUC - Requested to be added for workshops | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
CUEA | Executive Director | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Deer Springs Fire Protection District | Chief | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Deer Springs Fire Protection District | District Administrator | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Deer Springs Fire Protection District | Fire Captain | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Deer Springs Fire Protection District | Firefighter | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Deer Springs Fire Protection District | President | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Descanso Community Water District | Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Descanso Community Water District | Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
El Cajon Police Department | Captain | Tier-2 | See Appendix 2
El Cajon Police Department | Lieutenant | Tier-2 | See Appendix 2
El Cajon Police Department | Lieutenant | Tier-2 | See Appendix 2
Encina Waste Water Authority | Chief Plant Operator/Director of Operations - Tertiary | Non-HFTD¦Tier-2¦Tier-3 | See Appendix 2
Encina Waste Water Authority | Director of Operations | Non-HFTD¦Tier-2¦Tier-3 | See Appendix 2
Encina Waste Water Authority | Manager/Director of Operations - Secondary | Non-HFTD¦Tier-2¦Tier-3 | See Appendix 2
Encinitas Fire Department | Battalion Chief | Tier-2 | See Appendix 2
Encinitas Fire Department | Deputy Fire Chief | Tier-2 | See Appendix 2
Encinitas Fire Department | Management Analyst | Tier-2 | See Appendix 2
Engineering and Capital Projects Department | Director and City Engineer | Tier-2¦Tier-3 | See Appendix 2
Escondido Fire Department | Emergency Manager | Tier-3¦Tier-2 | See Appendix 2
Escondido Police and Fire Communications | Communications Officer | Tier-3¦Tier-2 | See Appendix 2
Escondido Police and Fire Communications | Executive Assistant | Tier-3¦Tier-2 | See Appendix 2
Escondido Police and Fire Communications | Public Safety Manager | Tier-3¦Tier-2 | See Appendix 2
Ewiiaapaayp Band of Kumeyaay Indians | CEO | Tier-3¦Tier-2¦Zone-1 | See Appendix 2
Ewiiaapaayp Band of Kumeyaay Indians | Director | Tier-3¦Tier-2¦Zone-1 | See Appendix 2
Ewiiaapaayp Band of Kumeyaay Indians | Vice Chairman | Tier-3¦Tier-2¦Zone-1 | See Appendix 2
FACT (Facilitating Access to Coordinated Transportation) | Mobility Coordinator | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
FACT (Facilitating Access to Coordinated Transportation) | Mobility Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Fallbrook Public Utility District | Field Services Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Fallbrook Public Utility District | Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Fallbrook Public Utility District | NA | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Fallbrook Public Utility District | Public Works Director | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Fallbrook Public Utility District | Safety Officer | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Fallbrook Public Utility District | Supervisor | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Fallbrook Public Utility District | System Operator | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Fallbrook Public Utility District | System Operator - Secondary | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Family Health Centers San Diego | APM. Manager- Facilities Operations | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Family Health Centers San Diego | Associate Project Manager, Construction Projects/Facility Services | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Family Health Centers San Diego | Manager of Construction | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Family Health Centers San Diego | Manager of Facilities - Operations | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Family Health Centers San Diego | NA | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Family Health Centers San Diego | Vice President of Physical Facilities | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Harrison Park Mutual Water | Rep | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Harrison Park Mutual Water | Rep | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Heartland Communications | Dispatch Supervisor | Non-HFTD¦Tier-2 | See Appendix 2
Heartland Communications | Dispatcher | Non-HFTD¦Tier-2 | See Appendix 2
Heartland Communications | Heartland Fire | Non-HFTD¦Tier-2 | See Appendix 2
Heartland Communications | Operations Manager | Non-HFTD¦Tier-2 | See Appendix 2
Heartland Fire | Division Chief | Non-HFTD¦Tier-2 | See Appendix 2
Heartland Fire | Emergency Manager - El Cajon, La Mesa, Lemon Grove | Non-HFTD¦Tier-2 | See Appendix 2
Heartland Fire | Fire Chief | Non-HFTD¦Tier-2 | See Appendix 2
Helix Water District | Helix Water District | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Helix Water District | Water Treatment Plant Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Iipay Nation of Santa Ysabel | Chairman | Tier-3¦Tier-2¦Zone-1 | See Appendix 2
Iipay Nation of Santa Ysabel | Director of Operations | Tier-3¦Tier-2¦Zone-1 | See Appendix 2
Iipay Nation of Santa Ysabel | Environmental Director | Tier-3¦Tier-2¦Zone-1 | See Appendix 2
Iipay Nation of Santa Ysabel | Tribal Enterprise | Tier-3¦Tier-2¦Zone-1 | See Appendix 2
Imperial Beach Fire Department | Assistant Fire Marshall | Non-HFTD | See Appendix 2
Imperial Beach Fire Department | Fire Captain/Paramedic | Non-HFTD | See Appendix 2
Inaja-Cosmit Band of Indians | Administrative Assistant | Tier-3 | See Appendix 2
Inaja-Cosmit Band of Indians | Vice Chairwoman | Tier-3 | See Appendix 2
Indian Health Council | Board Member | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Indian Health Council | Chief Executive Officer | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Indian Health Council | Chief Operating Officer | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Indian Health Council | Director | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Jacumba Community Service District | Jacumba Community Service District | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Jacumba Community Service District | Rep | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Jamul Indian Village A Kumeyaay Nation | Chairwoman | Tier-3 | See Appendix 2
Jamul Indian Village A Kumeyaay Nation | Environmental Director | Tier-3 | See Appendix 2
Julian Community Service District | Julian Community Service District | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Julian Community Service District | Rep | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Kaiser Permanente | Area information Officer | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Kaiser Permanente | Director, Facilities - SMMC & North County Clinics | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Kaiser Permanente | Director, Facilities – SDMC & Central County Clinics | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Kaiser Permanente | Director, Facilities – ZMC & South County Clinics | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Kaiser Permanente | Executive Director | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Kaiser Permanente | Manager, Facilities - East County Clinics | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
La Jolla Band of Luiseño Indians | Chairwoman | Tier-3 | See Appendix 2
La Jolla Band of Luiseño Indians | Councilman | Tier-3 | See Appendix 2
La Jolla Band of Luiseño Indians | Environmental Director | Tier-3 | See Appendix 2
La Jolla Band of Luiseño Indians | Operations | Tier-3 | See Appendix 2
La Jolla Band of Luiseño Indians | Tribal Fire Chief | Tier-3 | See Appendix 2
La Jolla Band of Luiseño Indians | Vice Chairman | Tier-3 | See Appendix 2
La Posta Band of Mission Indians | Councilman | Tier-3¦Zone-1 | See Appendix 2
La Posta Band of Mission Indians | Councilwoman | Tier-3¦Zone-1 | See Appendix 2
La Posta Band of Mission Indians | Councilwoman | Tier-3¦Zone-1 | See Appendix 2
La Posta Band of Mission Indians | Emergency Mitigation Specialist | Tier-3¦Zone-1 | See Appendix 2
La Posta Band of Mission Indians | Vice Chairman | Tier-3¦Zone-1 | See Appendix 2
Laguna Niguel Police Services | Chief | Tier-2 | See Appendix 2
Laguna Niguel Police Services | Sr. Emergency Management Program Coordinator | Tier-2 | See Appendix 2
Lakeside Fire Protection District | Fire Chief | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Lakeside Water District | General Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Lakeside Water District | Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Leucadia Wastewater Water District | Supervisor | Tier-3¦Tier-2 | See Appendix 2
Leucadia Wastewater Water District | Supervisor | Tier-3¦Tier-2 | See Appendix 2
Los Coyotes Band of Indians | Chairman | Tier-2¦Zone-1 | See Appendix 2
Los Coyotes Band of Indians | Environmental Director | Tier-2¦Zone-1 | See Appendix 2
Los Coyotes Band of Indians | Executive Council Member | Tier-2¦Zone-1 | See Appendix 2
Los Coyotes Band of Indians | Executive Council Member | Tier-2¦Zone-1 | See Appendix 2
Los Coyotes Band of Indians | Executive Council Member | Tier-2¦Zone-1 | See Appendix 2
Los Tules Mutual Water Company | Water System Supervisor | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Manzanita Band of the Kumeyaay Nation | Administrator | Tier-3¦Tier-2 | See Appendix 2
Manzanita Band of the Kumeyaay Nation | Chairwoman | Tier-3¦Tier-2 | See Appendix 2
Manzanita Band of the Kumeyaay Nation | Environmental Director | Tier-3¦Tier-2 | See Appendix 2
Manzanita Band of the Kumeyaay Nation | Executive Council Member | Tier-3¦Tier-2 | See Appendix 2
Mesa Grande Band of Mission Indians | Chairman | Tier-3¦Zone-1 | See Appendix 2
Mesa Grande Band of Mission Indians | Councilman | Tier-3¦Zone-1 | See Appendix 2
Mesa Grande Band of Mission Indians | Vice Chairman | Tier-3¦Zone-1 | See Appendix 2
Metropolitan Water District of Southern California | Duty Officer | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Metropolitan Water District of Southern California | Jacumba Community Service District | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Metropolitan Water District of Southern California | Metropolitan Water District EOC | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Mission Hospital Laguna Beach | Manager Facilities, Engineering | Tier-2 | See Appendix 2
Mission Hospital Mission Viejo | Director Facilities Services | Tier-2 | See Appendix 2
Mission Hospital Mission Viejo | Facilities Manager - Mission Viejo | Tier-2 | See Appendix 2
Mission Hospital Mission Viejo | Office Coordination, Safety and Security | Tier-2 | See Appendix 2
Monte Vista Fire Dispatch Center | Dispatch Supervisor | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Moulton Niguel Water District | Director of Operations | Non-HFTD¦Tier-2¦Zone-1 | See Appendix 2
Moulton Niguel Water District | GIS Analyst | Non-HFTD¦Tier-2¦Zone-1 | See Appendix 2
Moulton Niguel Water District | Information Systems Officer | Non-HFTD¦Tier-2¦Zone-1 | See Appendix 2
Moulton Niguel Water District | Moulton Niguel MWD | Non-HFTD¦Tier-2¦Zone-1 | See Appendix 2
Municipal Water District of Orange County | Director | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Municipal Water District of Orange County | Director of Emergency Management | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Municipal Water District of Orange County | Director of Emergency Management | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Municipal Water District of Orange County | Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Naval Base Coronado | Duty Officer | Non-HFTD¦Tier-2¦Tier-3 | See Appendix 2
Naval Base Coronado | Emergency Management | Non-HFTD¦Tier-2¦Tier-3 | See Appendix 2
Naval Base Coronado | Emergency Management Specialist | Non-HFTD¦Tier-2¦Tier-3 | See Appendix 2
Naval Base Coronado | Naval Base Coronado Emergency Operations Center | Non-HFTD¦Tier-2¦Tier-3 | See Appendix 2
Navy Region Southwest | Deputy Director for Emergency Management | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
North County Dispatch Center | Dispatch Supervisor | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
North County Dispatch Center | Operations Division Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
North County Fire Protection District | Deputy Fire Chief | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
North County Fire Protection District | Fire Chief | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Oceanside Fire Department | Fire Chief | Tier-2 | See Appendix 2
Oceanside Police Department | Police Chief | Tier-2 | See Appendix 2
Office of Representative Darrell Issa | Chief of Staff | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Office of Representative Juan Vargas | Chief of Staff | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Office of Representative Mike Levin | Chief of Staff | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Office of Representative Sara Jacobs | Chief of Staff | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Office of Representative Sara Jacobs | Military and Veterans Liaison/Community Representative | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Office of Representative Sara Jacobs | Staff Assistant | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Office of Representative Scott Peters | Chief of Staff | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Office of Senator Catherine Blakespear | District Representative | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Olivenhain Municipal Water District | Assistant General Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Olivenhain Municipal Water District | Olivenhain MWD | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Olivenhain Municipal Water District | Operations | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Olivenhain Municipal Water District | Operations Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Olivenhain Municipal Water District | Water System Supervisor | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Orange County Board of Supervisors | Supervisor 1st District | Non-HFTD¦Tier-2¦Zone-1 | See Appendix 2
Orange County Board of Supervisors | Supervisor 2nd District | Non-HFTD¦Tier-2¦Zone-1 | See Appendix 2
Orange County Board of Supervisors | Supervisor 3rd District | Non-HFTD¦Tier-2¦Zone-1 | See Appendix 2
Orange County Board of Supervisors | Supervisor 4th District | Non-HFTD¦Tier-2¦Zone-1 | See Appendix 2
Orange County Board of Supervisors | Supervisor 5th District | Non-HFTD¦Tier-2¦Zone-1 | See Appendix 2
Orange County Fire Authority | Director of Communications | Non-HFTD¦Tier-2¦Zone-1 | See Appendix 2
Orange County Fire Authority | Fire Chief | Non-HFTD¦Tier-2¦Zone-1 | See Appendix 2
Orange County OES | Office of Emergency Management | Non-HFTD¦Tier-2¦Zone-1 | See Appendix 2
Orange County Sheriff's Department | Senior Emergency Management Coordinator | Non-HFTD¦Tier-2¦Zone-1 | See Appendix 2
Orange County Sheriff's Department | Sergeant | Non-HFTD¦Tier-2¦Zone-1 | See Appendix 2
Orange County Sheriff's Department | Sergeant | Non-HFTD¦Tier-2¦Zone-1 | See Appendix 2
Orange County United Way, 2-1-1 Orange County | Contact Center Manager | Non-HFTD¦Tier-2¦Zone-1 | See Appendix 2
Orange County United Way, 2-1-1 Orange County | Duty Officer | Non-HFTD¦Tier-2¦Zone-1 | See Appendix 2
Orange County United Way, 2-1-1 Orange County | Sr. Program Manager | Non-HFTD¦Tier-2¦Zone-1 | See Appendix 2
Otay Water District | Chief of Water Operations | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Otay Water District | Lead Water System Operator | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Otay Water District | Otay Water District | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Otay Water District | Supervisor | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Otay Water District | Utility Maintenance Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Padre Dam Municipal Water District | Maintenance Supervisor | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Padre Dam Municipal Water District | NULL | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Padre Dam Municipal Water District | NULL | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Padre Dam Municipal Water District | Padre Dam MWD | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Padre Dam Municipal Water District | Systems Operator | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Pala Band of Mission Indians | Chairman | Tier-3¦Tier-2 | See Appendix 2
Pala Band of Mission Indians | Chief | Tier-3¦Tier-2 | See Appendix 2
Pala Band of Mission Indians | Environmental Director | Tier-3¦Tier-2 | See Appendix 2
Pala Band of Mission Indians | Fire Chief | Tier-3¦Tier-2 | See Appendix 2
Pala Band of Mission Indians | IT Director | Tier-3¦Tier-2 | See Appendix 2
Pala Band of Mission Indians | Public Safety Director | Tier-3¦Tier-2 | See Appendix 2
Pala Band of Mission Indians | Utility Department | Tier-3¦Tier-2 | See Appendix 2
Pala Band of Mission Indians | Veterans Program Director | Tier-3¦Tier-2 | See Appendix 2
Pala Band of Mission Indians | Vice Chair | Tier-3¦Tier-2 | See Appendix 2
Palomar Health San Marcos Medical Office | Emergency Management and Safety Coordinator | Tier-2 | See Appendix 2
Palomar Health | Emergency Management | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Palomar Health | Sr. Director/Facility Operations | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Palomar Medical Center Escondido | Emergency Mgmt and Safety Specialist, Disaster Preparedness | Tier-3¦Tier-2 | See Appendix 2
Palomar Medical Center Escondido | PMC Escondido Facility Manager | Tier-3¦Tier-2 | See Appendix 2
Palomar Medical Center Poway | PMC Poway Facility Manager | Tier-3¦Tier-2 | See Appendix 2
Palomar Mountain Water District | Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Paradise Valley Hospital | Director, Plant Operations | Non-HFTD | See Appendix 2
Paradise Valley Hospital | Plant Services Director/Paradise Village | Non-HFTD | See Appendix 2
Paradise Valley Hospital | Plant Services Engineering | Non-HFTD | See Appendix 2
Pauma Band of Luiseño Indians | Chairman | Tier-3¦Tier-2¦Zone-1 | See Appendix 2
Pauma Band of Luiseño Indians | Controller | Tier-3¦Tier-2¦Zone-1 | See Appendix 2
Pauma Band of Luiseño Indians | Fire Chief | Tier-3¦Tier-2¦Zone-1 | See Appendix 2
Pauma Band of Luiseño Indians | Tribal Administrator | Tier-3¦Tier-2¦Zone-1 | See Appendix 2
Pechanga Band of Indians | Utilities Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Pine Valley Mutual Water Company | Rep | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Port of San Diego Harbor Police Department | Harbor Port Dispatch | Tier-2¦Tier-3 | See Appendix 2
Port of San Diego Harbor Police Department | Harbor Port Dispatch | Tier-2¦Tier-3 | See Appendix 2
Port of San Diego Harbor Police Department | Lead Public Safety Dispatcher | Tier-2¦Tier-3 | See Appendix 2
Port of San Diego Harbor Police Department | Port Security Manager | Tier-2¦Tier-3 | See Appendix 2
Port of San Diego | Emergency Manager | Tier-2¦Tier-3 | See Appendix 2
Rady Children's Hospital San Diego | Admin Assoc | Tier-2¦Tier-3 | See Appendix 2
Rady Children's Hospital San Diego | Business Unit Coordinator/Plant Operations & Maintenance | Tier-2¦Tier-3 | See Appendix 2
Rady Children's Hospital San Diego | Sr Director Plant Operations | Tier-2¦Tier-3 | See Appendix 2
Rady Children's Hospital San Diego | Sr. Director Plant Operations and Maintenance | Tier-2¦Tier-3 | See Appendix 2
Rady Children's Hospital | Assoc Chief Operating Officer | Tier-2¦Tier-3 | See Appendix 2
Rainbow Municipal Water District | Chief Operating Officer | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Rainbow Municipal Water District | NA | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Rainbow Municipal Water District | NA | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Rainbow Municipal Water District | Operations Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Rainbow Municipal Water District | Rainbow MWD | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Ramona Municipal Water District | General Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Ramona Municipal Water District | Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Ramona Municipal Water District | Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Ramona Municipal Water District | Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Ramona Municipal Water District | Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Ramona Municipal Water District | Supervisor | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Ramona Municipal Water District | Utilities Supervisor | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Rancho Pauma Mutual Water Company | Consultant | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Rancho Pauma Mutual Water Company | Rep | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Rancho Pauma Mutual Water Company | Rep | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Rancho Pauma Mutual Water Company | Rep | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Rancho Pauma Mutual Water Company | Rep | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Rancho Pauma Mutual Water Company | Rep | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Rancho Santa Fe Assn. | Rancho Santa Fe Assn. | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Rancho Santa Fe Assn. | Rancho Santa Fe Assn. | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Rancho Santa Fe Assn. | Rancho Santa Fe Association Mgr | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Rancho Santa Teresa Water | Rep | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Rincon Band of Luiseño Indians | Chairman | Tier-3¦Tier-2 | See Appendix 2
Rincon Band of Luiseño Indians | Council | Tier-3¦Tier-2 | See Appendix 2
Rincon Band of Luiseño Indians | Council | Tier-3¦Tier-2 | See Appendix 2
Rincon Band of Luiseño Indians | Council | Tier-3¦Tier-2 | See Appendix 2
Rincon Band of Luiseño Indians | Environmental Director | Tier-3¦Tier-2 | See Appendix 2
Rincon Band of Luiseño Indians | Fire Chief | Tier-3¦Tier-2 | See Appendix 2
Rincon Band of Luiseño Indians | Group Emergency Email | Tier-3¦Tier-2 | See Appendix 2
Rincon Band of Luiseño Indians | Housing Manager | Tier-3¦Tier-2 | See Appendix 2
Rincon Band of Luiseño Indians | Public Safety Director | Tier-3¦Tier-2 | See Appendix 2
Rincon Band of Luiseño Indians | Public Safety Manager | Tier-3¦Tier-2 | See Appendix 2
Rincon Band of Luiseño Indians | Public Works Manager | Tier-3¦Tier-2 | See Appendix 2
Rincon Band of Luiseño Indians | Vice Chair | Tier-3¦Tier-2 | See Appendix 2
Rincon Del Diablo Municipal Water District | Consultant | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Rincon Del Diablo Municipal Water District | Supervisor | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Rincon Del Diablo Municipal Water District | Supervisor | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Rincon Del Diablo Municipal Water District | Water System Supervisor | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Rincon Del Diablo Municipal Water District | Water System Supervisor | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Saddleback College | Chief of Police | Tier-2 | See Appendix 2
San Diego Community Power | Account Services Analyst | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
San Diego Community Power | Director of Data Analytics & Account Services | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
San Diego Community Power | Director of Power Services | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
San Diego Community Power | Director of Programs | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
San Diego Community Power | Director of Public Affairs | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
San Diego Community Power | Key Accounts/Program Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
San Diego Community Power | Key Accounts/Program Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
San Diego Community Power | Senior Account Services Analyst | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
San Diego Community Power | Senior Manager of Strategic Partnerships | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
San Diego Community Power | Senior Marketing & Communications Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
San Diego County Regional Airport Authority | Emergency Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
San Diego County Regional Airport Authority | Emergency Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
San Diego County Sheriff's Department | Dispatch Supervisor | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
San Diego County Sheriff's Department | Emergency Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
San Diego County Sheriff's Department | Emergency Planning Detail | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
San Diego County Sheriff's Department | Emergency Planning Detail | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
San Diego County Sheriff's Department | Emergency Planning Detail | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
San Diego County Sheriff's Department | Emergency Services | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
San Diego County Water Authority | 24/7 Control Desk | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
San Diego County Water Authority | Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
San Diego County Water Authority | Principal Engineer | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
San Diego County Water Authority | Risk and Safety Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
San Diego County Water Authority | System Operator | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
San Diego Fire Rescue | Chief | Tier-2¦Tier-3 | See Appendix 2
San Diego Fire Rescue | On-Duty Fire Dispatch Supervisor | Tier-2¦Tier-3 | See Appendix 2
San Diego Fire Rescue | San Diego Fire Department | Tier-2¦Tier-3 | See Appendix 2
San Diego Fire Rescue | SDFD Duty Command BC | Tier-2¦Tier-3 | See Appendix 2
San Diego Fire Rescue | Unknown | Tier-2¦Tier-3 | See Appendix 2
San Diego Law Enforcement Coordination Center | Exercise Program Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
San Diego Police Department | Dispatch Administrator | Tier-2¦Tier-3 | See Appendix 2
San Diego Zoo Wildlife Alliance - Safari Park | Associate Director, Operations | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
San Diego Zoo Wildlife Alliance - Safari Park | Director of Facilities | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
San Diego Zoo Wildlife Alliance - Safari Park | Executive Director, SVP Wildlife Alliance | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
San Diego Zoo Wildlife Alliance - Safari Park | Unknown | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
San Diego Zoo Wildlife Alliance - Safari Park | VP and Deputy Director, San Diego Safari Park | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
San Elijo Joint Powers Authority | Director | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
San Elijo Joint Powers Authority | Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
San Elijo Joint Powers Authority | Systems Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
San Marcos Fire Department | Battalion Chief | Tier-2 | See Appendix 2
San Marcos Fire Department | Division Chief | Tier-2 | See Appendix 2
San Marcos Fire Department | Emergency Manager | Tier-2 | See Appendix 2
San Marcos Fire Department | Fire Chief | Tier-2 | See Appendix 2
San Marcos Fire Department | Fire Chief - Secondary | Tier-2 | See Appendix 2
San Marcos Fire Department | Fire Chief - Tertiary | Tier-2 | See Appendix 2
San Marcos Fire Department | On Duty Battalion Chief | Tier-2 | See Appendix 2
San Pasqual Band of Mission Indians | Chairman | Tier-3¦Zone-1 | See Appendix 2
San Pasqual Band of Mission Indians | Chief of Police | Tier-3¦Zone-1 | See Appendix 2
San Pasqual Band of Mission Indians | Environmental Director | Tier-3¦Zone-1 | See Appendix 2
San Pasqual Band of Mission Indians | Fire Chief | Tier-3¦Zone-1 | See Appendix 2
San Pasqual Band of Mission Indians | Sergeant | Tier-3¦Zone-1 | See Appendix 2
San Pasqual Band of Mission Indians | Utilities Manager | Tier-3¦Zone-1 | See Appendix 2
Santa Fe Irrigation District | Chief Operator | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Santa Fe Irrigation District | NA | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Santa Fe Irrigation District | Operations and Maintenance Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Santa Fe Irrigation District | Safety Coordinator | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Santa Fe Irrigation District | Santa Fe Irrigation District | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Santa Fe Irrigation District | Water Treatment Plant Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Santa Margarita Water District | Duty Officer | Tier-2¦Zone-1 | See Appendix 2
Santa Margarita Water District | Manager | Tier-2¦Zone-1 | See Appendix 2
Santa Margarita Water District | Manager | Tier-2¦Zone-1 | See Appendix 2
Santa Margarita Water District | Manager | Tier-2¦Zone-1 | See Appendix 2
Santa Margarita Water District | Manager | Tier-2¦Zone-1 | See Appendix 2
Santa Margarita Water District | Operator | Tier-2¦Zone-1 | See Appendix 2
Santa Margarita Water District | Safety Officer | Tier-2¦Zone-1 | See Appendix 2
Santa Margarita Water District | Superintendent, Field Ops | Tier-2¦Zone-1 | See Appendix 2
Santa Margarita Water District | Utilities Manager | Tier-2¦Zone-1 | See Appendix 2
Santa Margarita Water District | Water System Supervisor | Tier-2¦Zone-1 | See Appendix 2
Scripps Health | Corporate Safety Officer/EM Corporate | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Scripps Health | Corporate VP, Facilities and Support | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Scripps Health | Energy Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Scripps Health | Engineering Operations Director | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Scripps Health | Engineering Supervisor | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Scripps Health | Manager Data Center Operations/Data Center Outage | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Scripps Health | NA | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Scripps Health | Sr. Director, Facilities/Support Operations | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
SDG&E | AFN Liaison | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
SDG&E | CRC Support | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
SDG&E | Customer Outreach & Eng. Supv. | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
SDG&E | Director of Tribal Affairs | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
SDG&E | Liaisons Officer | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
SDG&E | Partner Portal Support Contact Email | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
SDG&E | SDG&E CCA Strategy & Policy Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
SDG&E | SDG&E Director - Emergency Management | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
SDG&E | SDG&E Emergency Services Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
SDG&E | SDG&E EOC Documentation Unit DL | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
SDG&E | SDG&E Internal | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
SDG&E | SDG&E Internal | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
SDG&E | SDG&E Public Affairs Team DL | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
SDG&E | Sr. Tribal Affairs Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
SDG&E | VP Customer Services | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Sharp Healthcare | Chief Engineer | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Sharp Healthcare | Chief Engineer | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Sharp Healthcare | Director of Engineering (Sharp Chula Vista) | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Sharp Healthcare | Director of Engineering at Sharp Metropolitan Hospital | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Sharp Healthcare | Director of Engineering for Sharp Coronado Hospital | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Sharp Healthcare | Engineering Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Sharp Healthcare | FMD/Program Coord | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Sharp Healthcare | Interim Chief Engineer/Plant, Operations and Maintenance | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Sharp Healthcare | Plant Operations and Maintenance Director/Sodexo at Sharp Grossmont Hospital | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Sharp Healthcare | Power Plant Lead | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
South Coast Water District | Manager | Tier-2 | See Appendix 2
South Coast Water District | Manager | Tier-2 | See Appendix 2
South Orange County Water Authority | Chief Plant Operator | Non-HFTD¦Tier-2¦Zone-1 | See Appendix 2
South Orange County Water Authority | Director | Non-HFTD¦Tier-2¦Zone-1 | See Appendix 2
South Orange County Water Authority | Manager | Non-HFTD¦Tier-2¦Zone-1 | See Appendix 2
South Orange County Water Authority | Manager | Non-HFTD¦Tier-2¦Zone-1 | See Appendix 2
Southern Indian Health Council | Director of Facilities | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Southern Indian Health Council | Indian Health Council | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Southern Indian Health Council | Safety Coordinator | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Southern Indian Health Council | Southern Indian Health Council | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Southern Indian Health Council | Southern Indian Health Council (COO) | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California Department of Water Resources | Principal Engineer | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California Department of Water Resources | Risk Management | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | Assemblymember | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | Assemblymember | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | Assemblymember | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | Assemblymember | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | Assemblymember | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | Assemblymember | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | Assemblymember, AD 75 | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | Assemblymember, AD 76 | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | Assemblymember, AD 79 | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | Capitol Chief of Staff | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | Capitol Chief of Staff | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | Capitol Chief of Staff | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | Capitol Chief of Staff | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | Capitol Chief of Staff | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | Capitol Chief of Staff | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | Capitol Director | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | Capitol Director | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | Chief of Staff | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | Chief of Staff | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | Chief of Staff | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | Chief of Staff | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | Chief of Staff | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | Chief of Staff | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | Chief of Staff - AD 77 | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | Chief of Staff - Asmbly. Laurie Davies | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | Chief of Staff - Toni Atkins | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | Chief of Staff, AD | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | Chief of Staff, AD 75 | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | Chief of Staff, AD 79 | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | Chief of Staff, SD 39 | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | Communications Director | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | District Communications Director | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | District Director | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | District Director | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | District Director | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | District Director | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | District Director | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | District Director | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | District Director | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | District Director | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | District Director - SD40 | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | District Mgr - SD39 | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | District Representative | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | Executive Assistant - S18 | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | Legislative Aide | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | Legislative Director | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | Legislative Director | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | Representative 18th State Senate District | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | SCHEDULER | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | Senator | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | Senator | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | Senator | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | Senator | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | Senator | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | Senator | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | Senator | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | Senator, SD 37 | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | Senator, SD39 | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | Sr Field Rep - SD 36 | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | Staff - Asmbly. Laurie Davies | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
State of California | Staff - Asmbly. Laurie Davies | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Sweetwater Water Authority | Director, Water Quality | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Sweetwater Water Authority | Engineering Tech & Supervisor | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Sweetwater Water Authority | Plant Maintenance Supervisor | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Sweetwater Water Authority | Program Specialist | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Sweetwater Water Authority | Supervisor | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Sweetwater Water Authority | Sweetwater Water Authority | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Sweetwater Water Authority | Water Quality Laboratory Supervisor | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Sweetwater Water Authority | Water Treatment Plant Operator Supervisor | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Sweetwater Water Authority | Watershed Caretaker | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Sycuan Band of the Kumeyaay Nation | Battalion Chief | Tier-3¦Tier-2¦Zone-1 | See Appendix 2
Sycuan Band of the Kumeyaay Nation | Chairman | Tier-3¦Tier-2¦Zone-1 | See Appendix 2
Sycuan Band of the Kumeyaay Nation | Chief Administrative Officer | Tier-3¦Tier-2¦Zone-1 | See Appendix 2
Sycuan Band of the Kumeyaay Nation | Chief of Police | Tier-3¦Tier-2¦Zone-1 | See Appendix 2
Sycuan Band of the Kumeyaay Nation | Distribution List - Facilities | Tier-3¦Tier-2¦Zone-1 | See Appendix 2
Sycuan Band of the Kumeyaay Nation | Fire Chief | Tier-3¦Tier-2¦Zone-1 | See Appendix 2
Sycuan Band of the Kumeyaay Nation | Planning & Development Manager | Tier-3¦Tier-2¦Zone-1 | See Appendix 2
Sycuan Band of the Kumeyaay Nation | Planning & Development Manager | Tier-3¦Tier-2¦Zone-1 | See Appendix 2
T-Mobile/Sprint | Engineering Operations Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
T-Mobile/Sprint | Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
T-Mobile/Sprint | Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
T-Mobile/Sprint | Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
T-Mobile/Sprint | Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
T-Mobile/Sprint | Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
T-Mobile/Sprint | Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
T-Mobile/Sprint | Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
T-Mobile/Sprint | Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
T-Mobile/Sprint | Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
T-Mobile/Sprint | Senior Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
T-Mobile/Sprint | Sprint | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
T-Mobile/Sprint | T-Mobile | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
T-Mobile/Sprint | T-Mobile | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
T-Mobile/Sprint | T-Mobile | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Tri-City Medical Center | Director of Facilities | Tier-2 | See Appendix 2
Tri-City Medical Center | Engineering Supervisor | Tier-2 | See Appendix 2
Tri-City Medical Center | Facilities Manager | Tier-2 | See Appendix 2
Tri-City Medical Center | NA | Tier-2 | See Appendix 2
Tri-City Medical Center | Plant Supervisor | Tier-2 | See Appendix 2
VA Medical Ctr | Assistant Chief, Engineering | Tier-2¦Tier-3 | See Appendix 2
VA Medical Ctr | Chief Maintenance Engineer | Tier-2¦Tier-3 | See Appendix 2
VA Medical Ctr | Healthcare Engineer | Tier-2¦Tier-3 | See Appendix 2
VA Medical Ctr | Project Engineer | Tier-2¦Tier-3 | See Appendix 2
VA Medical Ctr | Utilities Supervisor of Engineering | Tier-2¦Tier-3 | See Appendix 2
VA Medical Ctr | VA Hospital | Tier-2¦Tier-3 | See Appendix 2
Vallecitos Water District | Operations and Maintenance Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Vallecitos Water District | PIO | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Vallecitos Water District | Vallecitos Water District | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Vallecitos Water District | Water System Supervisor | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Valley Center Municipal Water District | Sr Techician | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Valley Center Municipal Water District | Valley Center Municipal Water District | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Verizon Wireless | Network Operations | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Verizon Wireless | Network Operations | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Verizon Wireless | Sr. Manager - Network Operations | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Verizon Wireless | Sr. Manager - Network Operations | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Verizon Wireless | Verizon Wireless | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Verizon Wireless | Verizon Wireless | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Verizon Wireless | Verizon Wireless | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Viejas Band of Kumeyaay Indians | Chairman | Tier-3 | See Appendix 2
Viejas Band of Kumeyaay Indians | Councilman | Tier-3 | See Appendix 2
Viejas Band of Kumeyaay Indians | Resource Manager Director | Tier-3 | See Appendix 2
Viejas Band of Kumeyaay Indians | Resource Project Officer | Tier-3 | See Appendix 2
Viejas Band of Kumeyaay Indians | Secretary | Tier-3 | See Appendix 2
Viejas Band of Kumeyaay Indians | Vice Chairman | Tier-3 | See Appendix 2
Vista Fire Department | Fire Chief | Non-HFTD¦Tier-2 | See Appendix 2
Vista Irrigation District | Director of Water Resources | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Vista Irrigation District | Director of Water Resources - Secondary | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Vista Irrigation District | Engineering Specialist | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Vista Irrigation District | Vista Irrigation District | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Vista Irrigation District | Water Distribution Supervisor | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Vista Irrigation District | Water Resource Supervisor/Director of Water Resources - Tertiary | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
West Cuca Mutual Water Company | Rep | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
West Cuca Mutual Water Company | Rep | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
West Cuca Mutual Water Company | Rep | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Yuima Municipal Water District | Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Yuima Municipal Water District | Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2
Yuima Municipal Water District | Manager | Non-HFTD¦Tier-2¦Tier-3¦Zone-1 | See Appendix 2

## Table 7.1
Section 6 – Local and State Public Safety Partner Engagement
Table 7.1 Entity List
Entity Name | Type
Alpine Union School District | Critical Facilities and Infrastructure
American Tower Corporation | Critical Facilities and Infrastructure & Public Safety Partner
Barona Band of Mission Indians | Critical Facilities and Infrastructure & Public Safety Partner
Bonsall Unified School District | Critical Facilities and Infrastructure
Borrego Springs Unified School District | Critical Facilities and Infrastructure
Borrego Water District | Critical Facilities and Infrastructure & Public Safety Partner
Cajon Valley Union School District | Critical Facilities and Infrastructure
Caltrans | Critical Facilities and Infrastructure & Public Safety Partner
Campo Band of Kumeyaay Indians | Critical Facilities and Infrastructure & Public Safety Partner
Charter Communications | Critical Facilities and Infrastructure & Public Safety Partner
City of Imperial Beach | Critical Facilities and Infrastructure & Public Safety Partner
City of Lemon Grove | Critical Facilities and Infrastructure & Public Safety Partner
City of Oceanside | Critical Facilities and Infrastructure & Public Safety Partner
City of Poway | Critical Facilities and Infrastructure & Public Safety Partner
City of San Diego | Critical Facilities and Infrastructure & Public Safety Partner
City of San Marcos | Critical Facilities and Infrastructure & Public Safety Partner
City of Santee | Critical Facilities and Infrastructure & Public Safety Partner
County of San Diego | Critical Facilities and Infrastructure & Public Safety Partner
Cox Communications | Critical Facilities and Infrastructure & Public Safety Partner
Dehesa School District | Critical Facilities and Infrastructure
Escondido Union High School District | Critical Facilities and Infrastructure
Escondido Union School District | Critical Facilities and Infrastructure
Ewiiaapaayp Band of Kumeyaay Indians | Critical Facilities and Infrastructure & Public Safety Partner
Fallbrook Public Utility District | Critical Facilities and Infrastructure & Public Safety Partner
Fallbrook Union School District | Critical Facilities and Infrastructure
Federal Aviation Administration | Critical Facilities and Infrastructure & Public Safety Partner
Fortistar | Critical Facilities and Infrastructure
General Services Administration | Critical Facilities and Infrastructure
Julian Union High School District | Critical Facilities and Infrastructure
Julian Union School District | Critical Facilities and Infrastructure
Kumeyaay Wind LLC | Critical Facilities and Infrastructure
La Jolla Band of Luiseno Indians | Critical Facilities and Infrastructure & Public Safety Partner
La Posta Band of Mission Indians | Critical Facilities and Infrastructure & Public Safety Partner
Lakeside Union School District | Critical Facilities and Infrastructure
Level 3 Communications | Critical Facilities and Infrastructure & Public Safety Partner
Los Coyotes Band of Cahuilla and Cupeño Indians | Critical Facilities and Infrastructure & Public Safety Partner
MAAC Project | Critical Facilities and Infrastructure
Manzanita Band of the Kumeyaay Nation | Critical Facilities and Infrastructure & Public Safety Partner
Mesa Grande Band of Diegueño Mission Indians | Critical Facilities and Infrastructure & Public Safety Partner
Mountain Empire Unified School District | Critical Facilities and Infrastructure
North County Transit District | Critical Facilities and Infrastructure & Public Safety Partner
NRG Energy | Critical Facilities and Infrastructure
Olivenhain Municipal Water District | Critical Facilities and Infrastructure & Public Safety Partner
Orange Grove Energy | Critical Facilities and Infrastructure
Otay Water District | Critical Facilities and Infrastructure & Public Safety Partner
Padre Dam Municipal Water District | Critical Facilities and Infrastructure & Public Safety Partner
Pala Band of Mission Indians | Critical Facilities and Infrastructure & Public Safety Partner
Palomar Community College | Critical Facilities and Infrastructure
Pauma Band of Luiseno Indians | Critical Facilities and Infrastructure & Public Safety Partner
Poway Unified School District | Critical Facilities and Infrastructure
Rainbow Municipal Water District | Critical Facilities and Infrastructure & Public Safety Partner
Ramona Municipal Water District | Critical Facilities and Infrastructure & Public Safety Partner
Ramona Unified School District | Critical Facilities and Infrastructure
Rancho Santa Fe School District | Critical Facilities and Infrastructure
Rincon Band of Luiseño Indians | Critical Facilities and Infrastructure & Public Safety Partner
Rincon del Diablo Municipal Water District | Critical Facilities and Infrastructure & Public Safety Partner
San Diego County Office of Education | Critical Facilities and Infrastructure & Public Safety Partner
San Diego County Water Authority | Critical Facilities and Infrastructure & Public Safety Partner
San Diego State University | Critical Facilities and Infrastructure
San Diego Zoo Wildlife Alliance | Critical Facilities and Infrastructure
San Dieguito Water District | Critical Facilities and Infrastructure & Public Safety Partner
San Marcos Unified School District | Critical Facilities and Infrastructure
San Pasqual Band of Mission Indians | Critical Facilities and Infrastructure & Public Safety Partner
San Pasqual Union School District | Critical Facilities and Infrastructure
Santa Fe Irrigation District | Critical Facilities and Infrastructure & Public Safety Partner
Santa Margarita Water District | Critical Facilities and Infrastructure & Public Safety Partner
Santee School District | Critical Facilities and Infrastructure
Southern California Tribal Chairman Association | Critical Facilities and Infrastructure & Public Safety Partner
Southern Indian Health Council | Critical Facilities and Infrastructure & Public Safety Partner
Spencer Valley School | Critical Facilities and Infrastructure
State of California | Critical Facilities and Infrastructure & Public Safety Partner
Sweetwater Authority | Critical Facilities and Infrastructure & Public Safety Partner
Sycuan Band of the Kumeyaay Nation | Critical Facilities and Infrastructure & Public Safety Partner
Tegna Inc - CBS News 8 | Critical Facilities and Infrastructure
T-Mobile | Critical Facilities and Infrastructure & Public Safety Partner
U.S. Customs and Border Protection | Critical Facilities and Infrastructure & Public Safety Partner
U.S. Department of Agriculture Forest Service | Critical Facilities and Infrastructure & Public Safety Partner
U.S. Marine Corps - Marine Corps Base Camp Pendleton | Critical Facilities and Infrastructure
U.S. Navy - Naval Special Warfare Command | Critical Facilities and Infrastructure
University of California San Diego | Critical Facilities and Infrastructure
Vallecitos School District | Critical Facilities and Infrastructure
Vallecitos Water District | Critical Facilities and Infrastructure & Public Safety Partner
Valley Center Municipal Water District | Critical Facilities and Infrastructure & Public Safety Partner
Valley Center-Pauma Unified School District | Critical Facilities and Infrastructure
Verizon Wireless | Critical Facilities and Infrastructure & Public Safety Partner
Viejas Band of Kumeyaay Indians | Critical Facilities and Infrastructure & Public Safety Partner
Vista Irrigation District | Critical Facilities and Infrastructure & Public Safety Partner
Warner Unified School District | Critical Facilities and Infrastructure
YMCA of San Diego County | Critical Facilities and Infrastructure
Yuima Municipal Water District | Critical Facilities and Infrastructure & Public Safety Partner

## Table 8
Public Safety Power Shutoff Post-Event Report: JANUARY 20 – JANUARY 24, 2025
Appendix 5: PSPS Event Data Workbook
Table 8: Services Provides to Customers with AFN
Type of Service | Number Provided
Accessible Transportation Trips | 2
Over Night Hotel Stays (AFN) | 62
Over Night Hotel Stays (non-AFN) | 8
Food Support Meals Provided | 4875
Generators Provided | 68
$50 Gift Cards distributed | 7
211 calls received for PSPS Information & Referral | 123

## Table 9
Public Safety Power Shutoff Post-Event Report: JANUARY 20 – JANUARY 24, 2025
Appendix 5: PSPS Event Data Workbook
Table 9: Backup Power – Description, Capacity and Estimated Maximum Duration
Location | # of Gens or Batteries | Type of Backup Power | Generator/ Battery Size | Maximum Duration of Operation | Actual PSPS Operation Status
CRC - Borrego Springs Library, 2580 Country Club Rd., CA 92004 | 1 | Generator | 250 kVA | Generators can run indefinitely, based on fuel supply | 01/23/2025 13:00 PDT - 01/24/2025 09:51 PDT
CRC - Lake Morena, 29765 Oak Drive, Campo CA 91906 | 1 | Generator | 125 kVA | Generators can run indefinitely, based on fuel supply | 01/20/2025 21:47 PDT - 01/24/2025 11:07 PDT
CRC - Potrero, 24550 Hwy 94, Potrero, CA 91963 | 1 | Generator | 70 kVA | Generators can run indefinitely, based on fuel supply | 01/20/2025 18:55 PDT - 01/22/2025 09:30 PDT, 01/23/2025 05:35 PDT - 01/24/2025 11:00 PDT
CRC - Pine Valley, 28890 Old Hwy 80, Pine Valley, CA 91962 | 1 | Generator | 70 kVA | Generators can run indefinitely, based on fuel supply | 01/20/2025 20:00 PDT - 01/24/2025 12:55 PDT
CRC - Whispering Winds Catholic Camp Resource Center Building, 17606 Harrison Park Rd., Julian, CA 92036 | 1 | Generator | 125 kVA | Generators can run indefinitely, based on fuel supply | 01/20/2025 19:50 PDT - 01/24/2025 10:55 PDT
CRC - Whispering Winds Catholic Camp Pump Station, 17606 Harrison Park Rd., Julian, CA 92036 | 1 | Generator | 70 kVA | Generators can run indefinitely, based on fuel supply | 01/20/2025 20:05 PDT - 01/24/2025 10:55 PDT
CRC - Boulevard, 39223 CA-94, Boulevard, CA 91905 | 1 | Generator | 70 kVA | Generators can run indefinitely, based on fuel supply | 01/20/2025 20:33 PDT - 01/24/2025 11:50 PDT
CRC - Dulzura, 1136 Community Building Rd., Dulzura, CA 91917 | 1 | Generator | 70 kVA | Generators can run indefinitely, based on fuel supply | 01/23/2025 13:25 PDT - 01/24/2025 08:45 PDT
CRC Fallbrook Library, 124 S. Mission Rd., Fallbrook, CA 92028 | 1 | Generator | 125 kVA | Generators can run indefinitely, based on fuel supply | Stand-By
CRC - Valley Center, 29200 Cole Grade Rd., Valley Center, CA 92082 | 1 | Generator | 125 kVA | Generators can run indefinitely, based on fuel supply | Stand-By
CRC - Ramona, 1275 Main St., Ramona, CA 92065 | 1 | Generator | 70 kVA | Generators can run indefinitely, based on fuel supply | Stand-By
Downtown Julian, 1901 4th St., Julian, CA 92036 | 1 | Generator | 1 MVA | Generators can run indefinitely, based on fuel supply | Stand-By
Shelter Valley, 7878 Great Southern Overland Stage Route, Julian, CA 92036 | 3 | Generator | 3-300 kVA | Generators can run indefinitely, based on fuel supply | 01/21/2025 00:07 PDT - 01/23/2025 18:47 PDT
Butterfield Ranch, 14926 Great Southern Overland Stage Route, Julian, CA 92036 | 3 | Generator | 3-300 kVA | Generators can run indefinitely, based on fuel supply | 01/21/2025 01:02 PDT - 01/23/2025 20:20 PDT
Cameron Corners, 1339 Buckman Springs Rd., Campo, CA 91906 | 2 | Generator | 2-300 kVA | Generators can run indefinitely, based on fuel supply | 01/21/2025 04:04 PDT - 01/24/2025 12:03 PDT
Ramona Air Attack Base, 2498 Montecito Rd., Ramona, CA 92065 | 1 | Battery | 500 kW/2 MWh | 3-days | Stand-By
Mountain Empire High School Cafeteria, 3305 Buckman Springs, Rd., Pine Valley, CA 91962 | 2 | Generator | 2-650 kVA | Generators can run indefinitely, based on fuel supply | 01/20/2025 19:40 PDT - 01/24/2025 17:53 PDT
Mountain Empire High School, 3305 Buckman Springs, Rd., Pine Valley, CA 91962 | 1 | Generator | 70 kVA | Generators can run indefinitely, based on fuel supply | 01/20/2025 20:50 PDT - 01/24/2025 16:55 PDT
Mountain Empire High School, 3305 Buckman Springs, Rd., Pine Valley, CA 91962 | 1 | Generator | 320 kVA | Generators can run indefinitely, based on fuel supply | 01/20/2025 20:50 PDT - 01/24/2025 14:25 PDT
Mountain Empire High School, 3305 Buckman Springs, Rd., Pine Valley, CA 91962 | 1 | Generator | 70 kVA | Generators can run indefinitely, based on fuel supply | 01/20/2025 18:00 PDT - 01/24/2025 14:20 PDT
Stone Ridge Estates, 35109 Highway 79, Warner Springs, CA 92086 | 1 | Generator | 1.8 MVA | Generators can run indefinitely, based on fuel supply | 01/20/2025 11:09 PDT - 01/24/2025 16:05 PDT
Campo Tribal Hall, 36190 Church Rd., Campo, CA 91906 | 1 | Generator | 40 kVA | Generators can run indefinitely, based on fuel supply | 01/20/2025 23:11 PDT - 01/24/2025 12:45 PDT
Golden Acorn Casino, 1800 Golden Acorn Wy., Campo, CA 91906 | 3 | Generator | 3-70 kVA | Generators can run indefinitely, based on fuel supply | 01/21/2025 10:30 PDT - 01/25/2025 08:00 PDT
La Posta Emergency Center, 8 Crestwood Rd., Boulevard, CA 91905 | 1 | Generator | 70 kVA | Generators can run indefinitely, based on fuel supply | 01/20/2025 14:20 PDT - 01/24/2025 13:35 PDT
Live Oaks Market, 37820 Old Hwy 80, Boulevard, CA 91905 | 1 | Generator | 70 kVA | Generators can run indefinitely, based on fuel supply | 01/20/2025 08:48 PDT - 01/24/2025 12:15 PDT
Mountain Top Market, 39710 Old Hwy 80, Boulevard, CA 91905 | 1 | Generator | 70 kVA | Generators can run indefinitely, based on fuel supply | 01/20/2025 20:15 PDT - 01/24/2025 12:00 PDT
X L Co Gas Station, 525 Palm Canyon Dr., Borrego Springs, CA 92004 | 1 | Generator | 70 kVA | Generators can run indefinitely, based on fuel supply | 01/23/2025 13:45 PDT - 01/24/2025 09:00 PDT
DG Market, 872 Palm Canyon Dr., Borrego Springs, CA 92004 | 1 | Generator | 200 kVA | Generators can run indefinitely, based on fuel supply | 01/23/2025 12:45 PDT - 01/24/2025 09:55 PDT
Borrego Springs Youth and Seniors Center, Inc., 580 Circle J Dr., Borrego Springs, CA 92004 | 1 | Generator | 300 kVA | Generators can run indefinitely, based on fuel supply | 01/23/2025 12:50 PDT - 01/24/2025 10:15 PDT
Borrego Springs Resort, 1112 Tilting T Dr., Borrego Springs, CA 92004 | 1 | Generator | 300 kVA | Generators can run indefinitely, based on fuel supply | 01/23/2025 12:49 PDT - 01/24/2025 09:51 PDT
La Casa Del Zorro Resort, 03845 Yaqui Pass Rd., Borrego Springs, CA 92004 | 1 | Generator | 300 kVA | Generators can run indefinitely, based on fuel supply | 01/23/2025 13:40 PDT - 01/24/2025 09:52 PDT

## Table 10
Public Safety Power Shutoff Post-Event Report: JANUARY 20 – JANUARY 24, 2025
Appendix 5: PSPS Event Data Workbook
Table 10: Community Generator Program Sites
Location | # of Gens or Batteries | Type of Backup Power | Generator/ Battery Size | Maximum Duration of Operation | Actual PSPS Operation Status
Live Oaks Market, 37820 Old Hwy 80, Boulevard, CA 91905 | 1 | Generator | 70 kVA | Generators can run indefinitely, based on fuel supply | 01/20/2025 08:48 PDT - 01/24/2025 12:15 PDT
Mountain Top Market, 39710 Old Hwy 80, Boulevard, CA 91905 | 1 | Generator | 70 kVA | Generators can run indefinitely, based on fuel supply | 01/20/2025 20:15 PDT - 01/24/2025 12:00 PDT
X L Co Gas Station, 525 Palm Canyon Dr., Borrego Springs, CA 92004 | 1 | Generator | 70 kVA | Generators can run indefinitely, based on fuel supply | 01/23/2025 13:45 PDT - 01/24/2025 09:00 PDT
DG Market, 872 Palm Canyon Dr., Borrego Springs, CA 92004 | 1 | Generator | 200 kVA | Generators can run indefinitely, based on fuel supply | 01/23/2025 12:45 PDT - 01/24/2025 09:55 PDT
Borrego Springs Youth and Seniors Center, Inc., 580 Circle J Dr., Borrego Springs, CA 92004 | 1 | Generator | 300 kVA | Generators can run indefinitely, based on fuel supply | 01/23/2025 12:50 PDT - 01/24/2025 10:15 PDT
Borrego Springs Resort, 1112 Tilting T Dr., Borrego Springs, CA 92004 | 1 | Generator | 300 kVA | Generators can run indefinitely, based on fuel supply | 01/23/2025 12:49 PDT - 01/24/2025 09:51 PDT
La Casa Del Zorro Resort, 03845 Yaqui Pass Rd., Borrego Springs, CA 92004 | 1 | Generator | 300 kVA | Generators can run indefinitely, based on fuel supply | 01/23/2025 13:40 PDT - 01/24/2025 09:52 PDT
Mountain Empire High School Cafeteria, 3305 Buckman Springs, Rd., Pine Valley, CA 91962 | 2 | Generator | 2-650 kVA | Generators can run indefinitely, based on fuel supply | 01/20/2025 19:40 PDT - 01/24/2025 17:53 PDT
Mountain Empire High School, 3305 Buckman Springs, Rd., Pine Valley, CA 91962 | 1 | Generator | 70 kVA | Generators can run indefinitely, based on fuel supply | 01/20/2025 20:50 PDT - 01/24/2025 16:55 PDT
Mountain Empire High School, 3305 Buckman Springs, Rd., Pine Valley, CA 91962 | 1 | Generator | 320 kVA | Generators can run indefinitely, based on fuel supply | 01/20/2025 20:50 PDT - 01/24/2025 14:25 PDT
Mountain Empire High School, 3305 Buckman Springs, Rd., Pine Valley, CA 91962 | 1 | Generator | 70kVA | Generators can run indefinitely, based on fuel supply | 01/20/2025 18:00 PDT - 01/24/2025 14:20 PDT
Stone Ridge Estates, 35109 Highway 79, Warner Springs, CA 92086 | 1 | Generator | 1.8 MVA | Generators can run indefinitely, based on fuel supply | 01/20/2025 11:09 PDT - 01/24/2025 16:05 PDT
Campo Tribal Hall, 36190 Church Rd., Campo, CA 91906 | 1 | Generator | 70 kVA | Generators can run indefinitely, based on fuel supply | 01/20/2025 23:11 PDT - 01/24/2025 12:45 PDT
Golden Acorn Casino, 1800 Golden Acorn Wy., Campo, CA 91906 | 3 | Generator | 3-70 kVA | Generators can run indefinitely, based on fuel supply | 01/21/2025 10:30 PDT - 01/25/2025 08:00 PDT
La Posta Emergency Center, 8 Crestwood Rd., Boulevard, CA 91905 | 1 | Generator | 70 kVA | Generators can run indefinitely, based on fuel supply | 01/20/2025 14:20 PDT - 01/24/2025 13:35 PDT

## Table 11
Public Safety Power Shutoff Post-Event Report: JANUARY 20 – JANUARY 24, 2025
Appendix 5: PSPS Event Data Workbook
Table 11: Total Number of Backup Generators and Mobile Batteries
Location | # of Gens or Batteries | Generator/ Battery Size | Fuel Type
CRC - Borrego Springs Library, 2580 Country Club Rd., CA 92004 | 1 | 250 kVA | Diesel
CRC - Lake Morena, 29765 Oak Drive, Campo CA 91906 | 1 | 125 kVA | Diesel
CRC - Potrero, 24550 Hwy 94, Potrero, CA 91963 | 1 | 70 kVA | Diesel
CRC - Pine Valley, 28890 Old Hwy 80, Pine Valley, CA 91962 | 1 | 70 kVA | Diesel
CRC - Whispering Winds Catholic Camp Resource Center Building, 17606 Harrison Park Rd., Julian, CA 92036 | 1 | 125 kVA | Diesel
CRC - Whispering Winds Catholic Camp Pump Station, 17606 Harrison Park Rd., Julian, CA 92036 | 1 | 70 kVA | Diesel
CRC - Boulevard, 39223 CA-94, Boulevard, CA 91905 | 1 | 70 kVA | Diesel
CRC - Dulzura, 1136 Community Building Rd., Dulzura, CA 91917 | 1 | 70 kVA | Diesel
CRC Fallbrook Library, 124 S. Mission Rd., Fallbrook, CA 92028 | 1 | 125 kVA | Diesel
CRC - Valley Center, 29200 Cole Grade Rd., Valley Center, CA 92082 | 1 | 125 kVA | Diesel
CRC - Ramona, 1275 Main St., Ramona, CA 92065 | 1 | 70 kVA | Diesel
Downtown Julian, 1901 4th St., Julian, CA 92036 | 1 | 1 MVA | Diesel
Shelter Valley, 7878 Great Southern Overland Stage Route, Julian, CA 92036 | 3 | 300 kVA | Diesel
Butterfield Ranch, 14926 Great Southern Overland Stage Route, Julian, CA 92036 | 3 | 300 kVA | Diesel
Cameron Corners, 1339 Buckman Springs Rd., Campo, CA 91906 | 2 | 300 kVA | Diesel
Ramona Air Attack Base, 2498 Montecito Rd., Ramona, CA 92065 | 1 | 500 kW/2 MWh | Battery
Mountain Empire High School Cafeteria, 3305 Buckman Springs, Rd., Pine Valley, CA 91962 | 2 | 650 kVA | Diesel
Mountain Empire High School, 3305 Buckman Springs, Rd., Pine Valley, CA 91962 | 1 | 70 kVA | Diesel
Mountain Empire High School, 3305 Buckman Springs, Rd., Pine Valley, CA 91962 | 1 | 320 kVA | Diesel
Mountain Empire High School, 3305 Buckman Springs, Rd., Pine Valley, CA 91962 | 1 | 70 kVA | Diesel
Stone Ridge Estates, 35109 Highway 79, Warner Springs, CA 92086 | 1 | 1.8 MVA | Diesel
Campo Tribal Hall, 36190 Church Rd., Campo, CA 91906 | 1 | 40 kVA | Diesel
Golden Acorn Casino, 1800 Golden Acorn Wy., Campo, CA 91906 | 3 | 70 kVA | Diesel
La Posta Emergency Center, 8 Crestwood Rd., Boulevard, CA 91905 | 1 | 70 kVA | Diesel
Live Oaks Market, 37820 Old Hwy 80, Boulevard, CA 91905 | 1 | 70 kVA | Diesel
Mountain Top Market, 39710 Old Hwy 80, Boulevard, CA 91905 | 1 | 70 kVA | Diesel
X L Co Gas Station, 525 Palm Canyon Dr., Borrego Springs, CA 92004 | 1 | 70 kVA | Diesel
DG Market, 872 Palm Canyon Dr., Borrego Springs, CA 92004 | 1 | 200 kVA | Diesel
Borrego Springs Youth and Seniors Center, Inc., 580 Circle J Dr., Borrego Springs, CA 92004 | 1 | 300 kVA | Diesel
Borrego Springs Resort, 1112 Tilting T Dr., Borrego Springs, CA 92004 | 1 | 300 kVA | Diesel
La Casa Del Zorro Resort, 03845 Yaqui Pass Rd., Borrego Springs, CA 92004 | 1 | 300 kVA | Diesel

## Table 12
Public Safety Power Shutoff Post-Event Report: JANUARY 20 – JANUARY 24, 2025
Appendix 5: PSPS Event Data Workbook
Table 12: Critical Facility and Infrastructure Customers
Location | # of Customers | Critical Facility and Infrastructure Customers
CRC - Borrego Springs Library, 2580 Country Club Rd., CA 92004 | 1 | Community Resource Center
CRC - Lake Morena, 29765 Oak Drive, Campo CA 91906 | 1 | Community Resource Center
CRC - Potrero, 24550 Hwy 94, Potrero, CA 91963 | 1 | Community Resource Center
CRC - Pine Valley, 28890 Old Hwy 80, Pine Valley, CA 91962 | 1 | Community Resource Center
CRC - Whispering Winds Catholic Camp Resource Center Building, 17606 Harrison Park Rd., Julian, CA 92036 | 1 | Community Resource Center
CRC - Whispering Winds Catholic Camp Pump Station, 17606 Harrison Park Rd., Julian, CA 92036 | 1 | Community Resource Center
CRC - Boulevard, 39223 CA-94, Boulevard, CA 91905 | 1 | Community Resource Center
CRC - Dulzura, 1136 Community Building Rd., Dulzura, CA 91917 | 1 | Community Resource Center
CRC Fallbrook Library, 124 S. Mission Rd., Fallbrook, CA 92028 | 1 | Community Resource Center
CRC - Valley Center, 29200 Cole Grade Rd., Valley Center, CA 92082 | 1 | Community Resource Center
CRC - Ramona, 1275 Main St., Ramona, CA 92065 | 1 | Community Resource Center
Downtown Julian, 1901 4th St., Julian, CA 92036 | 124 | • Schools • Food and Markets • Veterinary Hospital • Telecommunications • Postal Service
Shelter Valley, 7878 Great Southern Overland Stage Route, Julian, CA 92036 | 219 | • Stagecoach Trails Campground & RV Park • SD County Fire Station • Library • Water Wells Infrastructure • Sewage Infrastructure
Butterfield Ranch, 14926 Great Southern Overland Stage Route, Julian, CA 92036 | 119 | • Butterfield Manufactured Home & RV Community • Water Wells Infrastructure • Sewage Infrastructure
Cameron Corners, 1339 Buckman Springs Rd., Campo, CA 91906 | 13 | • Cal Fire • ATT Telecom Hub • Library – Cool Zone • San Ysidro Health Center • Schools • Food and Markets • Gas Stations
Ramona Air Attack Base, 2498 Montecito Rd., Ramona, CA 92065 | 2 | • Cal Fire • US Forest Service
Mountain Empire High School, 3305 Buckman Springs, Rd., Pine Valley, CA 91962 | 5 | • Mountain Empire School District food refrigeration and commercial kitchen • School & Childcare for School District
Stone Ridge Estates, 35109 Highway 79, Warner Springs, CA 92086 | 1 | Primary-Metered Senior Residential Community
Campo Tribal Hall, 36190 Church Rd., Campo, CA 91906 | 4 | • Restrooms • Showers • Security Light Tower • Food Service
Golden Acorn Casino, 1800 Golden Acorn Wy., Campo, CA 91906 | 3 | • Lighting • Food Service
La Posta Emergency Center, 8 Crestwood Rd., Boulevard, CA 91905 | 1 | Government and Community Resource Center
Live Oaks Market, 37820 Old Hwy 80, Boulevard, CA 91905 | 1 | • Food and Market • Gas Station
Mountain Top Market, 39710 Old Hwy 80, Boulevard, CA 91905 | 1 | • Food and Market • Gas Station
X L Co Gas Station, 525 Palm Canyon Dr., Borrego Springs, CA 92004 | 1 | Gas Station
DG Market, 872 Palm Canyon Dr., Borrego Springs, CA 92004 | 1 | Grocery Store
Borrego Springs Youth and Seniors Center, Inc., 580 Circle J Dr., Borrego Springs, CA 92004 | 1 | Youth and Senior Center
Borrego Springs Resort, 1112 Tilting T Dr., Borrego Springs, CA 92004 | 1 | • Hotel and Lodging • Cool Zone
La Casa Del Zorro Resort, 03845 Yaqui Pass Rd., Borrego Springs, CA 92004 | 1 | • Hotel and Lodging • Food Refrigeration & Restaurant • Cool Zone

## Table 13
Public Safety Power Shutoff Post-Event Report: JANUARY 20 – JANUARY 24, 2025
Appendix 5: PSPS Event Data Workbook
Table 13: Community Generator Program Sites
Location | # of Customers | Community Generator Program Sites
Mountain Empire High School, 3305 Buckman Springs, Rd., Pine Valley, CA 91962 | 5 | Mountain Empire School District commercial kitchen and child care for the entire school district
Stone Ridge Estates, 35109 Highway 79, Warner Springs, CA 92086 | 1 | Primary-Metered Senior Citizen Residential Community
Campo Tribal Hall, 36190 Church Rd., Campo, CA 91906 | 4 | Restrooms, showers, food service and security lighting
Golden Acorn Casino, 1800 Golden Acorn Wy., Campo, CA 91906 | 3 | Lighting and food service
La Posta Emergency Center, 8 Crestwood Rd., Boulevard, CA 91905 | 1 | Government and Community Resource Center
Live Oaks Market, 37820 Old Hwy 80, Boulevard, CA 91905 | 1 | Local and convenient location for food and fuel in the Boulevard Community
Mountain Top Market, 39710 Old Hwy 80, Boulevard, CA 91905 | 1 | Local and convenient location for food and fuel in the Boulevard Community
X L Co Gas Station, 525 Palm Canyon Dr., Borrego Springs, CA 92004 | 1 | Local and convenient location for fuel in the Borrego Springs Community
DG Market, 872 Palm Canyon Dr., Borrego Springs, CA 92004 | 1 | Local and convenient location for food in the Borrego Springs Community
Borrego Springs Youth and Seniors Center, Inc., 580 Circle J Dr., Borrego Springs, CA 92004 | 1 | Borrego Springs community center
Borrego Springs Resort, 1112 Tilting T Dr., Borrego Springs, CA 92004 | 1 | Borrego Springs hotel/lodging and cool zone
La Casa Del Zorro Resort, 03845 Yaqui Pass Rd., Borrego Springs, CA 92004 | 1 | Borrego Springs hotel/lodging, restuarant and cool zone

## Table 14
Public Safety Power Shutoff Post-Event Report: JANUARY 20 – JANUARY 24, 2025
Appendix 5: PSPS Event Data Workbook
Table 14: Number and Nature of Complaints Received
Nature of Complaint | Number of Complaints
PSPS Frequency/Duration Including, but not limited to complaints regarding the frequency and/or duration of PSPS events, delays in restoring power, scope of PSPS and dynamic of weather conditions | 21
Safety/Health Concern Including, but not limited to complaints regarding difficulties experienced by AFN/MBL populations, traffic accidents due to non-operating traffic lights, inability to get medical help, well water or access to clean water, inability to keep property cool/warm during outage raising health concern | 6
Communications/Notifications Including, but not limited to complaints regarding lack of notice, excessive notices, confusing notice, false alarm notice, problems with getting up-to-date information, inaccurate information provided, not being able to get information in the prevalent languages and/or information accessibility, complaints about website, Public Safety Partner Portal, REST/DAM sites (as applicable) | 9
Outreach/Assistance Including, but not limited to complaints regarding community resource centers, community crew vehicles, backup power, hotel vouchers, other assistance provided by utility to mitigate impact of PSPS | 6
General PSPS Dissatisfaction/Other Including, but not limited to complaints about being without power during PSPS event and related hardships such as food loss, income loss, inability to work/attend school, plus any PSPS-related complaints that do not fall into any other category | 61
Total: | 103

## Table 15
Public Safety Power Shutoff Post-Event Report: JANUARY 20 – JANUARY 24, 2025
Appendix 5: PSPS Event Data Workbook
Table 15: Claims Filed Against SDG&E Due to De-energization
Nature of Claim | Number of Claims
Property Damage | 4
Solar Related | 0
Food Loss | 29
Inconvenience of Being Without Power | 5
Business Loss | 1
Hotel Stays | 0
Generator | 4
Total: | 43

## Table 16
Public Safety Power Shutoff Post-Event Report: JANUARY 20 – JANUARY 24, 2025
Appendix 5: PSPS Event Data Workbook
Table 16: Circuits requiring more than 24 hours to restore
Circuit Name | Reason the Utility was Unable to Restore the Circuit Within 24 Hours
N/A | N/A

## Table 17
Public Safety Power Shutoff Post-Event Report: JANUARY 20 – JANUARY 24, 2025
Appendix 5: PSPS Event Data Workbook
Table 17: Community Resource Centers
# | County | Site Name | Address | Operating Hours | Attendance | Site Type | Amenities Provided
1 | San Diego | Borrego Springs CRC | 2580 Country Club Rd Borrego Springs, CA 92004 | 1/23/2025: 13:20 - 22:00 1/24/2025: 08:00 - 9:50 | 242 | Brick & Mortar | Water, WiFi, Medical Device Charging, Snacks, Phone Charging, Ice, Car Power Inverter, Battery Bank, Emergency Light, and Warming Items
2 | San Diego | Boulevard CRC | 39919 Ribbonwood Rd Boulevard, CA 91905 | 1/20/2025: 08:50 - 22:00 1/21/2025: 08:00 - 22:00 1/22/2025: 08:00 - 22:00 1/23/2025: 08:00 - 22:00 1/24/2025: 08:00 - 13:13 | 1380 | Brick & Mortar | Water, WiFi, Medical Device Charging, Snacks, Phone Charging, Ice, Car Power Inverter, Battery Bank, Emergency Light, Warming Items, Warm Meals, Water Truck, and Warm Showers
3 | San Diego | Descanso CRC | 9545 River Dr Descanso, CA 91916 | 1/20/2025: 08:43 - 22:00 1/21/2025: 08:00 - 22:00 1/22/2025: 08:00 - 22:00 1/23/2025: 08:00 - 22:00 1/24/2025: 08:00 - 13:58 | 289 | Brick & Mortar | Water, WiFi, Medical Device Charging, Snacks, Phone Charging, Ice, Car Power inverter, Battery Bank, Emergency Light, Warming Items, and Water Truck
4 | San Diego | Dulzura CRC | 1136 Community Building Rd Dulzura, CA 91917 | 1/23/2025: 13:36 - 22:00 | 14 | Brick & Mortar | Water, WiFi, Medical Device Charging, Snacks, Phone Charging, Ice, Car Power Inverter, Battery Bank, Emergency Light, and Warming Items
5 | San Diego | Fallbrook CRC | 124 S Mission Rd Fallbrook, CA 92028 | 1/21/2025: 08:00 - 22:00 1/22/2025: 08:00 - 22:00 1/23/2025: 08:00 - 22:00 1/24/2025: 08:00 - 15:05 | 162 | Brick & Mortar | Water, WiFi, Medical Device Charging, Snacks, Phone Charging, Ice, Car Power Inverter, Battery Bank, Emergency Light, and Warming Items
6 | San Diego | Julian CRC | 17606 Harrison Park Rd Julian, CA 92036 | 1/20/2025: 19:25 - 22:00 1/21/2025: 08:00 - 22:00 1/22/2025: 08:00 - 22:00 1/23/2025: 08:00 - 22:00 1/24/2025: 08:00 - 11:43 | 48 | Brick & Mortar | Water, WiFi, Medical Device Charging, Snacks, Phone Charging, Ice, Car Power Inverter, Battery Bank, Emergency Light, Warming Items, and Water Truck
7 | San Diego | Lake Morena CRC | 29765 Oak Dr Campo, CA 91906 | 1/20/2025: 19:49 - 22:00 1/21/2025: 08:00 - 22:00 1/22/2025: 08:00 - 22:00 1/23/2025: 08:00 - 22:00 1/24/2025: 08:00 - 11:51 | 391 | Brick & Mortar | Water, WiFi, Medical Device Charging, Snacks, Phone Charging, Ice, Car Power Inverter, Battery Bank, Emergency Light, Warming Items, and Water Truck
8 | San Diego | Pine Valley CRC | 28890 Old Highway 80 Pine Valley, CA 91962 | 1/20/2025: 19:28 - 22:00 1/21/2025: 08:00 - 22:00 1/22/2025: 08:00 - 22:00 1/23/2025: 08:00 - 22:00 1/24/2025: 08:00 - 13:04 | 483 | Brick & Mortar | Water, WiFi, Medical Device Charging, Snacks, Phone Charging, Ice, Car Power Inverter, Battery Bank, Emergency Light, Warming Items, and Water Truck,
9 | San Diego | Potrero CRC | 24550 Hwy 94 Potrero, CA 91963 | 1/20/2025: 18:58 - 22:00 1/21/2025: 08:00 - 22:00 1/22/2025: 08:00 - 22:00 1/23/2025: 08:00 - 22:00 1/24/2025: 08:00 - 10:43 | 76 | Brick & Mortar | Water, WiFi, Medical Device Charging, Snacks, Phone Charging, Ice, Car Power Inverter, Battery Bank, and Warming Items
10 | San Diego | Ramona CRC | 1275 Main St Ramona, CA 92065 | 1/20/2025: 19:25 - 22:00 1/21/2025: 08:00 - 22:00 1/22/2025: 08:00 - 22:00 1/23/2025: 08:00 - 22:00 1/24/2025: 08:00 - 14:34 | 72 | Brick & Mortar | Water, WiFi, Medical Device Charging, Snacks, Phone Charging, Ice, Car Power Inverter, Battery Bank, Emergency Light, and Warming Items
11 | San Diego | Valley Center CRC | 29200 Cole Grade Rd Valley Center, CA 92082 | 1/20/2025: 18:31 - 22:00 1/21/2025: 08:00 - 22:00 1/22/2025: 08:00 - 22:00 1/23/2025: 08:00 - 22:00 1/24/2025: 08:00 - 15:05 | 189 | Brick & Mortar | Water, WiFi, Medical Device Charging, Snacks, Phone Charging, Ice, Car power inverter, Battery Bank, Emergency Light, and Warming Items
12 | San Diego | Warner Springs CRC | 20950 CA-79 Warner Springs, CA 92086 | 1/20/2025: 11:02 - 22:00 1/21/2025: 08:00 - 22:00 1/22/2025: 08:00 - 22:00 1/23/2025: 08:00 - 22:00 1/24/2025: 08:00 - 16:03 | 168 | Brick & Mortar | Water, WiFi, Medical Device Charging, Snacks, Phone Charging, Ice, Car Power Inverter, Battery Bank, Emergency Light, Warming Items, and Water Truck

## Table 18
Public Safety Power Shutoff Post-Event Report: JANUARY 20 – JANUARY 24, 2025
Appendix 5: PSPS Event Data Workbook
Table 18: Summary of Avoided Customer Impacts
Mitigation Action | Avoided Impacts
Sectionalizing Devices | 15225
Temporary Generation | 200
Microgrids | 353
Permanent Backup Generation | 828
Strategic Undergrounding | 1206
Situational Awareness | 35838
Total: | 53650

## Table 19
Public Safety Power Shutoff Post-Event Report: JANUARY 20 – JANUARY 24, 2025
Appendix 5: PSPS Event Data Workbook
Table 19: Summary of Avoided Customer Impacts by Circuit
Circuit | Avoided Impacts
67 | 587
73 | 1
79 | 12
157 | 370
171 | 6
172 | 3
175 | 196
176 | 60
212 | 1
214 | 1
215 | 1
217 | 1130
220 | 1
221 | 1094
222 | 583
230 | 1
235 | 2136
237 | 1464
240 | 264
242 | 531
286 | 1
288 | 1
350 | 838
351 | 369
352 | 1
353 | 1524
354 | 1268
355 | 1211
356 | 3
357 | 1721
358 | 797
441 | 18
442 | 2
444 | 1
445 | 9
448 | 13
449 | 2
450 | 1611
454 | 2002
470 | 1053
502 | 1
520 | 1929
521 | 1741
523 | 1
524 | 734
540 | 839
542 | 2117
597 | 1415
788 | 2039
840 | 16
907 | 1
908 | 2
970 | 1389
971 | 1097
972 | 2638
973 | 1385
974 | 343
975 | 1565
1001 | 538
1021 | 850
1022 | 136
1030 | 512
1039 | 868
1081 | 1
1090 | 1037
1101 | 614
1106 | 2207
1138 | 906
1215 | 30
1233 | 162
1234 | 2443
1243 | 83
1458 | 1815
235/RA3 | 1
239/RB1 | 1308
Total: | 53650

## Table 20
Public Safety Power Shutoff Post-Event Report: JANUARY 20 – JANUARY 24, 2025
Appendix 5: PSPS Event Data Workbook
Table 20: Summary of Customers Served by Microgrids
Microgrid Location | Total Customers
Shelter Valley, 7878 Great Southern Overland Stage Route, Julian, CA 92036 | 219
Butterfield Ranch, 14926 Great Southern Overland Stage Route, Julian, CA 92036 | 119
Cameron Corners, 1339 Buckman Springs Rd., Campo, CA 91906 | 13
Ramona Air Attack Base, 2498 Montecito Rd., Ramona, CA 92065 | 2
Total: | 353

## Table 21
Public Safety Power Shutoff Post-Event Report: JANUARY 20 – JANUARY 24, 2025
Appendix 5: PSPS Event Data Workbook
Table 21: Lessons Learned from PSPS Event
Issue | Discussion | Resolution
Meteorology Staffing | Having one meteorologist assigned to an operational period was not sufficient. | Two meteorologists were assigned to support each operational period.
Customer Notifications | It was challenging to quickly identify and send targeted notifications to customers on special switching plans prior to the completion of post-patrols. | Surgical notifications have been identified as an enhancement to the new Customer Notification System prior to the next PSPS season.

## Appendix 1
Public Safety Power Shutoff Post-Event Report: JANUARY 20 – JANUARY 24, 2025
Appendix 1 – Customer Notifications: Descriptions, Dates, Times, and Scripts of Notifications
Overview of Communications by Method2
|  | Notification Method | Total Notifications | Who Made the Notification
|  | Email | 479513 | SDG&E
|  | Voice | 464339 | SDG&E
|  | Text Message | 412808 | SDG&E
|  | Total: | 1356660
Customer Notifications: Detailed Communications2
Count of Notifications by M Message- Appendix 1
Event Order | Description of Notification1 | Required Minimum Timeline3 | Date | Time of First Notification | Time of Last Notification | Email | Voice | Text Message | Total Sent
Pre De-energization (Prior) | M2: 24-48 hours prior to a PSPS (Outage Warning) | 48–24 hours | 2025-01-18 | 2025-01-18 13:28 | 2025-01-23 02:22 | 140609 | 140324 | 125725 | 406658
| M3: 12 hours prior to PSPS (Outage Warning) | N/A | 2025-01-20 | 2025-01-20 08:25 | 2025-01-23 06:29 | 34060 | 33184 | 29325 | 96569
| M4: Within 4 hours prior to PSPS (Outage Warning) | 1–4 hours prior to PSPS (if possible) | 2025-01-20 | 2025-01-20 07:56 | 2025-01-23 12:27 | 60609 | 55960 | 49435 | 166004
Initiation (During) | M6: PSPS Confirmed - Power is Out | When de-energization is initiated | 2025-01-20 | 2025-01-20 08:08 | 2025-01-23 19:51 | 32014 | 28467 | 24749 | 85230
| M9: PSPS risk continues power remains off | N/A | 2025-01-21 | 2025-01-21 16:18 | 2025-01-23 19:35 | 36789 | 35380 | 31241 | 103410
| M16: Customers Transitioning onto a Microgrid (Outage Warning) | N/A | 2025-01-20 | 2025-01-20 22:05 | 2025-01-20 22:11 | 428 | 363 | 291 | 1082
Restoration (After) | M10: Safety Inspections of Power Lines Started (Patrolling) | When re-energization efforts begin | 2025-01-21 | 2025-01-21 14:05 | 2025-01-24 08:45 | 25606 | 24461 | 21588 | 71655
| M11: Power line Inspections damage found |  | 2025-01-24 | 2025-01-24 12:22 | 2025-01-24 12:22 | 3 | 2 | 1 | 6
| M12: Power Restored; However, PSPS risk continues and PSPS possible | When re-energization is complete, but further de-energizations may occur | 2025-01-21 | 2025-01-21 15:01 | 2025-01-23 11:47 | 10316 | 9231 | 8110 | 27657
| M12a: Power Restored; However, PSPS risk continues and PSPS possible | When re-energization is complete, but further de-energizations may occur | 2025-01-21 | 2025-01-21 16:53 | 2025-01-21 16:53 | 63900 | 63882 | 57216 | 184998
| M17: Conditions Improved Customers Transitioning Off a Microgrid (Outage Alert) | N/A | 2025-01-22 | 2025-01-22 08:34 | 2025-01-24 07:23 | 754 | 674 | 550 | 1978
| M14: PSPS risk passed, If previous notification received, no longer at risk of losing power | When a PSPS event is cancelled | 2025-01-24 | 2025-01-24 12:49 | 2025-01-24 12:49 | 54966 | 54919 | 49412 | 159297
| M15: Power Restored (Final Notification) | When re-energization is complete | 2025-01-22 | 2025-01-22 06:15 | 2025-01-24 16:02 | 19459 | 17492 | 15165 | 52116
Totals: | [5 empty] | 479513 | 464339 | 412808 | 1356660
3Decision 19-05-042, Appendix A, Timing of Notification.
2The total number of notifications does not represent unique customers. Some customers received notifications through multiple channels.
3Decision 19-05-042, Appendix A, Timing of Notification.

## Appendix 2
Public Safety Power Shutoff Post-Event Report: JANUARY 20 – JANUARY 24, 2025
Appendix 2 – Public Safety Partner Notifications: Descriptions, Dates, Times, and Copies of Notifications
Event Order | Type of Notification | Recipents | Description | Date/Time Contacted | Who Made the Notification
Pre-de- energization (prior) | 48-72 Hours | Public safety partners including local and tribal governments, water/wastewater, emergency management, communications providers, hospitals and CBOs. | SDG&E Public Safety Power Shutoff Possible in 48-72 Hours | 1/17/2025 at 12:39 PDT | SDG&E
| 24-48 Hours | Public safety partners including local and tribal governments, water/wastewater, emergency management, communications providers, hospitals and CBOs. | SDG&E Public Safety Power Shutoff possible in 24-48 hours. | 1/18/2025 at 12:54 PDT | SDG&E
| Imminent | Public safety partners including local and tribal governments, water/wastewater, emergency management, communications providers, hospitals and CBOs. | SDG&E Public Safety Power Shutoff possible within 12 hours. SDG&E's Emergency Operations Center activating at 6 p.m. | 1/19/2025 at 12:15 PDT 1/20/2025 at 9:04 PDT | SDG&E
Initiation (during) | De-Energized | Public safety partners including local and tribal governments, water/wastewater, emergency management, communications providers, hospitals and CBOs. | SDG&E has shut off power for public safety | 1/20/2025 at 10:08 PDT 1/20/2025 at 22:24 PDT 1/21/2025 at 1:28 PDT 1/21/2025 at 5:39 PDT 1/21/2025 at 11:35 PDT 1/22/2025 at 21:36 PDT | SDG&E
| Update #1 | Public safety partners including local and tribal governments, water/wastewater, emergency management, communications providers, hospitals and CBOs. | SDG&E has shut off power for public safety | 1/20/2025 at 15:56 PDT 1/23/2025 at 5:27 PDT | SDG&E
| Update #2 | Public safety partners including local and tribal governments, water/wastewater, emergency management, communications providers, hospitals and CBOs. | SDG&E has shut off power for public safety | 1/20/2025 at 20:40 PDT 1/23/2025 at 11:14 PDT 1/23/2025 at 13:53 PDT 1/23/2025 at 19:25 PDT | SDG&E
| Update #3 | Public safety partners including local and tribal governments, water/wastewater, emergency management, communications providers, hospitals and CBOs. | SDG&E has shut off power for public safety, Community Resource Centers to Open | 1/20/2025 at 10:53 PDT 1/23/2025 at 9:26 PDT | SDG&E
Restoration (after) | Imminent Re-Energize | Public safety partners including local and tribal governments, water/wastewater, emergency management, communications providers, hospitals and CBOs. | SDG&E power remains turned off for public safety. SDG&E is determining when power can be turned back on. | 1/21/2025 at 15:01 PDT 1/24/2025 at 8:31 PDT | SDG&E
| Update #4 | Public safety partners including local and tribal governments, water/wastewater, emergency management, communications providers, hospitals and CBOs. | SDG&E has shut off power for public safety. Power will remain out overnight | 1/21/2025 at 16:28 PDT 1/22/2025 at 8:54 PDT | SDG&E
| Re-Energized | Public safety partners including local and tribal governments, water/wastewater, emergency management, communications providers, hospitals and CBOs. | SDG&E continues to restore power to impacted areas. | 1/24/2025 at 12:31 PDT | SDG&E
Post-event | Event Concluded | Public safety partners including local and tribal governments, water/wastewater, emergency management, communications providers, hospitals and CBOs. | Final Notification: SDG&E Public Safety Power Shutoff event has ended | 1/24/2025 at 16:31 PDT | SDG&E
| Event concluded - Survey | Public safety partners including local and tribal governments, water/wastewater, emergency management, communications providers, hospitals and CBOs. | SDG&E Survey Request on Recent Public Safety Power Shutoff | 1/24/2025 at 16:31 PDT | SDG&E

## Appendix 4
Public Safety Power Shutoff Post-Event Report: JANUARY 20 – JANUARY 24, 2025
Appendix 4 – AFN Community Based Organization (CBO) Notifications: Descriptions, Dates, Times, and Copies of Notifications
Event Order | Type of Notification | Timeline | Date/Time Sent | Description of Notification | Who Made the Notification
Pre-de- energization (prior) | Initial Notice for PSPS Event | 72 hours | 1/17/2025 at 12:45 PDT | • SDG&E EOC Activated • Weather details and number of potentially impacted customers • Link to SDG&E’s Social Media Kit that includes PSPS Spanish and AFN content • Contact information for Customers to Request Services | SDG&E
| Initial Notice for PSPS Event | 72–48 hours | 1/18/2025 at 12:59 PDT |  | SDG&E
| Initial Notice for PSPS Event | 48–24 hours | 1/19/2025 at 12:20 PDT |  | SDG&E
| Initial Notice for PSPS Event | 1-4 Hours | 1/20/2025 at 10:12 PDT |  | SDG&E
Initiation (during) and Restoration (after) | De-energized | When de-energization is initiated | 1/20/2025 at 10:22 PDT | • Details of current PSPS outages • Link to SDG&E’s PSPS Web Page and Social Media Kit • Contact information for Customers to Request Services | SDG&E
| Update | As necessary | 1/19/2025 at 15:50 PDT 1/20/2025 at 11:16 PDT 1/20/2025 at 16:02 PDT 1/20/2025 at 20:45 PDT 1/20/2025 at 22:26 PDT 1/21/2025 at 01:31 PDT 1/21/2025 at 05:41 PDT 1/21/2025 at 12:16 PDT 1/21/2025 at 15:12 PDT 1/21/2025 at 17:12 PDT 1/22/2025 at 21:39 PDT 1/23/2025 at 05:29 PDT 1/23/2025 at 09:39 PDT 1/23/2025 at 11:18 PDT 1/23/2025 at 14:35 PDT 1/23/2025 at 19:27 PDT 1/24/2025 at 09:00 PDT 1/24/2025 at 13:09 PDT |  | SDG&E
| At the time service is restored to all customers | When re-energization is complete | 1/24/2025 at 16:46 PDT | • Timing of full restoration and EOC demobilization | SDG&E

## Appendix 2 (2)
SDG&E Emergency Management
CalOES & County OES Warning Center Notfications
Op Period | Notification Type | Time (Of Submission) | Date (Of Request) | Initiated By (Jurisdiction Name) | Information Source | CalOES Confirmation (Rep Name, Time Confirmed) | Message Contents/Notes
1 | Contact CalOES & County OES Warning Center | 12:02 | 2025-01-17 | SDG&E | Sit Stat Unit | Nick Womack @1203 | CalOES Form 1 Submitted @ 1202 hours – CalOES Nick Womack confirmed receipt at 1203 hours. San Diego County OES – Called at 1204 and phone sent to voicemail. Voicemail left at 1205 hours. Attempt two resulted in the same at 1207 hours
2 | Contact CalOES & County OES Warning Center | 6:57 | 2025-01-17 | SDG&E | Sit Stat Unit | Fuchinh Xiong @ 0659 | CalOES Form 2 Submitted @ 06:57 hours San Diego County OES- Laura Caracciolo confirmed receipt at 06:58 hours. CalOES Warning Center-Fuchinh Xiong Confirmed receipt at 6:59 hours.
2 | Contact CalOES & County OES Warning Center | 12:19 | 2025-01-17 | SDG&E | Sit Stat Unit | Nick Womack @ 1220 | CalOES Form 3 Submitted @ 12:19 hours San Diego County OES- Laura Caracciolo confirmed receipt at 12:21 hours. CalOES Warning Center-Nick Womack confirmed receipt at 12:20 hours.
2 | Contact CalOES & County OES Warning Center | 14:53 | 2025-01-18 | SDG&E | Sit Stat Unit | Benito Soto @ 1458 | CalOES Form 4 Submitted @ 1453 hours San Diego County OES- Laura Caraccilo confirmed 14:56 hours. CalOES Warning Center-Benito Soto confirmed receipt at 1458 hours.
3 | Contact CalOES & County OES Warning Center | 6:55 | 2025-01-19 | SDG&E | Sit Stat Unit | Sam Montoya @ 0656 | CalOES Form 5 Submitted CalOES Form 5 Submitted @ 0655 hours – CalOES Sam Montoya confirmed receipt at 0656 hours. San Diego County OES Laura Caracciolo confirmed receipt at 0658 hours.
3 | Contact CalOES & County OES Warning Center | 14:55 | 2025-01-19 | SDG&E | Sit Stat Unit | Benito Soto @ 1456 | CalOES Form 6 Submitted - CalOES Form 6 Submitted @ 1455 hours – CalOES Benito Soto confirmed receipt at 1456 hours. San Diego County OES Laura Caracciolo confirmed receipt at 1458 hours.
4 | Contact CalOES & County OES Warning Center | 7:00 | 2025-01-20 | SDG&E | Sit Stat Unit | Dave Hetland @ 0702 | CalOES Form 7 Submitted at 0700 - Dave Hetland at CalOES confirmed receipt at 0702 and Laura Caracciolo at County OES confirmed at 0703
4 | Contact CalOES & County OES Warning Center | 8:17 | 2025-01-20 | SDG&E | Sit Stat Unit | Benito Soto @ 0818 | CalOES Form 8 Submitted at 0817. Benito Soto at CalOES confirmed receipt at 0818 and Laura Caracciolo at County OES confirmed at 0819
4 | Contact CalOES & County OES Warning Center | 15:00 | 2025-01-20 | SDG&E | Sit Stat Unit | Benito Soto @ 1501 | CalOES Form 9 submitted at 1500. Benito Soto at CalOES confirmed receipt at 1501 and Laura Caracciolo at County OES confirmed at 1502
6 | Contact CalOES & County OES Warning Center | 6:56 | 2025-01-21 | SDG&E | Sit Stat Unit | Rosa Pulido @ 0658 | CalOES Form 10 Submitted @ 0656 hours – CalOES Rosa Pulido confirmed receipt at 0658 hours. San Diego County OES Laura Caracciolo confirmed receipt at 0659 hours
6 | Contact CalOES & County OES Warning Center | 14:23 | 2025-01-21 | SDG&E | Sit Stat Unit | Rosa Pulido @1425 | CalOES Form 11 Submitted @ 1423 hours – CalOES Rosa Pulido confirmed receipt at 1425 hours. San Diego County OES Laur Caracciolo confirmed receipt at 1426
8 | Contact CalOES & County OES Warning Center | 6:59 | 2025-01-22 | SDG&E | Sit Stat Unit | Joe Lurea @ 0703 | CalOES Form 12 Submitted @ 0659 hours – CalOES Joe Lurea confirmed receipt at 0703 hours. San Diego County OES Laura Caracciolo confirmed receipt at 0704 hours.
8 | Contact CalOES & County OES Warning Center | 15:00 | 2025-01-22 | SDG&E | Sit Stat Unit | Nick Womack @1502 | CalOES Form 13 Submitted @ 1500 hours –CalOES Nick Womack confirmed receipt at 1502 hours. San Diego County OES Laura Caracciolo confirmed receipt at 1503 hours.
10 | Contact CalOES & County OES Warning Center | 7:00 | 2025-01-23 | SDG&E | Sit Stat Unit | Nick Womack @ 0703 | CalOES Form 14 Submitted @ 0700 hours – CalOES Nick Womack confirmed receipt at 0703 hours. San Diego County OES Laura Caracciolo confirmed receipt at 0704 hours.
10 | Contact CalOES & County OES Warning Center | 14:58 | 2025-01-23 | SDG&E | Sit Stat Unit | Nick Womack @ 1500 | CalOES Form 15 Submitted @ 1458 hours – CalOES Nick Womack confirmed receipt at 1500 hours. San Diego County OES Laura Caracciolo confirmed receipt at 1504 hours.
12 | Contact CalOES & County OES Warning Center | 7:00 | 2025-01-24 | SDG&E | Sit Stat Unit | Benito Soto @ 0705 | CalOES Form 16 Submitted @ 0700 hours – CalOES Benito Soto confirmed receipt at 0705 hours. San Diego County OES Nick Tomlinson confirmed receipt at 0706 hours.
12 | Contact CalOES & County OES Warning Center | 15:00 | 2025-01-24 | SDG&E | Sit Stat Unit | Benito Soto @ 1501 | CalOES Form 17 Submitted @ 1500 hours – CalOES Benito Soto confirmed receipt at 1501 hours. San Diego County OES Edwin Ullua confirmed receipt at 1503 hours.
12 | Contact CalOES & County OES Warning Center | 16:27 | 2025-01-24 | SDG&E | Sit Stat Unit | Benito Soto @ 1628 | CalOES Form 18 Submitted @ 1627 hours – CalOES Benito Soto confirmed receipt at 1628 hours. San Diego County OES Nick Tomlinson confirmed receipt at 1629 hours.
CalOES PSPS Notification Dashboard

## Appendix 3
Public Safety Power Shutoff Post-Event Report: JANUARY 20 – JANUARY 24, 2025
Appendix 3 – CPUC Notifications: Descriptions, Dates, Times, and Copies of Notifications
Event Order | Type of Notification | Required Minimum Timeline1 | Date/Time Sent | Description of Notification | Who Made the Notification
Pre-de- energization (prior) | Initial Notice for PSPS Event | 72–48 hours | 1/17/2025 at 12:30 PDT | • Weather details and number of potentially impacted customers • Link to SDG&E’s secure public safety partner PSPS Portal to access anticipated timing of de-energization and re-energization, consolidated device information, maps and GIS shapefiles • Time of EOC activation | SDG&E
| Initial Notice for PSPS Event | 48–24 hours | 1/18/2025 at 12:53 PDT 1/19/2025 at 11:39 PDT |  | SDG&E
| Initial Notice for PSPS Event | 1–4 hours prior to PSPS (if possible) | 1/20/2025 at 9:04 PDT* |  | SDG&E
Initiation (during) | De-energized | When de-energization is initiated | 1/20/2025 at 08:26 PDT | • Details of current PSPS outages (timing, customer and community impacts) • Anticipated timing of re-energization • Link to SDG&E’s secure public safety partner PSPS Portal to access anticipated timing of de-energization and re-energization, consolidated device information, maps and GIS shapefiles | SDG&E
| Update | N/A | 1/20/2025 at 09:01 PDT 1/20/2025 at 12:11 PDT 1/20/2025 at 14:41 PDT 1/20/2025 at 20:06 PDT 1/20/2025 at 22:08 PDT 1/21/2025 at 01:07 PDT 1/21/2025 at 05:35 PDT 1/21/2025 at 11:28 PDT 1/22/2025 at 21:00 PDT 1/23/2025 at 05:22 PDT 1/23/2025 at 08:47 PDT 1/23/2025 at 10:46 PDT 1/23/2025 at 13:22 PDT 1/23/2025 at 18:07 PDT 1/23/2025 at 22:50 PDT |  | SDG&E
Restoration (after) | Re-energized | When re-energization efforts begin or immediately before re-energization begins | 1/21/2025 at 15:00 PDT 1/24/2025 at 08:29 PDT | • Details of current PSPS outages (timing, customer and community impacts) • Status of restoration efforts • Anticipated timing of re-energization • Link to SDG&E’s secure public safety partner PSPS Portal to access anticipated timing of de-energization and re-energization, consolidated device information, maps and GIS shapefiles | SDG&E
| Update | N/A | 1/21/2025 at 16:28 PDT 1/22/2025 at 08:31 PDT 1/22/2025 at 21:00 PDT 1/23/2025 at 05:22 PDT 1/24/2025 at 12:15 PDT |  | SDG&E
| At the time service is restored to all customers | When re-energization is complete | 1/24/2025 at 16:29 PDT | • Timing of full restoration and EOC demobilization • Timing of post-event report | SDG&E
1Decision 19-05-042, Appendix A, Timing of Notification.
*Notification provided to Public Safety Partners includes the CPUC. See Appendix 2.