## Table 1
Public Safety Power Shutoff Post-Event Report: JANUARY 7 – JANUARY 16, 2025
Appendix 5: PSPS Event Data Workbook
Table 1: PSPS Event Summary
Total Customers Notified | Total Customers De-energized | Total Customers Cancelled | MBL Customers De-energized | Number of Counties De-energized | Number of Tribes De-energized | Critical Facilities and Infrastructure Customers De-energized | Number of Transmission Lines De-energized | Number of Distribution Circuits in Scope | Number of Distribution Circuits De-energized | Damage/Hazard Count
74652 | 21,508 23,013 | 53,114 51,639 | 1,336 1,394 | 4 | 9 | 1,211 1,262 | 3 | 85 | 26 | 12

## Table 2
Public Safety Power Shutoff Post-Event Report: JANUARY 7 – JANUARY 16, 2025
Appendix 5: PSPS Event Data Workbook
Table 2: Factors Considered in the Decision to Shut Off Power
# | Circuit/Device Name | Sustained Wind Speeds (mph) | Gust Wind Speeds (mph) | Peak Gust Speed (mph) | Temperature (°F) | Humidity (%) | Moisture | Fire Potential Index1 (FPI) | Temp Config2 (Y/N) | Vegetation Risk Index3 (VRI) | Circuit Risk Index3 (CRI) | Alert Speed4 (mph) | WiNGS Ops5 (mph) | Wildfire Consequence Score | PSPS Consequence Score | Wildfire/ PSPS Ratio6 | De-energized Date/Time
1 | 214-1122R | 30 | 55 | 62 | 55 | 22% | 7% | 15 | N | Medium | Low | 45 | 24.2264 | 0.7777 | 0.0033563 | 231.7115 | 2025-01-07 21:04
2 | 448-744R | 23 | 42 | 51 | 53 | 27% | 6% | 15 | Y | Medium | Low | 35 | 44.8057 | 0.0077268 | 0.0028954 | 2.6687 | 2025-01-07 21:04
3 | 212-1204R | 24 | 47 | 48 | 44 | 33% | 5% | 15 | N | Low | Medium | 41 | 38.8744 | 0.02635 | 0.0019797 | 13.3103 | 2025-01-07 22:12
4 | RIN-12KV-217 | 13 | 42 | 71 | 57 | 23% | 7% | 15 | Y | Medium | Medium | 35 | 22.3901 | 0.21339 | 0.01133 | 18.8335 | 2025-01-07 22:14
5 | 445-1325F | 27 | 48 | 59 | 44 | 41% | 6% | 15 | Y | Low | Low | 35 | 43.3246 | 0.0085627 | 0.00054616 | 15.678 | 2025-01-07 22:55
6 | CW-12.47KV-1215 | 27 | 48 | 59 | 44 | 40% | 6% | 15 | N | Low | Low | 45 | 36.7561 | 0.40141 | 0.0014747 | 272.1908 | 2025-01-07 23:04
7 | BUE-12.47KV-444 | 26 | 44 | 51 | 47 | 34% | 5% | 15 | N | Low | Low | 45 | --- | --- | --- | --- | 2025-01-07 23:26
8 | STY-12KV-222 | 32 | 53 | 53 | 47 | 33% | 6% | 15 | Y | Medium | Low | 35 | 28.0434 | 0.40542 | 0.012403 | 32.6882 | 2025-01-07 23:44
9 | 79-799R | 30 | 55 | 59 | 46 | 40% | 6% | 15 | N | Low | Low | 45 | 55.4813 | 0.0040966 | 0.00018656 | 21.959 | 2025-01-08 00:40
10 | 441-23R | 31 | 45 | 55 | 44 | 44% | 6% | 15 | N | Low | Low | 45 | 29.0933 | 0.53125 | 0.0010889 | 487.8554 | 2025-01-08 01:13
11 | 442-16R | 25 | 48 | 55 | 45 | 40% | 6% | 15 | N | Medium | Low | 41 | 34.1465 | 0.014591 | 0.00026433 | 55.2016 | 2025-01-08 02:42
12 | LI-12KV-352 | 22 | 47 | 48 | 59 | 26% | 6% | 15 | N | Medium | Medium | 35 | 29.3416 | 0.042237 | 0.0020537 | 20.5668 | 2025-01-08 05:07
13 | 358-682F | 30 | 52 | 54 | 51 | 31% | 6% | 15 | N | Low | Low | 45 | 40.6094 | 0.044133 | 0.001557 | 28.3454 | 2025-01-08 05:53
14 | 908-1368R | 23 | 40 | 40 | 59 | 25% | 6% | 15 | N | Medium | High | 35 | 20.096 | 0.27551 | 0.0016053 | 171.6264 | 2025-01-08 05:53
15 | 220-298R | 29 | 42 | 49 | 46 | 32% | 6% | 15 | N | Medium | Low | 45 | 41.9354 | 0.023033 | 0.0015528 | 14.8332 | 2025-01-08 05:54
16 | 1243-45R | 21 | 40 | 42 | 58 | 21% | 6% | 15 | Y | Low | Medium | 35 | 29.9605 | 0.011109 | 0.00056488 | 19.6653 | 2025-01-08 06:41
17 | 449-683 | 35 | 47 | 49 | 50 | 36% | 6% | 16 | N | Low | High | 45 | --- | --- | --- | --- | 2025-01-08 06:57
18 | 79-799R | 26 | 41 | 85 | 53 | 14% | 5% | 16 | N | Low | Low | 45 | 55.4813 | 0.0040966 | 0.00018656 | 21.959 | 2025-01-09 17:48
19 | 445-897R | 29 | 37 | 75 | 47 | 23% | 5% | 16 | Y | Low | Low | 35 | 35.4737 | 0.45027 | 0.0031283 | 143.934 | 2025-01-09 20:58
20 | 444-43R | 25 | 39 | 44 | 53 | 19% | 5% | 16 | N | Low | Low | 35 | 30.9847 | 0.039344 | 0.0038155 | 10.3117 | 2025-01-09 21:02
21 | 212-1204R | 32 | 49 | 50 | 47 | 21% | 4% | 16 | N | Low | Medium | 41 | 38.8744 | 0.02635 | 0.0019797 | 13.3103 | 2025-01-09 21:13
22 | STY-12KV-222 | 19 | 36 | 44 | 51 | 19% | 4% | 16 | Y | Medium | Low | 35 | 28.0434 | 0.40542 | 0.012403 | 32.6882 | 2025-01-09 22:42
23 | CW-12.47KV-1215 | 34 | 50 | 75 | 46 | 24% | 5% | 16 | N | Low | Low | 45 | 36.7561 | 0.40141 | 0.0014747 | 272.1908 | 2025-01-09 22:44
24 | 441-23R | 32 | 50 | 66 | 47 | 22% | 5% | 16 | N | Low | Low | 45 | 29.0933 | 0.53125 | 0.0010889 | 487.8554 | 2025-01-09 22:46
25 | 221-36 | 25 | 39 | 44 | 47 | 21% | 5% | 16 | N | High | Low | 35 | --- | 0.0006 | 0.0119 | 0.05042 | 2025-01-09 23:57
26 | 358-682F | 26 | 43 | 61 | 54 | 16% | 4% | 16 | N | Low | Low | 45 | 40.6094 | 0.044133 | 0.001557 | 28.3454 | 2025-01-10
27 | 214-1122R | 34 | 53 | 63 | 55 | 15% | 5% | 16 | N | Medium | Low | 45 | 24.2264 | 0.7777 | 0.0033563 | 231.7115 | 2025-01-10 02:58
28 | 73-1163 | 28 | 52 | 52 | 45 | 22% | 5% | 16 | Y | Medium | Low | 35 | 35.879 | 0.076494 | 0.006191 | 12.3556 | 2025-01-10 05:13
29 | 1458-519 | 23 | 40 | 49 | 53 | 17% | 4% | 16 | Y | Medium | Medium | 35 | 36.9457 | 0.074201 | 0.0041429 | 17.9102 | 2025-01-10 05:39
30 | DE-12KV-78 | 21 | 54 | 54 | 49 | 18% | 5% | 16 | N | Low | Low | 45 | 44.459 | 0.025084 | 0.0010053 | 24.9513 | 2025-01-10 05:56
31 | 448-735R | 33 | 56 | 60 | 51 | 18% | 5% | 16 | N | Low | Low | 50 | --- | --- | --- | --- | 2025-01-10 07:33
32 | 445-897R | 29 | 41 | 57 | 37 | 29% | 4% | 15 | Y | Low | Low | 35 | 35.4737 | 0.45027 | 0.0031283 | 143.934 | 2025-01-14 01:36
33 | 79-685R | 30 | 48 | 59 | 36 | 26% | 5% | 15 | N | Low | Low | 45 | 47.3417 | 0.005145 | 6.4663e-05 | 79.5659 | 2025-01-14 04:18
34 | CW-12.47KV-1215 | 36 | 50 | 57 | 37 | 29% | 4% | 15 | N | Low | Low | 45 | 36.7561 | 0.40141 | 0.0014747 | 272.1908 | 2025-01-14 05:31
35 | 358-682F | 29 | 46 | 56 | 47 | 18% | 4% | 15 | N | Low | Low | 45 | 40.6094 | 0.044133 | 0.001557 | 28.3454 | 2025-01-14 06:03
36 | 441-23R | 33 | 49 | 60 | 38 | 28% | 4% | 15 | N | Low | Low | 45 | 29.0933 | 0.53125 | 0.0010889 | 487.8554 | 2025-01-14 06:28
37 | 222-1503R | 31 | 44 | 46 | 39 | 25% | 6% | 15 | N | Medium | Low | 45 | 42.1598 | 0.0058122 | 0.0026137 | 2.2237 | 2025-01-14 12:00
38 | 242-1428 | 26 | 38 | 40 | 64 | 12% | 4% | 15 | N | High | High | 36 | 45 | 0.001447 | 0.0043183 | 0.33509 | 2025-01-14 12:59
39 | 396-699R | 26 | 38 | 40 | 64 | 12% | 4% | 15 | Y | High | High | 35 | 45 | 0.0011672 | 0.0048702 | 0.23967 | 2025-01-14 13:04
40 | 393-14R | 26 | 38 | 40 | 64 | 12% | 4% | 15 | N | High | High | 36 | 45 | 0.0034863 | 0.010089 | 0.34554 | 2025-01-14 13:07
41 | SN-12KV-1138 | 26 | 38 | 40 | 64 | 12% | 4% | 15 | Y | High | High | 35 | 45 | 0.0022168 | 0.0073346 | 0.30223 | 2025-01-14 13:12
42 | 220-294R | 32 | 49 | 56 | 43 | 25% | 4% | 15 | N | Low | Low | 45 | 38.6948 | 0.032527 | 0.0027895 | 11.6605 | 2025-01-15 07:15
43 | 221-36 | 20 | 38 | 39 | 41 | 25% | 5% | 15 | N | High | Low | 35 | 27.5 | 0.0005 | 0.0119 | 0.042017 | 2025-01-14 09:30
Note: Missing values are indicated by '---'. SDG&E will integrate these Circuit Breakers into the WiNGS-Ops tool.
1 Fire Potential Index is described in Section 2.2
2 Temporary Construction and Compliance Poles (TCC) are assessed by Electrical Distribution and Transmission engineering teams before a PSPS activation. They evaluate compliance risks, considering factors like wire distances from objects and pole capacities, and may lower wind gust speed thresholds based on the severity of their findings. Legend (Y*) indicates the presence of one or more TCC poles downstream of the SCADA sectionalizing device, with no change in alert speed due to this TCC condition. Legend (Y**) signifies that the TCC pole(s) downstream of the SCADA sectionalizing device meet the criteria to lower wind gust thresholds.
3 VRI and CRI provide a relative assessment of vegetation as well as conductor risk for each segment. Methodologies reported in SDG&E's 2021 WMP, Section 4.5.1.
4 This Alert Speed is the recommended wind gust threshold for initiating de-energization during this specific PSPS activation.
5 WiNGS Ops provides an estimated wind gust threshold at which the expected wildfire risk exceeds the PSPS risk at each feeder segment. This output incorporates both an estimate of likelihood of the risk as well as consequence. Calculations described in Section 2.4
6 This ratio depicts the comparison between wildfire consequence score using historical weather events and PSPS consequence score (excludes likelihood of risk). A value greater than 1 means the wildfire risk exceeds the PSPS risk.

## Table 3
Public Safety Power Shutoff Post-Event Report: JANUARY 7 – JANUARY 16, 2025
Appendix 5: PSPS Event Data Workbook
Table 3: Circuits De-energized
Distribution/ Transmission | Circuit/ Device Name | County | De-energization Date and Time | Restoration Date/Time | Duration | All clear Date/Time | HFTD Tier | Total Customers | Residential Customers | Commercial/ Industrial Customers | MBL Customers | AFN other than MBL Customers1 | Other Customers
Distribution | 1138-6R | San Diego | 2025-01-14 13:12 | 2025-01-15 09:20 | 0.83889 | 2025-01-15 07:32 | Non HFTD | 592 | 571 | 21 | 76 | 151 | N/A
Distribution | 1215-10R | San Diego | 2025-01-07 23:04 | 2025-01-09 09:42 | 1899-12-31 10:38 | 2025-01-09 08:45 | Tier-3 | 10 | 0 | 10 | 0 | 0 | N/A
Distribution | 1215-10R | San Diego | 2025-01-09 22:44 | 2025-01-10 14:16 | 0.64722 | 2025-01-10 13:43 | Tier-3 | 10 | 0 | 10 | 0 | 0 | N/A
Distribution | 1215-10R | San Diego | 2025-01-14 05:31 | 2025-01-16 10:25 | 1900-01-01 04:54 | 2025-01-16 09:50 | Tier-3 | 10 | 0 | 10 | 0 | 0 | N/A
Distribution | 1215-12R | San Diego | 2025-01-07 23:04 | 2025-01-09 09:44 | 1899-12-31 10:40 | 2025-01-09 08:45 | Tier-3 | 35 | 33 | 2 | 5 | 15 | N/A
Distribution | 1215-12R | San Diego | 2025-01-09 22:44 | 2025-01-10 14:15 | 0.64653 | 2025-01-10 13:43 | Tier-3 | 35 | 33 | 2 | 5 | 15 | N/A
Distribution | 1215-12R | San Diego | 2025-01-14 05:31 | 2025-01-16 10:23 | 1900-01-01 04:52 | 2025-01-16 09:50 | Tier-3 | 35 | 33 | 2 | 5 | 15 | N/A
Distribution | 1215-28R | San Diego | 2025-01-07 23:04 | 2025-01-09 09:51 | 1899-12-31 10:47 | 2025-01-09 08:45 | Tier-3 | 33 | 19 | 14 | 2 | 13 | N/A
Distribution | 1215-28R | San Diego | 2025-01-09 22:44 | 2025-01-10 14:24 | 0.65278 | 2025-01-10 13:43 | Tier-3 | 33 | 19 | 14 | 2 | 13 | N/A
Distribution | 1215-28R | San Diego | 2025-01-14 05:31 | 2025-01-16 10:39 | 1900-01-01 05:08 | 2025-01-16 09:50 | Tier-3 | 33 | 19 | 14 | 2 | 13 | N/A
Distribution | 1215-32R | San Diego | 2025-01-07 23:04 | 2025-01-09 10:01 | 1899-12-31 10:57 | 2025-01-09 08:45 | Tier-3 | 76 | 58 | 18 | 1 | 24 | N/A
Distribution | 1215-32R | San Diego | 2025-01-09 22:44 | 2025-01-10 14:30 | 0.65694 | 2025-01-10 13:43 | Tier-3 | 76 | 58 | 18 | 1 | 24 | N/A
Distribution | 1215-32R | San Diego | 2025-01-14 05:31 | 2025-01-16 10:47 | 1900-01-01 05:16 | 2025-01-16 09:50 | Tier-3 | 76 | 58 | 18 | 1 | 24 | N/A
Distribution | 1243-157 | Orange | 2025-01-08 06:41 | 2025-01-08 19:49 | 0.54722 | 2025-01-08 16:38 | Tier-2 | 3 | 0 | 3 | 0 | 0 | N/A
Distribution | 1243-319R | Orange | 2025-01-08 06:41 | 2025-01-08 18:59 | 0.5125 | 2025-01-08 16:38 | Tier-2 | 13 | 5 | 8 | 0 | 0 | N/A
Distribution | 1243-38R | Orange | 2025-01-08 06:41 | 2025-01-08 16:59 | 0.42917 | 2025-01-08 16:38 | Tier-2 | 1 | 0 | 1 | 0 | 0 | N/A
Distribution | 1243-45R | Orange | 2025-01-08 06:41 | 2025-01-08 16:56 | 0.42708 | 2025-01-08 16:38 | Tier-2 | 28 | 3 | 25 | 0 | 0 | N/A
Distribution | 1458-1131R | San Diego | 2025-01-10 05:39 | 2025-01-10 11:31 | 0.24444 | 2025-01-10 10:53 | Tier-2 | 161 | 140 | 21 | 8 | 44 | N/A
Distribution | 1458-519 | San Diego | 2025-01-10 05:39 | 2025-01-10 11:05 | 0.22639 | 2025-01-10 10:53 | Tier-2 | 1 | 0 | 1 | 0 | 0 | N/A
Distribution | 1458-601R | San Diego | 2025-01-10 05:39 | 2025-01-10 11:14 | 0.23264 | 2025-01-10 10:53 | Tier-2 | 288 | 228 | 60 | 38 | 93 | N/A
Distribution | 212-1204R | San Diego | 2025-01-07 22:12 | 2025-01-09 09:49 | 1899-12-31 11:37 | 2025-01-09 09:09 | Tier-2 | 77 | 59 | 18 | 1 | 20 | N/A
Distribution | 212-1204R | San Diego | 2025-01-09 21:13 | 2025-01-10 10:42 | 0.56181 | 2025-01-10 10:31 | Tier-2 | 77 | 59 | 18 | 1 | 20 | N/A
Distribution | 212-773R | San Diego | 2025-01-07 22:12 | 2025-01-09 10:08 | 1899-12-31 11:56 | 2025-01-09 09:09 | Tier-2 | 125 | 109 | 16 | 3 | 33 | N/A
Distribution | 212-773R | San Diego | 2025-01-09 21:13 | 2025-01-10 10:45 | 0.56389 | 2025-01-10 10:31 | Tier-2 | 125 | 109 | 16 | 3 | 33 | N/A
Distribution | 212-886R | San Diego | 2025-01-07 22:12 | 2025-01-09 10:30 | 1899-12-31 12:18 | 2025-01-09 09:09 | Tier-2 | 21 | 9 | 12 | 1 | 3 | N/A
Distribution | 212-886R | San Diego | 2025-01-09 21:13 | 2025-01-10 11:06 | 0.57847 | 2025-01-10 10:31 | Tier-2 | 21 | 9 | 12 | 1 | 3 | N/A
Distribution | 214-1122R | San Diego | 2025-01-07 21:04 | 2025-01-09 11:51 | 1899-12-31 14:47 | 2025-01-09 11:33 | Tier-3 | 236 | 185 | 51 | 8 | 64 | N/A
Distribution | 214-1122R | San Diego | 2025-01-10 02:58 | 2025-01-10 10:11 | 0.30069 | 2025-01-10 10:00 | Tier-3 | 236 | 185 | 51 | 8 | 64 | N/A
Distribution | 214-1135R | San Diego | 2025-01-07 21:51 | 2025-01-09 11:46 | 1899-12-31 13:55 | 2025-01-09 11:33 | Tier-3 | 112 | 60 | 52 | 6 | 21 | N/A
Distribution | 214-4R | San Diego | 2025-01-07 21:51 | 2025-01-09 12:00 | 1899-12-31 14:09 | 2025-01-09 11:33 | Tier-3 | 36 | 11 | 25 | 0 | 1 | N/A
Distribution | 214-536R | San Diego | 2025-01-07 21:51 | 2025-01-09 11:53 | 1899-12-31 14:02 | 2025-01-09 11:33 | Tier-3 | 13 | 7 | 6 | 0 | 0 | N/A
Distribution | 214-583R | San Diego | 2025-01-07 21:51 | 2025-01-09 11:50 | 1899-12-31 13:59 | 2025-01-09 11:33 | Tier-3 | 50 | 38 | 12 | 4 | 17 | N/A
Distribution | 214-613R | San Diego | 2025-01-07 21:51 | 2025-01-09 12:01 | 1899-12-31 14:10 | 2025-01-09 11:33 | Tier-3 | 100 | 82 | 18 | 2 | 7 | N/A
Distribution | 214-647R | San Diego | 2025-01-07 21:04 | 2025-01-09 11:56 | 1899-12-31 14:52 | 2025-01-09 11:33 | Tier-3 | 136 | 115 | 21 | 7 | 59 | N/A
Distribution | 214-647R | San Diego | 2025-01-10 02:58 | 2025-01-10 10:23 | 0.30903 | 2025-01-10 10:00 | Tier-3 | 136 | 115 | 21 | 7 | 59 | N/A
Distribution | 217-835R | San Diego | 2025-01-07 22:14 | 2025-01-09 15:04 | 1899-12-31 16:50 | 2025-01-09 14:40 | Tier-3 | 91 | 29 | 62 | 0 | 3 | N/A
Distribution | 217-837R | San Diego | 2025-01-07 22:14 | 2025-01-09 14:52 | 1899-12-31 16:38 | 2025-01-09 14:40 | Tier-3 | 903 | 650 | 253 | 47 | 118 | N/A
Distribution | 217-972R | San Diego | 2025-01-07 22:14 | 2025-01-09 14:55 | 1899-12-31 16:41 | 2025-01-09 14:40 | Tier-3 | 135 | 83 | 52 | 4 | 36 | N/A
Distribution | 217-983R | Riverside, San Diego | 2025-01-07 22:14 | 2025-01-09 15:09 | 1899-12-31 16:55 | 2025-01-09 14:40 | Tier-3 | 82 | 76 | 6 | 4 | 16 | N/A
Distribution | 220-294R | San Diego | 2025-01-15 07:15 | 2025-01-16 09:30 | 1899-12-31 02:15 | 2025-01-16 07:22 | Tier-3 | 130 | 102 | 28 | 10 | 54 | N/A
Distribution | 220-298R | San Diego | 2025-01-08 05:54 | 2025-01-09 10:27 | 1899-12-31 04:33 | 2025-01-09 10:11 | Tier-3 | 171 | 119 | 52 | 1 | 30 | N/A
Distribution | 220-298R | San Diego | 2025-01-15 07:15 | 2025-01-16 09:56 | 1899-12-31 02:41 | 2025-01-16 07:22 | Tier-3 | 171 | 119 | 52 | 1 | 30 | N/A
Distribution | 221-1249R | San Diego | 2025-01-09 23:57 | 2025-01-10 16:52 | 0.70486 | 2025-01-10 14:30 | Tier-3 | 196 | 158 | 38 | 7 | 42 | N/A
Distribution | 221-1251R | San Diego | 2025-01-09 23:57 | 2025-01-10 04:58 | 0.20903 | 2025-01-10 03:47 | Tier-3 | 117 | 100 | 17 | 4 | 30 | N/A
Distribution | 221-23R | San Diego | 2025-01-09 23:57 | 2025-01-10 17:00 | 0.71042 | 2025-01-10 14:30 | Tier-3 | 267 | 249 | 18 | 19 | 73 | N/A
Distribution | 221-344R | San Diego | 2025-01-09 23:57 | 2025-01-10 16:56 | 0.70764 | 2025-01-10 14:30 | Tier-3 | 99 | 77 | 22 | 0 | 14 | N/A
Distribution | 221-37AE | San Diego | 2025-01-09 23:57 | 2025-01-10 04:23 | 0.18472 | 2025-01-10 03:48 | Tier-3 | 222 | 195 | 27 | 17 | 92 | N/A
Distribution | 221-38AE | San Diego | 2025-01-09 23:57 | 2025-01-10 01:21 | 0.058333 | 2025-01-10 01:18 | Tier-3 | 362 | 239 | 123 | 10 | 71 | N/A
Distribution | 221-675R | San Diego | 2025-01-09 23:57 | 2025-01-10 17:23 | 0.72639 | 2025-01-10 14:30 | Tier-3 | 7 | 5 | 2 | 0 | 2 | N/A
Distribution | 221-6R | San Diego | 2025-01-09 23:57 | 2025-01-10 17:15 | 0.72083 | 2025-01-10 14:30 | Tier-3 | 1 | 0 | 1 | 0 | 0 | N/A
Distribution | 221-782R | San Diego | 2025-01-09 23:57 | 2025-01-10 17:12 | 0.71875 | 2025-01-10 14:30 | Tier-3 | 3 | 0 | 3 | 0 | 0 | N/A
Distribution | 221-824 | San Diego | 2025-01-09 23:57 | 2025-01-10 17:18 | 0.72292 | 2025-01-10 14:30 | Tier-3 | 273 | 258 | 15 | 17 | 67 | N/A
Distribution | 222-1433R | San Diego | 2025-01-07 23:44 | 2025-01-09 09:25 | 1899-12-31 09:41 | 2025-01-09 08:29 | Tier-3 | 16 | 13 | 3 | 1 | 5 | N/A
Distribution | 222-1433R | San Diego | 2025-01-09 22:42 | 2025-01-10 15:59 | 0.72014 | 2025-01-10 14:30 | Tier-3 | 16 | 13 | 3 | 1 | 5 | N/A
Distribution | 222-1503R | San Diego | 2025-01-07 23:44 | 2025-01-09 09:36 | 1899-12-31 09:52 | 2025-01-09 08:29 | Tier-3 | 46 | 38 | 8 | 2 | 5 | N/A
Distribution | 222-1503R | San Diego | 2025-01-09 22:42 | 2025-01-10 15:55 | 0.71736 | 2025-01-10 14:30 | Tier-3 | 46 | 38 | 8 | 2 | 5 | N/A
Distribution | 222-1503R | San Diego | 2025-01-14 12:00 | 2025-01-16 09:13 | 1899-12-31 21:13 | 2025-01-16 08:52 | Tier-3 | 46 | 38 | 8 | 2 | 5 | N/A
Distribution | 222-1523R | San Diego | 2025-01-07 23:44 | 2025-01-09 09:14 | 1899-12-31 09:30 | 2025-01-09 08:29 | Tier-3 | 197 | 162 | 35 | 17 | 36 | N/A
Distribution | 222-1523R | San Diego | 2025-01-09 22:42 | 2025-01-10 15:42 | 0.70833 | 2025-01-10 14:30 | Tier-3 | 197 | 162 | 35 | 17 | 36 | N/A
Distribution | 222-1986R | San Diego | 2025-01-07 23:44 | 2025-01-09 09:44 | 1899-12-31 10:00 | 2025-01-09 08:29 | Tier-3 | 307 | 220 | 87 | 17 | 52 | N/A
Distribution | 222-1986R | San Diego | 2025-01-09 22:42 | 2025-01-10 16:14 | 0.73056 | 2025-01-10 14:30 | Tier-3 | 307 | 220 | 87 | 17 | 52 | N/A
Distribution | 222-1988R | San Diego | 2025-01-07 23:44 | 2025-01-09 09:33 | 1899-12-31 09:49 | 2025-01-09 08:29 | Tier-3 | 10 | 9 | 1 | 0 | 3 | N/A
Distribution | 222-1988R | San Diego | 2025-01-09 22:42 | 2025-01-10 16:18 | 0.73333 | 2025-01-10 14:30 | Tier-3 | 10 | 9 | 1 | 0 | 3 | N/A
Distribution | 222-1990R | San Diego | 2025-01-07 23:44 | 2025-01-09 09:20 | 1899-12-31 09:36 | 2025-01-09 08:29 | Tier-3 | 78 | 42 | 36 | 3 | 9 | N/A
Distribution | 222-1990R | San Diego | 2025-01-09 22:42 | 2025-01-10 15:50 | 0.71389 | 2025-01-10 14:30 | Tier-3 | 78 | 42 | 36 | 3 | 9 | N/A
Distribution | 222-1992R | San Diego | 2025-01-07 23:44 | 2025-01-09 09:09 | 1899-12-31 09:25 | 2025-01-09 08:29 | Tier-3 | 27 | 12 | 15 | 2 | 4 | N/A
Distribution | 222-1992R | San Diego | 2025-01-09 22:42 | 2025-01-10 15:38 | 0.70556 | 2025-01-10 14:30 | Tier-3 | 27 | 12 | 15 | 2 | 4 | N/A
Distribution | 222-2013R | San Diego | 2025-01-07 23:44 | 2025-01-09 09:47 | 1899-12-31 10:03 | 2025-01-09 08:29 | Tier-3 | 247 | 199 | 48 | 10 | 42 | N/A
Distribution | 222-2013R | San Diego | 2025-01-09 22:42 | 2025-01-10 16:04 | 0.72361 | 2025-01-10 14:30 | Tier-3 | 247 | 199 | 48 | 10 | 42 | N/A
Distribution | 222-2013R | San Diego | 2025-01-14 12:00 | 2025-01-16 09:29 | 1899-12-31 21:29 | 2025-01-16 08:52 | Tier-3 | 247 | 199 | 48 | 10 | 42 | N/A
Distribution | 222-724 | San Diego | 2025-01-07 23:44 | 2025-01-09 10:54 | 1899-12-31 11:10 | 2025-01-09 08:29 | Tier-3 | 1 | 1 | 0 | 0 | 1 | N/A
Distribution | 242-1428 | San Diego | 2025-01-14 12:59 | 2025-01-15 10:15 | 0.88611 | 2025-01-15 10:02 | Non HFTD | 530 | 502 | 28 | 20 | 89 | N/A
Distribution | 352-27R | San Diego | 2025-01-08 05:07 | 2025-01-09 09:01 | 1899-12-31 03:54 | 2025-01-09 08:47 | Tier-2 | 242 | 216 | 26 | 19 | 50 | N/A
Distribution | 358-682F | San Diego | 2025-01-08 05:53 | 2025-01-09 09:40 | 1899-12-31 03:47 | 2025-01-09 07:12 | Tier-3 | 186 | 167 | 19 | 11 | 55 | N/A
Distribution | 358-682F | San Diego | 2025-01-10 | 2025-01-10 11:45 | 0.48958 | 2025-01-10 11:35 | Tier-3 | 186 | 167 | 19 | 11 | 55 | N/A
Distribution | 358-682F | San Diego | 2025-01-14 06:03 | 2025-01-15 14:42 | 1899-12-31 08:39 | 2025-01-15 14:31 | Tier-3 | 187 | 168 | 19 | 11 | 55 | N/A
Distribution | 393-14R | San Diego | 2025-01-14 13:07 | 2025-01-15 08:44 | 0.81736 | 2025-01-15 08:10 | Non HFTD | 1247 | 1201 | 46 | 117 | 421 | N/A
Distribution | 396-699R | San Diego | 2025-01-14 13:04 | 2025-01-15 09:35 | 0.85486 | 2025-01-15 09:23 | Non HFTD | 608 | 595 | 13 | 83 | 144 | N/A
Distribution | 441-23R | San Diego | 2025-01-08 01:13 | 2025-01-09 09:49 | 1899-12-31 08:36 | 2025-01-09 09:26 | Tier-3 | 25 | 7 | 18 | 0 | 2 | N/A
Distribution | 441-23R | San Diego | 2025-01-09 22:46 | 2025-01-10 13:11 | 0.60069 | 2025-01-10 12:58 | Tier-3 | 25 | 7 | 18 | 0 | 2 | N/A
Distribution | 441-23R | San Diego | 2025-01-14 06:28 | 2025-01-15 14:42 | 1899-12-31 08:14 | 2025-01-15 14:11 | Tier-3 | 25 | 7 | 18 | 0 | 2 | N/A
Distribution | 441-279R | San Diego | 2025-01-08 01:13 | 2025-01-09 09:51 | 1899-12-31 08:38 | 2025-01-09 09:26 | Tier-3 | 15 | 3 | 12 | 0 | 0 | N/A
Distribution | 441-279R | San Diego | 2025-01-09 22:46 | 2025-01-10 13:13 | 0.60208 | 2025-01-10 12:58 | Tier-3 | 15 | 3 | 12 | 0 | 0 | N/A
Distribution | 441-279R | San Diego | 2025-01-14 06:28 | 2025-01-15 14:44 | 1899-12-31 08:16 | 2025-01-15 14:11 | Tier-3 | 15 | 3 | 12 | 0 | 0 | N/A
Distribution | 441-27R | San Diego | 2025-01-08 01:13 | 2025-01-09 10:06 | 1899-12-31 08:53 | 2025-01-09 09:26 | Tier-3 | 30 | 22 | 8 | 1 | 5 | N/A
Distribution | 441-27R | San Diego | 2025-01-09 22:46 | 2025-01-10 13:26 | 0.61111 | 2025-01-10 12:58 | Tier-3 | 30 | 22 | 8 | 1 | 5 | N/A
Distribution | 441-27R | San Diego | 2025-01-14 06:28 | 2025-01-15 14:54 | 1899-12-31 08:26 | 2025-01-15 14:11 | Tier-3 | 30 | 22 | 8 | 1 | 5 | N/A
Distribution | 441-30R | San Diego | 2025-01-08 01:13 | 2025-01-09 10:07 | 1899-12-31 08:54 | 2025-01-09 09:26 | Tier-3 | 25 | 19 | 6 | 2 | 8 | N/A
Distribution | 441-30R | San Diego | 2025-01-09 22:46 | 2025-01-10 13:27 | 0.61181 | 2025-01-10 12:58 | Tier-3 | 25 | 19 | 6 | 2 | 8 | N/A
Distribution | 441-30R | San Diego | 2025-01-14 06:28 | 2025-01-15 14:53 | 1899-12-31 08:25 | 2025-01-15 14:11 | Tier-3 | 24 | 18 | 6 | 2 | 8 | N/A
Distribution | 442-16R | San Diego | 2025-01-08 02:42 | 2025-01-09 09:41 | 1899-12-31 06:59 | 2025-01-09 09:00 | Tier-3 | 26 | 11 | 15 | 0 | 0 | N/A
Distribution | 442-16R | San Diego | 2025-01-09 22:59 | 2025-01-10 15:05 | 0.67083 | 2025-01-10 14:20 | Tier-3 | 26 | 11 | 15 | 0 | 0 | N/A
Distribution | 442-28R | San Diego | 2025-01-09 08:36 | 2025-01-09 10:01 | 0.059028 | 2025-01-09 10:00 | Tier-3 | 2 | 1 | 1 | 0 | 0 | N/A
Distribution | 442-28R | San Diego | 2025-01-09 17:39 | 2025-01-09 19:38 | 0.082639 | 2025-01-09 12:57 | Tier-3 | 2 | 1 | 1 | 0 | 0 | N/A
Distribution | 442-28R | San Diego | 2025-01-09 23:12 | 2025-01-10 15:31 | 0.67986 | 2025-01-10 14:20 | Tier-3 | 2 | 1 | 1 | 0 | 0 | N/A
Distribution | 442-32R | San Diego | 2025-01-09 08:36 | 2025-01-09 10:05 | 0.061806 | 2025-01-09 10:00 | Tier-3 | 2 | 0 | 2 | 0 | 0 | N/A
Distribution | 442-32R | San Diego | 2025-01-09 17:39 | 2025-01-09 19:41 | 0.084722 | 2025-01-09 12:57 | Tier-3 | 2 | 0 | 2 | 0 | 0 | N/A
Distribution | 442-32R | San Diego | 2025-01-09 23:12 | 2025-01-10 15:35 | 0.68264 | 2025-01-10 14:20 | Tier-3 | 2 | 0 | 2 | 0 | 0 | N/A
Distribution | 442-46R | San Diego | 2025-01-09 08:36 | 2025-01-09 13:30 | 0.20417 | 2025-01-09 12:57 | Tier-3 | 171 | 141 | 30 | 2 | 10 | N/A
Distribution | 442-46R | San Diego | 2025-01-09 17:39 | 2025-01-10 16:10 | 0.93819 | 2025-01-10 14:20 | Tier-3 | 40 | 37 | 3 | 2 1 | 10 | N/A
Distribution | 442-509R | San Diego | 2025-01-09 08:36 | 2025-01-09 13:34 | 0.20694 | 2025-01-09 12:57 | Tier-3 | 58 | 48 | 10 | 0 | 2 | N/A
Distribution | 442-509R | San Diego | 2025-01-09 17:39 | 2025-01-10 16:18 | 0.94375 | 2025-01-10 14:20 | Tier-3 | 58 | 48 | 10 | 0 | 2 | N/A
Distribution | 442-728R | San Diego | 2025-01-09 22:59 | 2025-01-10 14:47 | 0.65833 | 2025-01-10 14:20 | Tier-3 | 843 | 754 | 89 | 65 | 186 | N/A
Distribution | 442-758F | San Diego | 2025-01-09 08:36 | 2025-01-09 13:14 | 0.19306 | 2025-01-09 12:57 | Tier-3 | 2 | 0 | 2 | 0 | 0 | N/A
Distribution | 442-758F | San Diego | 2025-01-09 17:39 | 2025-01-10 15:45 | 0.92083 | 2025-01-10 14:20 | Tier-3 | 2 | 0 | 2 | 0 | 0 | N/A
Distribution | 442-764R | San Diego | 2025-01-09 08:36 | 2025-01-09 13:25 | 0.20069 | 2025-01-09 12:57 | Tier-3 | 19 | 17 | 2 | 0 | 1 | N/A
Distribution | 442-764R | San Diego | 2025-01-09 17:39 | 2025-01-10 16:02 | 0.93264 | 2025-01-10 14:20 | Tier-3 | 19 | 17 | 2 | 0 | 1 | N/A
Distribution | 442-777 | San Diego | 2025-01-09 17:39 | 2025-01-10 16:14 | 0.94097 | 2025-01-10 14:20 | Tier-3 | 131 | 104 | 27 | 1 | 5 | N/A
Distribution | 444-15R | Imperial, San Diego | 2025-01-07 23:26 | 2025-01-09 09:21 | 1899-12-31 09:55 | 2025-01-09 08:30 | Tier-2 | 16 | 9 | 7 | 2 | 5 | N/A
Distribution | 444-15R | Imperial, San Diego | 2025-01-09 21:02 | 2025-01-10 13:54 | 0.70278 | 2025-01-10 13:21 | Tier-2 | 16 | 9 | 7 | 2 | 5 | N/A
Distribution | 444-43R | San Diego | 2025-01-07 23:26 | 2025-01-09 09:07 | 1899-12-31 09:41 | 2025-01-09 08:30 | Tier-2 | 123 | 93 | 30 | 11 | 37 | N/A
Distribution | 444-43R | San Diego | 2025-01-09 21:02 | 2025-01-10 13:31 | 0.68681 | 2025-01-10 13:21 | Tier-2 | 123 | 93 | 30 | 11 | 37 | N/A
Distribution | 444-9R | San Diego | 2025-01-07 23:26 | 2025-01-09 09:11 | 1899-12-31 09:45 | 2025-01-09 08:30 | Tier-2 | 282 | 236 | 46 | 15 | 132 | N/A
Distribution | 444-9R | San Diego | 2025-01-09 21:02 | 2025-01-10 13:46 | 0.69722 | 2025-01-10 13:21 | Tier-2 | 282 | 236 | 46 | 15 | 132 | N/A
Distribution | 445-1311R | San Diego | 2025-01-07 23:10 | 2025-01-09 09:23 | 1899-12-31 10:13 | 2025-01-09 08:30 | Tier-2 | 176 | 150 | 26 | 11 | 73 | N/A
Distribution | 445-1311R | San Diego | 2025-01-09 20:58 | 2025-01-10 15:15 | 0.76181 | 2025-01-10 14:32 | Tier-2 | 176 | 150 | 26 | 11 | 73 | N/A
Distribution | 445-1311R | San Diego | 2025-01-14 01:36 | 2025-01-16 09:30 | 1900-01-01 07:54 | 2025-01-16 07:54 | Tier-2 | 176 | 150 | 26 | 11 | 73 | N/A
Distribution | 445-1325F | San Diego | 2025-01-07 22:55 | 2025-01-09 09:03 | 1899-12-31 10:08 | 2025-01-09 08:27 | Tier-2 | 90 | 73 | 17 | 8 | 23 | N/A
Distribution | 445-1325F | San Diego | 2025-01-09 21:02 | 2025-01-10 15:07 | 0.75347 | 2025-01-10 14:32 | Tier-2 | 90 | 73 | 17 | 8 | 23 | N/A
Distribution | 445-1325F | San Diego | 2025-01-14 01:37 | 2025-01-16 09:44 | 1900-01-01 08:07 | 2025-01-16 07:54 | Tier-2 | 90 | 73 | 17 | 8 | 23 | N/A
Distribution | 445-17R | San Diego | 2025-01-07 23:22 | 2025-01-09 09:02 | 1899-12-31 09:40 | 2025-01-09 08:27 | Tier-2 | 58 | 47 | 11 | 6 | 26 | N/A
Distribution | 445-17R | San Diego | 2025-01-10 00:15 | 2025-01-10 15:03 | 0.61667 | 2025-01-10 14:32 | Tier-2 | 58 | 47 | 11 | 6 | 26 | N/A
Distribution | 445-18R | San Diego | 2025-01-07 23:10 | 2025-01-09 09:24 | 1899-12-31 10:14 | 2025-01-09 08:27 | Tier-2 | 163 | 133 | 30 | 8 | 75 | N/A
Distribution | 445-18R | San Diego | 2025-01-09 20:58 | 2025-01-10 15:34 | 0.775 | 2025-01-10 14:32 | Tier-2 | 163 | 133 | 30 | 8 | 75 | N/A
Distribution | 445-18R | San Diego | 2025-01-14 01:36 | 2025-01-16 09:32 | 1900-01-01 07:56 | 2025-01-16 07:54 | Tier-2 | 163 | 133 | 30 | 8 | 75 | N/A
Distribution | 445-19R | San Diego | 2025-01-07 23:22 | 2025-01-09 09:04 | 1899-12-31 09:42 | 2025-01-09 08:27 | Tier-2 | 84 | 71 | 13 | 9 | 34 | N/A
Distribution | 445-19R | San Diego | 2025-01-10 00:15 | 2025-01-10 15:08 | 0.62014 | 2025-01-10 14:32 | Tier-2 | 84 | 71 | 13 | 9 | 34 | N/A
Distribution | 445-39R | San Diego | 2025-01-07 23:22 | 2025-01-09 08:58 | 1899-12-31 09:36 | 2025-01-09 08:27 | Tier-2 | 177 | 150 | 27 | 12 | 59 | N/A
Distribution | 445-39R | San Diego | 2025-01-10 00:15 | 2025-01-10 15:01 | 0.61528 | 2025-01-10 14:32 | Tier-2 | 177 | 150 | 27 | 12 | 59 | N/A
Distribution | 445-894R | San Diego | 2025-01-07 23:22 | 2025-01-09 09:15 | 1899-12-31 09:53 | 2025-01-09 08:27 | Tier-2 | 179 | 149 | 30 | 9 | 71 | N/A
Distribution | 445-894R | San Diego | 2025-01-09 23:51 | 2025-01-10 15:09 | 0.6375 | 2025-01-10 14:32 | Tier-2 | 179 | 149 | 30 | 9 | 71 | N/A
Distribution | 445-897R | San Diego | 2025-01-07 23:10 | 2025-01-09 09:17 | 1899-12-31 10:07 | 2025-01-09 08:27 | Tier-2 | 8 | 8 | 0 | 1 | 4 | N/A
Distribution | 445-897R | San Diego | 2025-01-09 20:58 | 2025-01-10 15:10 | 0.75833 | 2025-01-10 14:32 | Tier-2 | 8 | 8 | 0 | 1 | 4 | N/A
Distribution | 445-897R | San Diego | 2025-01-14 01:36 | 2025-01-16 09:11 | 1900-01-01 07:35 | 2025-01-16 07:54 | Tier-2 | 8 | 8 | 0 | 1 | 4 | N/A
Distribution | 448-1234R | San Diego | 2025-01-10 07:33 | 2025-01-10 15:47 | 0.34306 | 2025-01-10 14:39 | Tier-3 | 8 | 8 | 0 | 2 | 2 | N/A
Distribution | 448-47R | San Diego | 2025-01-10 07:33 | 2025-01-10 15:24 | 0.32708 | 2025-01-10 14:39 | Tier-3 | 58 | 49 | 9 | 3 | 31 | N/A
Distribution | 448-735R | San Diego | 2025-01-10 07:33 | 2025-01-10 15:03 | 0.3125 | 2025-01-10 14:39 | Tier-3 | 45 | 31 | 14 | 0 | 20 | N/A
Distribution | 448-744R | San Diego | 2025-01-07 21:04 | 2025-01-09 08:57 | 1899-12-31 11:53 | 2025-01-09 08:30 | Tier-3 | 341 | 302 | 39 | 27 | 137 | N/A
Distribution | 449-683 | San Diego | 2025-01-08 06:57 | 2025-01-09 09:31 | 1899-12-31 02:34 | 2025-01-09 08:05 | Tier-3 | 8 | 0 | 8 | 0 | 0 | N/A
Distribution | 73-1130R | San Diego | 2025-01-10 05:13 | 2025-01-10 14:52 | 0.40208 | 2025-01-10 13:12 | Tier-3 | 145 | 137 | 8 | 11 | 46 | N/A
Distribution | 73-1163 | San Diego | 2025-01-10 05:13 | 2025-01-10 13:22 | 0.33958 | 2025-01-10 13:12 | Tier-3 | 248 | 213 | 35 | 11 | 62 | N/A
Distribution | 73-23R | San Diego | 2025-01-10 05:13 | 2025-01-10 14:40 | 0.39375 | 2025-01-10 13:12 | Tier-3 | 75 | 56 | 19 | 8 | 14 | N/A
Distribution | 73-678R | San Diego | 2025-01-10 05:13 | 2025-01-10 14:30 | 0.38681 | 2025-01-10 13:12 | Tier-3 | 149 | 129 | 20 | 14 | 32 | N/A
Distribution | 73-683R | San Diego | 2025-01-10 05:13 | 2025-01-10 14:00 | 0.36597 | 2025-01-10 13:12 | Tier-3 | 126 | 98 | 28 | 10 | 22 | N/A
Distribution | 78-782R | San Diego | 2025-01-10 05:56 | 2025-01-10 13:10 | 0.30139 | 2025-01-10 12:43 | Tier-3 | 17 | 14 | 3 | 1 | 4 | N/A
Distribution | 79-1215F | San Diego | 2025-01-10 06:00 | 2025-01-10 14:41 | 0.36181 | 2025-01-10 14:20 | Tier-3 | 1 | 1 | 0 | 0 | 0 | N/A
Distribution | 79-658R | San Diego | 2025-01-08 02:24 | 2025-01-09 10:32 | 1899-12-31 08:08 | 2025-01-09 09:46 | Tier-3 | 33 | 13 | 20 | 1 | 2 | N/A
Distribution | 79-658R | San Diego | 2025-01-09 23:33 | 2025-01-10 15:18 | 0.65625 | 2025-01-10 14:20 | Tier-3 | 33 | 13 | 20 | 1 | 2 | N/A
Distribution | 79-660R | San Diego | 2025-01-08 02:24 | 2025-01-09 10:45 | 1899-12-31 08:21 | 2025-01-09 09:45 | Tier-3 | 18 | 4 | 14 | 0 | 0 | N/A
Distribution | 79-660R | San Diego | 2025-01-09 23:33 | 2025-01-10 15:30 | 0.66458 | 2025-01-10 14:20 | Tier-3 | 18 | 4 | 14 | 0 | 0 | N/A
Distribution | 79-660R | San Diego | 2025-01-14 08:42 | 2025-01-16 08:17 | 1899-12-31 23:35 | 2025-01-16 07:52 | Tier-3 | 18 | 4 | 14 | 0 | 0 | N/A
Distribution | 79-668R | San Diego | 2025-01-08 02:24 | 2025-01-09 11:00 | 1899-12-31 08:36 | 2025-01-09 09:46 | Tier-3 | 194 | 154 | 40 | 3 | 18 | N/A
Distribution | 79-668R | San Diego | 2025-01-09 23:33 | 2025-01-10 15:49 | 0.67778 | 2025-01-10 14:20 | Tier-3 | 194 | 154 | 40 | 3 | 18 | N/A
Distribution | 79-668R | San Diego | 2025-01-14 08:42 | 2025-01-16 08:34 | 1899-12-31 23:52 | 2025-01-16 07:52 | Tier-3 | 194 | 154 | 40 | 3 | 18 | N/A
Distribution | 79-676R | San Diego | 2025-01-10 06:00 | 2025-01-10 14:44 | 0.36389 | 2025-01-10 14:20 | Tier-3 | 76 | 68 | 8 | 0 | 17 | N/A
Distribution | 79-679R | San Diego | 2025-01-10 05:52 | 2025-01-10 14:43 | 0.36875 | 2025-01-10 14:20 | Tier-3 | 96 | 89 | 7 | 10 | 11 | N/A
Distribution | 79-685R | San Diego | 2025-01-08 01:59 | 2025-01-09 10:37 | 1899-12-31 08:38 | 2025-01-09 09:46 | Tier-3 | 5 | 3 | 2 | 0 | 0 | N/A
Distribution | 79-685R | San Diego | 2025-01-09 20:58 | 2025-01-10 15:36 | 0.77639 | 2025-01-10 14:20 | Tier-3 | 5 | 3 | 2 | 0 | 0 | N/A
Distribution | 79-685R | San Diego | 2025-01-14 04:18 | 2025-01-16 08:08 | 1900-01-01 03:50 | 2025-01-16 07:52 | Tier-3 | 5 | 3 | 2 | 0 | 0 | N/A
Distribution | 79-714R | San Diego | 2025-01-08 02:24 | 2025-01-09 10:27 | 1899-12-31 08:03 | 2025-01-09 09:46 | Tier-3 | 95 | 79 | 16 | 6 | 21 | N/A
Distribution | 79-714R | San Diego | 2025-01-10 04:52 | 2025-01-10 15:03 | 0.42431 | 2025-01-10 14:20 | Tier-3 | 95 | 79 | 16 | 6 | 21 | N/A
Distribution | 79-782R | San Diego | 2025-01-08 02:24 | 2025-01-09 10:53 | 1899-12-31 08:29 | 2025-01-09 09:46 | Tier-3 | 1 | 0 | 1 | 0 | 0 | N/A
Distribution | 79-782R | San Diego | 2025-01-09 23:33 | 2025-01-10 15:45 | 0.675 | 2025-01-10 14:20 | Tier-3 | 1 | 0 | 1 | 0 | 0 | N/A
Distribution | 79-782R | San Diego | 2025-01-14 08:42 | 2025-01-16 08:26 | 1899-12-31 23:44 | 2025-01-16 07:52 | Tier-3 | 1 | 0 | 1 | 0 | 0 | N/A
Distribution | 79-785 | San Diego | 2025-01-08 02:24 | 2025-01-09 10:16 | 1899-12-31 07:52 | 2025-01-09 09:46 | Tier-3 | 270 | 239 | 31 | 23 | 74 | N/A
Distribution | 79-785 | San Diego | 2025-01-10 04:52 | 2025-01-10 14:53 | 0.41736 | 2025-01-10 14:20 | Tier-3 | 270 | 239 | 31 | 23 | 74 | N/A
Distribution | 79-799R | San Diego | 2025-01-08 00:40 | 2025-01-09 10:06 | 1899-12-31 09:26 | 2025-01-09 09:46 | Tier-3 | 18 | 14 | 4 | 1 | 4 | N/A
Distribution | 79-799R | San Diego | 2025-01-09 17:48 | 2025-01-10 15:00 | 0.88333 | 2025-01-10 14:20 | Tier-3 | 18 | 14 | 4 | 1 | 4 | N/A
Distribution | 79-799R | San Diego | 2025-01-14 05:33 | 2025-01-16 08:13 | 1900-01-01 02:40 | 2025-01-16 07:52 | Tier-3 | 18 | 14 | 4 | 1 | 4 | N/A
Distribution | 79-808R | San Diego | 2025-01-10 05:52 | 2025-01-10 14:47 | 0.37153 | 2025-01-10 14:20 | Tier-3 | 70 | 54 | 16 | 2 | 12 | N/A
Distribution | 908-1368R | San Diego | 2025-01-08 05:53 | 2025-01-09 10:49 | 1899-12-31 04:56 | 2025-01-09 10:36 | Tier-2 | 195 | 155 | 40 | 12 | 34 | N/A
Distribution | BUE-12.47KV-444 | San Diego | 2025-01-07 23:26 | 2025-01-09 09:03 | 1899-12-31 09:37 | 2025-01-09 08:30 | Tier-2 | 4 | 3 | 1 | 1 | 3 | N/A
Distribution | BUE-12.47KV-444 | San Diego | 2025-01-10 00:11 | 2025-01-10 13:27 | 0.55278 | 2025-01-10 13:21 | Tier-2 | 4 | 3 | 1 | 1 | 3 | N/A
Distribution | BUE-12.47KV-445 | San Diego | 2025-01-07 23:22 | 2025-01-09 08:54 | 1899-12-31 09:32 | 2025-01-09 07:25 | Tier-2 | 28 | 16 | 12 | 1 | 7 | N/A
Distribution | BUE-12.47KV-445 | San Diego | 2025-01-10 00:15 | 2025-01-10 14:58 | 0.61319 | 2025-01-10 14:32 | Tier-2 | 28 | 16 | 12 | 1 | 7 | N/A
Distribution | CTL1-3R | San Diego | 2025-01-07 21:51 | 2025-01-09 12:19 | 1899-12-31 14:28 | 2025-01-09 11:33 | Tier-3 | 192 | 173 | 19 | 3 | 31 | N/A
Distribution | DE-12KV-78 | San Diego | 2025-01-10 05:56 | 2025-01-10 12:50 | 0.2875 | 2025-01-10 12:43 | Tier-3 | 106 | 98 | 8 | 15 | 27 | N/A
Distribution | GC-12.47KV-441 | San Diego | 2025-01-08 02:01 | 2025-01-09 09:47 | 1899-12-31 07:46 | 2025-01-09 08:03 | Tier-3 | 18 | 5 | 13 | 0 | 0 | N/A
Distribution | GC-12.47KV-441 | San Diego | 2025-01-09 23:52 | 2025-01-10 13:09 | 0.55347 | 2025-01-10 12:58 | Tier-3 | 18 | 5 | 13 | 0 | 0 | N/A
Distribution | GC-12.47KV-441 | San Diego | 2025-01-14 14:44 | 2025-01-15 14:39 | 0.99653 | 2025-01-15 14:11 | Tier-3 | 18 | 5 | 13 | 0 | 0 | N/A
Distribution | GC-12.47KV-442 | San Diego | 2025-01-09 23:12 | 2025-01-10 14:46 | 0.64861 | 2025-01-10 14:20 | Tier-3 | 10 | 2 | 8 | 0 | 0 | N/A
Distribution | LBE.246 | San Diego | 2025-01-09 23:57 | 2025-01-10 17:11 | 0.71806 | 2025-01-10 14:30 | Tier-3 | 83 | 68 | 15 | 2 | 20 | N/A
Distribution | LI-12KV-352 | San Diego | 2025-01-08 05:07 | 2025-01-09 08:57 | 1899-12-31 03:50 | 2025-01-09 07:28 | Tier-2 | 1 | 0 | 1 | 0 | 0 | N/A
Distribution | SN-12KV-1138 | San Diego | 2025-01-14 13:12 | 2025-01-15 09:06 | 0.82917 | 2025-01-15 07:32 | Non HFTD | 311 | 290 | 21 | 39 | 78 | N/A
Distribution | STY-12KV-222 | San Diego | 2025-01-07 23:44 | 2025-01-09 08:58 | 1899-12-31 09:14 | 2025-01-09 08:29 | Tier-3 | 534 | 427 | 107 | 31 | 80 | N/A
Distribution | STY-12KV-222 | San Diego | 2025-01-09 22:42 | 2025-01-10 15:27 | 0.69792 | 2025-01-10 14:30 | Tier-3 | 535 | 428 | 107 | 31 | 80 | N/A
Transmission | TL629 | San Diego | 2025-01-09 23:53 | 2025-01-10 12:18 | 0.51736 | 2025-01-10 08:53 | Tier-3 | 0 | 0 | 0 | 0 | 0 | N/A
Transmission | TL6931 | San Diego | 2025-01-09 23:46 | 2025-01-10 12:29 | 0.52986 | 2025-01-10 08:53 | Tier-2 | 0 | 0 | 0 | 0 | 0 | N/A
Transmission | TL6958 | San Diego | 2025-01-09 23:49 | 2025-01-10 12:25 | 0.525 | 2025-01-10 08:53 | Tier-3 | 0 | 0 | 0 | 0 | 0 | N/A
Distribution | 221-1249R | San Diego | 2025-01-14 09:30 | 2025-01-16 09:44 | 1900-01-01 00:14 | 2025-01-16 06:35 | Tier-3 | 189 | 153 | 36 | 7 | 41 | N/A
Distribution | 221-1251R | San Diego | 2025-01-14 09:30 | 2025-01-14 13:00 | 0.14583 | 2025-01-14 09:50 | Tier-3 | 113 | 96 | 17 | 4 | 28 | N/A
Distribution | 221-23R | San Diego | 2025-01-14 09:30 | 2025-01-16 09:49 | 1900-01-01 00:19 | 2025-01-16 09:25 | Tier-3 | 267 | 249 | 18 | 19 | 73 | N/A
Distribution | 221-344R | San Diego | 2025-01-14 09:30 | 2025-01-16 09:53 | 1900-01-01 00:23 | 2025-01-16 09:25 | Tier-3 | 99 | 77 | 22 | 0 | 14 | N/A
Distribution | 221-36 | San Diego | 2025-01-14 09:30 | 2025-01-14 10:27 | 0.039583 | 2025-01-14 09:50 | Tier-3 | 365 | 242 | 123 | 10 | 72 | N/A
Distribution | 221-37 | San Diego | 2025-01-14 09:30 | 2025-01-14 11:46 | 0.094444 | 2025-01-14 09:50 | Tier-3 | 222 | 195 | 27 | 17 | 92 | N/A
Distribution | 221-675R | San Diego | 2025-01-14 09:30 | 2025-01-16 10:11 | 1900-01-01 00:41 | 2025-01-16 09:25 | Tier-3 | 7 | 5 | 2 | 0 | 2 | N/A
Distribution | 221-6R | San Diego | 2025-01-14 09:30 | 2025-01-16 09:59 | 1900-01-01 00:29 | 2025-01-16 09:25 | Tier-3 | 1 | 0 | 1 | 0 | 0 | N/A
Distribution | 221-782R | San Diego | 2025-01-14 09:30 | 2025-01-16 09:56 | 1900-01-01 00:26 | 2025-01-16 09:25 | Tier-3 | 3 | 0 | 3 | 0 | 0 | N/A
Distribution | 221-824 | San Diego | 2025-01-14 09:30 | 2025-01-16 10:17 | 1900-01-01 00:47 | 2025-01-16 09:25 | Tier-3 | 156 | 142 | 14 | 10 | 38 | N/A
Distribution | LBE.246 | San Diego | 2025-01-14 09:30 | 2025-01-15 16:40 | 1899-12-31 07:10 | 2025-01-15 16:31 | Tier-3 | 83 | 68 | 15 | 2 | 20 | N/A
1Includes all customers that meet any of the 15 AFN conditions flagged in SDG&E’s customer information system as long as MBL is not the only condition.
Formulas:
Duration = [Restoration Date/Time]-[De-energization Date and Time]

## Table 18
Public Safety Power Shutoff Post-Event Report: JANUARY 7 – JANUARY 16, 2025
Appendix 5: PSPS Event Data Workbook
Table 18: Summary of Avoided Customer Impacts
Mitigation Action | Avoided Impacts
Sectionalizing Devices | 10,443 10,609
Temporary Generation | 172 296
Microgrids | 353 691
Permanent Backup Generation | 658 685
Strategic Undergrounding | 393
Situational Awareness | 39893
Total: | 51,912 52,567

## Table 19
Public Safety Power Shutoff Post-Event Report: JANUARY 7 – JANUARY 16, 2025
Appendix 5: PSPS Event Data Workbook
Table 19: Summary of Avoided Customer Impacts by Circuit
Circuit | Avoided Impacts
67 | 587
73 | 9
79 | 28
157 | 1028
210 | 211
211 | 298
212 | 400
214 | 1
215 | 524
217 | 1
220 | 34
221 | 892 1,547
222 | 583
230 | 1
233 | 840
235 | 3
237 | 456
240 | 263
242 | 2674
246 | 1547
247 | 1039
249 | 547
280 | 3172
283 | 487
286 | 1
288 | 1
350 | 1609
351 | 369
352 | 1
353 | 1526
354 | 1268
355 | 1211
356 | 1723
357 | 1944
358 | 863
393 | 1125
396 | 948
401 | 2
411 | 1739
441 | 15
442 | 5
445 | 3
448 | 696
449 | 621
450 | 1112
454 | 19
470 | 1051
502 | 1
520 | 546
523 | 1
524 | 736
542 | 1
576 | 1
788 | 2037
840 | 16
907 | 3128
908 | 1601
909 | 435
970 | 2
972 | 3
973 | 1385
974 | 343
975 | 1
1021 | 850
1022 | 136
1023 | 1202
1030 | 875
1039 | 868
1081 | 1
1090 | 16
1138 | 1
1166 | 162
1215 | 27
1233 | 293
1243 | 38
1250 | 1827
1458 | 1821
RA3 | 1
RB1 | 44
TM1 | 36
Total: | 51,912 52,567