## Sheet1
Data request for | San Diego Gas & Electric
Date sent | 2020-03-13
Response requested by | 2020-03-18
Should you need clarification on this data request, please contact Ryan Arba (ryan.arba@cpuc.ca.gov)
This data request shall be completed according to the process outlined in Resolution WSD 001. In particular: 1. Any discovery or data requests and responses shall be posted on the responding electrical corporation’s website in an easy to follow format that identifies what the discovery was about, what the responses were about, and links to any documents produced. The electrical corporations shall update the website weekly, with an e-mail to the service list of R.18-10-007 with the relevant link and discussion of what is new on the website. The website (or portion of webpage) shall be labeled “2020 Wildfire Mitigation Plan Discovery/Data requests” for each electrical corporation. 2. Electrical corporations must copy any data requests received from or responses to Commission staff to the e-mail address wildfiresafetydivision@cpuc.ca.gov. Requests from staff to the electrical corporations may also come from this address or from individual e-mail addresses. 3. Each electrical corporation shall send to wildfiresafetydivision@cpuc.ca.gov the name of their single point of contact for all data requests and response matters for Commission staff use. 4. Electrical corporations must respond to all data and discovery requests within 3 business days of the request. Both requests and responses shall be sent by e-mail. Exceptions to the 3-business-day requirement will require a letter to the Division Director and a strong showing of the specific reason for the delay. In your response to each data request please specify the relevant item index being responded to, found here in column B. 5. Parties conducting discovery must first analyze the significant data that will be submitted with 2020 WMPs along with the Supplemental Data Request.2 Entities submitting data requests should avoid submissions where such information is contained in the electrical corporations’ WMP filings. 6. All documents the electrical corporation references in its WMP plans shall be collected on the above website in an easy to follow format, with notice to the service list of the location of such documents. This will be in addition to the posting of WMPs on the Commission’s website as required by Pub. Util. Code § 8386(d).
A. Item Index [For CPUC tracking purposes. Please reference this item index with the response provided.] | C. Relevant section of WMP (if applicable) | D. Relevant question in Maturity Survey (if applicable) | E. Relevant meeting or call (if applicable) | F. Specific Data request | G. Format in which the data is to be provided | SDG&E Internal Question # | Does response result in WMP revisions (Y/N); If yes, citation is provided | SDG&E Response
SDGE-43900-Z -636 | 5.3.7.4 | NA | NA | Submit locations for near misses (areas where damage and/or faults nearly caused a fire). | GIS file | 1 | N | Please see attachment: “SDGE-43900-Z-636_20200313_Q1.gdb.” The attached data identifies the locations of heat-related electrical anomalies in SDG&E’s distribution system.
SDGE-43900-Z -637 | Various | NA | NA | Submit locations of asset faults. | GIS file | 2 | N | SDG&E anticipates providing a response to this item by March 20, 2020. Please see attachment: “SDGE-43900-Z-637_20200313_Q2.gdb.7z.”
SDGE-43900-Z -638 | 5.3.5 | NA | NA | Submit locations of vegetation projects (completed in the last 5 years and planned for the future). | GIS file | 3 | N | For vegetation projects completed in the last 5 years, please see attached documents “SDGE-43900-Z-638_20200313_Q3.gdb” and “SDGE-43900-Z-638_20200313_Q3.xslx.” The locations of the vegetation projects planned for the future will generally be in a similar vicinity as the locations of the completed projects, however, at this time SDG&E does not have those planned locations available geospatially. The specific project locations will be dependent on the results of future inspections. The frequency and number of planned, future tree trim and removal projects is expected to increase for both routinely-scheduled and off-cycle enhanced work. The vegetation risk index will assist in scoping future project patrols.
SDGE-43900-Z -639 | 6.4: Current baseline state of service territory and utility equipment | NA | NA | Submit line data showing the current locations of covered conductors. | GIS file | 4 | N | SDG&E anticipates providing a response to this item by March 20, 2020. Please see attachment: “SDGE-43900-Z-639_20200313_Q4.gdb.7z.”
SDGE-43900-Z -640 | 6.4: Current baseline state of service territory and utility equipment | NA | NA | Provide SDG&E/private connection points for where distribution lines transition from SDG&E-owned lines to privately-owned lines. | GIS file | 5 | N | Please see attachment: “SDGE-43900-Z-640_20200313_Q5.gdb.7z.”
SDGE-43900-Z -641 | 6.4: Current baseline state of service territory and utility equipment | NA | NA | In the "Table9_CustomersPerCensusTract" layer, what are the definitions of the following fields: "MBL_Customers" and "LS_Customers"? | GIS file | 6 | N | In the Table 9 customers per census tract layer, the field ‘MBL_Customers’ stands for “medical baseline customers,” and the field ‘LS_Customers’ stands for “life support customers.”
SDGE-43900-Z -642 | 6.4: Current baseline state of service territory and utility equipment | NA | NA | Submit any remaining data (not previously submitted) for circuit risk levels (including vegetation risk index data) for all transmission lines and distribution lines | GIS file | 7 | N | Please see attachment: “SDGE-43900-Z-642_20200313_Q7.gdb.”
SDGE-43900-​I-672 | 5.3.5 | NA | NA | How does transmission differ from distribution for both inspections and enhanced vegetation management measures? | Narrative | 8 | N | For inspections, transmission and distribution are similar with both performing yearly visual patrols, wood pole intrusive inspections on a ten year cycle, and routine detailed patrols. At this time, the differences would be in regard to infrared inspections and routine detailed inspection frequency. As noted in SDG&E’s 2020 WMP, transmission infrared inspections currently occur on a yearly cycle. Previously, distribution infrared inspections had been on an ad hoc basis, but a new program is being developed to create a routine infrared inspection program for distribution with the program beginning this year. For routine detailed inspections, transmission currently utilizes a three year cycle, whereas distribution utilizes a five year cycle. For Vegetation Management, the tree inspections for distribution and transmission occur simultaneously during the annual cycle and during the off-cycle patrols. Time-of–trim clearances are generally greater on transmission lines compared with distribution lines to meet the increased minimum clearance requirements for transmission, and to ensure no vegetation-related impacts to the bulk electric system. Post-trim clearances on transmission voltages generally range from 20 feet up to 40-50 feet depending on site-specific conditions. Technology such as laser rangefinders are typically used on transmission inspections such as 230kV and 500kV to enhance the inspector’s ability to make empirical measurements of tree height and clearances to conductors.
SDGE-43900-​I-673 | 5.3.5 | NA | NA | Regarding emergency VM practices as discussed in section 5.3.5.9 on page 122: a. How many patrols did San Diego Gas & Electric perform as warranted by a forecasted RFW? Break down by patrols completed “in advance of, during, or immediately following red flag events.” b. Out of those patrols, how many hazards were identified and abated? Break down by if the hazard was identified during a patrol that was “in advance of, during, or immediately following red flag events.” c. How many crew are typically reserved for standby to perform patrols in response to RFW events? | Narrative | 9 | N | a. In advance of the RFW events which occurred in SDG&E’s service territory in late October 2019, SDG&E’s Electric Troubleshooters (ETS) performed patrols in areas of the service territory forecasted for strong winds to identify potential equipment or vegetation issues. During the October 2019 RFW, patrollers (ETS) were dispatched to observe conditions throughout the HFTD. During this same event approximately 25-30 Vegetation Management pre-inspectors were working in these same areas assessing trees. Following the RFW event in late October, Vegetation Management performed a hazard tree patrol on ten (10) circuits in areas affected. b. During the ETS patrol conducted in advance of the RFW events in October, only a few tree-related issues were identified. That work was completed in advance of the event. During the RFW event, Vegetation Management identified approximately 18 trees that required priority work. This included instances where wind was blowing trees in proximity to the lines, and trees deemed to require priority work due to a defect. All this was completed during the RFW event or shortly thereafter. During the post-RFW patrols conducted by Vegetation Management, 7 trees were identified that required follow-up work. All work was completed. c. SDG&E’s pre-inspection contractor maintains a workforce of approximately 60 individuals. The contractor can provide 10-15 inspectors as needed for unplanned patrols for a short duration without negatively impacting schedule. SDG&E’s two tree trim contract companies currently employ a workforce of approximately 120 total crews. Most tree crews include two individuals. The tree contractor workforce is sufficient to respond to unplanned work activities including off-cycle patrols and RFW events. Tree crews may be dispatched for standby in advance of and during RFW events. These determinations are made during resource operations calls which occur before and during events. The number of crews utilized is dependent on the forecasted strength of the event, the expected geographical impact, and the duration.
SDGE-43900-​I-674 | 5.3.5 | NA | NA | In Table 4 regarding the two “Three aerial fire suppression resources available year-round” rows, provide a percentage of drops and gallons used specifically for San Diego Gas & Electric-caused fires. | Table, Narrative | 10 | N | In 2019, SDG&E had twenty-one fires that met the definition of a CPUC reportable ignition. Three of these fires grew over ¼ acre but none required the fire department’s use of the SDG&E supported aerial fire suppression resources to contain. Thus, the answer for both rows is 0%.
SDGE-43900-​I-675 | 5.3.5 | NA | NA | How does SDG&E prioritize vegetation management work (i.e. priority similar to Rule 18, risk ranking, etc.)? | Narrative | 11 | N | Within its vegetation management annual master schedule, SDG&E prioritizes its pre-inspection activities by performing two separate patrols within the HFTD each year, a routine inspection and an off-cycle patrol. The off-cycle patrol, which occurs several months in advance of the routine inspection provides another look to assess and mitigate hazard trees within the HFTD where conditions may have changed in between activities. During the inspection and auditing activities, tree work that is deemed a priority and cannot wait until the routine trim schedule can be completed on a priority basis. This would include trees in close proximity to conductors or trees with a defect that requires urgent abatement. Risk ranking is an element of hazard tree assessment. The inspector considers several factors when assessing risk and determining priority including the extent of defect, known species failure potential, site-specific conditions, trim schedule, etc. Trees that require priority work can be issued to be completed same-day, next-day, within two weeks or within one month from date of inspection.
SDGE-43879-Y-58 | 2.3 -Recent performance on outcome metrics, last 5 years Table 2 Sections 2.1, 2.3, 2.4, 2.6, 2.7, 2.8, 2.9, 2.10, 2.11 | NA | NA | All normalized values must be normalized by the same values per year unless otherwise stated. RFW circuit mile days within the same year should not change on a per metric basis. Must recalculate all fields and link all calculations to Table 10 where RFW circuit mile days are. Update the WMP submission excel and highlight changes. Do not send as a PDF. | Update the WMP submission excel and highlight changes. Do not send as a PDF. | 12 | N | Please refer to the response to WSD DR 2, Item Index SDGE-43895-Y-278, which SDG&E restates below: Based on the instructions provided in the WMP Guidelines, SDG&E does not believe that it miscalculated or used inconsistent normalization in WMP Table 2. To illustrate this, please refer to WMP Table 2, row 1 “near misses” for 2019. SDG&E experienced 1,558 near misses on its overhead system in 2019. SDG&E had a total of 6.46 red flag warning days (RFWD) and has 6,478 miles of overhead distribution system miles. On those 6.46 red flag warning days, SDG&E experienced 29 near misses. The normalizing calculation was 29 near misses on RFWD / 6.46 total RFWD in 2019 / 6478 circuit miles = .0007. In general, this is the formula SDG&E used to normalize by RFWD circuit miles. RFW circuit mile day per year = RFW (near misses, hours, customer minutes, etc.) / number of RFW days / total overhead system circuit miles.) If this is not the expected calculation, please let us know.
SDGE-43879-Y-59 | 3.1 - Weather patterns, last 5 years - RFW circuit mile days per year Table 10 | NA | NA | Determine the correct value for this metric and update if needed. Ensure this is the proper denominator to normalized Table 2 (and other) values throughout WMP submissions. Update the WMP submission excel and highlight changes. Do not send as a PDF. | Update the WMP submission excel and highlight changes. Do not send as a PDF. | 13 | N | Please refer to the response to WSD DR 2, Item Index SDGE-43895-Y-279, which SDG&E restates below: SDG&E has re-checked the data provided in WMP Table 10 and determined that the information as presented is correct. As such, no changes are necessary.
SDGE-43879-Y-60 | 3.3 - Recent use of PSPS, last 5 years Table 12 | NA | NA | All normalized values must be normalized by the same values per year unless otherwise stated. RFW circuit mile days within the same year should not change on a per metric basis. Must recalculate all fields and link all calculations to Table 10 where RFW circuit mile days are. Update the WMP submission excel and highlight changes. Do not send as a PDF. | Update the WMP submission excel and highlight changes. Do not send as a PDF. | 14 | N | Please refer to the response to WSD DR 2, Item Index SDGE-43895-Y-280. The response to Item Index SDGE-43879-Y-58 above restates SDG&E’s explanation of the methodology used to perform the calculation.
SDGE-43879-Y-61 | 3.2 Recent drivers of ignition probability, last 5 years Table 11 Equipment / facility failure | NA | NA | Equipment failure - all types does not represent the same value as the sub of the sub components. This means the numbers must be off, were not segmenteded properly, or some other tabulation error. Ensure that all sub catagories sum to the equipment failure - all types row for all table 11 considerations. Update the WMP submission excel and highlight changes. Do not send as a PDF. | Update the WMP submission excel and highlight changes. Do not send as a PDF. | 15 | N | Please refer to the response to WSD DR 2, Item Index SDGE-43895-Y-281, which SDG&E restates below: Please refer to “Appendix A – WMP Tables 1-31 Revised 03-10-2020 highlighted.xslx.” SDG&E has revised the data in WMP Table 11 to ensure equipment failure total is now the sum of equipment failure rows. This issue occurred due to what SDG&E had interpreted as other totals, such as conductor failure all and fuse failure all. SDG&E separated those rows individually, so that all can now add correctly. SDG&E would suggest that fuse failure conventional be tracked separately, however, as the operation of a fuse is not an equipment failure, and tracking it here artificially inflates the total number of equipment failures.
SDGE-43879-Y-62 | 3.4.3 Status quo ignition probability drivers by service territory Table 18 Equipment / facility failure | NA | NA | Equipment failure - all types does not represent the same value as the sub of the sub components. This means the numbers must be off, were not segmenteded properly, or some other tabulation error. Ensure that all sub catagories sum to the equipment failure - all types row for all table 18 considerations. Update the WMP submission excel and highlight changes. Do not send as a PDF. | Update the WMP submission excel and highlight changes. Do not send as a PDF. | 16 | N | Please refer to the response to WSD DR 2, Item Index SDGE-43895-Y-282, which SDG&E restates below: Please refer to “Appendix A – WMP Tables 1-31 Revised 03-10-2020 highlighted.xlsx.” The data changes from WMP Table 11 were transferred to WMP Table 18, which resolves this issue.
SDGE-43879-Y-63 | 5.3 - Detailed wildfire mitigation programs (All) Tables 21-30 | NA | NA | Replace modified headers with those specified in the WMP template, Report capital expenditure/operating expenditure, and Provide 1 finite number for spending instead of a hi/low range of spend. Update the WMP submission excel and highlight changes. Do not send as a PDF. | Update the WMP submission excel and highlight changes. Do not send as a PDF. | 17 | N | Please refer to the response to WSD DR 2, Item Index SDGE-43895-Y-283, which SDG&E restates below: Please refer to “Appendix A – WMP Tables 1-31 Revised 03-10-2020 highlighted.xlsx.”
SDGE-43879-Y-64 | 3.2 Recent drivers of ignition probability, last 5 years Table 11 Equipment / facility failure 3.4.3 Status quo ignition probability drivers by service territory Table 18 Equipment / facility failure 5.3 - Detailed wildfire mitigation programs (All) Tables 21-30 | NA | NA | Provide the data in the selected tables in the manner demonstrated in the WMP Guidelines. A template will be attached to be filled in. | Update & reformat the WMP submission excel and highlight changes. Do not send as a PDF. | 18 | N | Please refer to “Appendix A – WMP Tables 1-31 Revised 03-10-2020 highlighted.xslx,” which was provided to WSD on March 10, 2020.
SDGE-43895-Y-276 | 2.7 Mapping recent, modelled, and baseline conditions | NA | NA | Provide PSPS event data at the circuit level (i.e., each circuit shut-off in an event should have its own row in the shapefile dataset). The exact schema for the spatial data can be found in the attaced excel file, "20200303_PSPS_schema", in the sheet "PSPS Schema for utilities". "Risk drivers" should be the same across circuits in an event, but all other values should be unique to each circuit. The priority for each field is listed in the "priority" column. An example of the table is provided in the sheet "PSPS Event Template". Table should be organized as shown in "Example onlyPSPS Event Template" sheet with the column names matching "Field Name Shapefile" column in the "Schema" sheet. Each field is explained in the "Field description" column, and type of data for each field is in the "Field Type", and priority of data being received by CPUC is in the "Priority" column | GIS File with same schema as attached (see attached excel file - 20200202_PSPS_schema) | 19 | N | Please refer to attachment: “SDGE-43895-Y-276_20200313_Q19.gdb.7z.” This attachment includes all SDG&E circuit-level PSPS data from 2019 within the provided PSPS schema. Asset risk is not available and thus not provided in the attached. Dead and live fuel values are both included within the FPI and are not considered as a separate risk for PSPS decisions. Other risks are not tracked.
SDGE-43895-Y-277 | 2.7 Mapping recent, modelled, and baseline conditions | NA | FRom WMP: Summarized risk map: Operation wildfire risk reduction model used to prioritize long-term hardening efforts. Referred to on page 48, section 5.3.1.1. From the section: “SDG&E leveraged 30 years of high‐resolution weather data to establish a climate scenario and failure rates of its assets. SDG&E then simulated virtual wildfires to assess, quantify and prioritize risk mitigation efforts. SDG&E also updated risk algorithms to better capture weather effects on failure modes, and how existing hardware is impacted through the integration of wind factors that are applied at higher wind speeds.” | Provide the most recent map of overhead distribution, transmission, and substation facilities (as was provided earlier) in entire utility region with additional fields for… 1. Ignition probability – projected likelihood of target asset causing an ignition in the next year (0.0 – 1.0) 2. Failure probability – projected likelihood of target asset failing in the next year (0.0 – 1.0) 3. Wildfire spread and consequence score (normalized from 0.0 – 1.0) – relative ability ignition spread and quantity of homes or timber affected if ignition occurs 4. Prioritization ranking of assets for maintenance – calculated ranking of assets for prioritizing asset maintenance, upgrades, and equipment replacement. This is a percentile ranking with 99th percentile being highest priority and 0th percentile being lowest priority for asset maintenance 5. Any remaining data for circuit risk levels (including vegetation risk index data) for all transmission lines and distribution lines | GIS File | 20 | N | Please refer to the response to WSD DR 2, Item Index SDGE-43895-Y-277, which SDG&E restates below: SDG&E utilizes the Wildfire Risk Reduction Model (WRRM) to perform live modeling of the ignition probability and failure rates of assets summed up to the circuit level given the current meteorological and fuel conditions within the service territory. This tool was designed as an operational tool and currently does not contain an export capability to provide this data within a GIS file. SDG&E will work with its vendor Technosylva to develop an export solution to provide this data at a later date.
SDGE-43903-Y-5 | 6.6: Planned 2020 WMP initiative activity per year | NA | NA | Provide planned initiative data at the most granular level possible for each initiative activity (e.g., each asset location for each activity under an initiative). The exact schema for the spatial data can be found in the attaced excel file, "20200311_Initiative_schema", in the sheet "Initiative schema for utilities". The priority for each field is listed in the "priority" column. An example of the table is provided in the sheet "Initiative Template". Table should be organized as shown in "Initiative Template" sheet with the column names matching "Field Name Shapefile" column in the "Schema" sheet. Each field is explained in the "Field description" column, and type of data for each field is in the "Field Type". Attached to this dataset should be lat/lon points corresponding to each row in the data | GIS File with same schema as attached (see specfic data request) | 21 | N | SDG&E anticipates providing a response to this item by March 20, 2020. Please see attachment: “SDGE-43903-Y-5_20200313_Q21.gdb.7z.”
SDGE-43903-Y-6 | 5.3.4 Asset management and inspections | NA | NA | Provide asset spatial data at the individual asset level for each of the asset categories listed (substations, weather stations, capacitor banks, conductors, poles, transmission lines and distribution lines). The exact schema for the spatial data can be found in the attaced excel file, "20200311_Asset_schema", in the sheets "Asset schema for utils - points" and "Asset schema for utils - lines". The priority for each field is listed in the "priority" column. An example of the table is provided in the "Asset Template" sheets. Table should be organized as shown in "Asset Template" sheets with the column names matching "Field Name Shapefile" column in the "Schema" sheet. Each field is explained in the "Field description" column, and type of data for each field is in the "Field Type". Attached should be two spatial files, one for points data and one for lines data, where each dataset should have its respective shape features (lat/lon points or lines) corresponding to each row in the data | GIS Files with same schema as attached (see specfic data request) - one for lines and one for points | 22 | N | SDG&E anticipates providing a response to this item by March 20, 2020. Please see attachment: “SDGE-43903-Y-6_20200313_Q22.gdb.7z.” and CONFIDENTIAL attachment: “CONFIDENTIAL SDGE-43903-Y-6_20200313_Q22.gdb.7z.” SDG&E did not update the date format for the installation date field as doing so would have an impact to many, if not all, of the internal system integrations with GIS. SDG&E utilizes the Wildfire Risk Reduction Model (WRRM) to perform live modeling of the ignition probability and failure rates of assets summed up to the circuit level given the current meteorological and fuel conditions within the service territory. This tool was designed as an operational tool and currently does not contain an export capability to provide this data within a GIS file. SDG&E will work with its vendor Technosylva to develop an export solution to provide this data at a later date.