## Table 1
TABLE 1: Recent Performance on Progress Metrics, Last 5 Years
Project Metric Name | Annual Performance |  |  |  |  | Unit(s)
| 2015 | 2016 | 2017 | 2018 | 2019
Grid condition findings from inspection- Electric Transmission | Issues in FTZ / FTZ Circuit Miles in 2015 Inspection Type Level 1 Level 2 Level 3 Type 1 0.000 0.013 0.000 Type 2 0.000 0.298 0.009 Type 3 0.000 0.010 0.000 Issues/ Total Circuit Miles in 2015 Inspection Type Level 1 Level 2 Level 3 Type 1 0.001 0.035 0.000 Type 2 0.002 0.533 0.031 Type 3 0.003 0.034 0.000 | Issues in FTZ / FTZ Circuit Miles in 2016 Inspection Type Level 1 Level 2 Level 3 Type 1 0.000 0.001 0.000 Type 2 0.000 0.044 0.002 Type 3 0.000 0.010 0.000 Issues/ Total Circuit Miles in 2016 Inspection Type Level 1 Level 2 Level 3 Type 1 0.000 0.021 0.000 Type 2 0.001 0.156 0.032 Type 3 0.001 0.023 0.000 | Issues in FTZ / FTZ Circuit Miles in 2017 Inspection Type Level 1 Level 2 Level 3 Type 1 0.000 0.002 0.000 Type 2 0.000 0.043 0.010 Type 3 0.000 0.001 0.017 Issues/ Total Circuit Miles in 2017 Inspection Type Level 1 Level 2 Level 3 Type 1 0.001 0.006 0.000 Type 2 0.001 0.226 0.033 Type 3 0.001 0.009 0.009 | Issues in HFTD / HFTD Circuit Miles in 2018 Inspection Type Level 1 Level 2 Level 3 Type 1 0.000 0.009 0.000 Type 2 0.002 0.413 0.029 Type 3 0.000 0.006 0.000 Issues/ Total Circuit Miles in 2018 Inspection Type Level 1 Level 2 Level 3 Type 1 0.000 0.005 0.000 Type 2 0.004 0.445 0.032 Type 3 0.000 0.005 0.000 | Issues in HFTD / HFTD Circuit Miles in 2019 Inspection Type Level 1 Level 2 Level 3 Type 1 0.000 0.004 0.000 Type 2 0.000 0.228 0.026 Type 3 0.000 0.009 0.000 Issues/ Total Circuit Miles in 2019 Inspection Type Level 1 Level 2 Level 3 Type 1 0.000 0.004 0.000 Type 2 0.001 0.338 0.026 Type 3 0.004 0.013 0.000 | Number of Level 1, 2, and 3 findings per mile of circuit in HFTD, and per total miles of circuit for each of the following inspection types: 1. Patrol inspections 2. Detailed inspections 3. Other inspection types
Grid condition findings from inspection- Electric Distribution | Issues in FTZ / FTZ Circuit Miles in 2015 Inspection Type Level 1 Level 2 Level 3 Patrol 0.008 0.049 NA Detail 0.0014 0.1929 NA QC 0.0006 0.2408 NA Issues/ Total Circuit Miles in 2015 Inspection Type Level 1 Level 2 Level 3 Patrol 0.0070 0.1059 NA Detail 0.0097 0.3856 NA QC 0.0001 0.0505 NA | Issues in FTZ / FTZ Circuit Miles in 2016 Inspection Type Level 1 Level 2 Level 3 Patrol 0.0083 0.0596 NA Detail 0.0049 0.1408 NA QC 0.0003 0.1958 NA Issues/ Total Circuit Miles in 2016 Inspection Type Level 1 Level 2 Level 3 Patrol 0.0055 0.1328 NA Detail 0.0069 0.3575 NA QC 0.0001 0.0411 NA | Issues in FTZ / FTZ Circuit Miles in 2017 Inspection Type Level 1 Level 2 Level 3 Patrol 0.0017 0.0602 NA Detail 0.0011 0.0659 NA QC 0.0009 0.1032 NA Issues/ Total Circuit Miles in 2017 Inspection Type Level 1 Level 2 Level 3 Patrol 0.0058 0.1311 NA Detail 0.0044 0.3005 NA QC 0.0002 0.0217 NA | Issues in HFTD / HFTD Circuit Miles in 2018 Inspection Type Level 1 Level 2 Level 3 Patrol 0.008 0.043 NA Detail 0.0009 0.0614 NA QC 0.0003 0.1775 NA Issues/ Total Circuit Miles in 2018 Inspection Type Level 1 Level 2 Level 3 Patrol 0.0041 0.1269 NA Detail 0.0074 0.2984 NA QC 0.0001 0.0372 NA | Issues in HFTD/ HFTD Circuit Miles in 2019 Inspection Type Level 1 Level 2 Level 3 Patrol 0.002 0.1216 NA Detail 0.0011 0.0648 NA QC 0.0003 0.0665 NA Issues/ Total Circuit Miles in 2019 Inspection Type Level 1 Level 2 Level 3 Patrol 0.0031 0.1263 NA Detail 0.0039 0.3770 NA QC 0.0001 0.0140 NA | Number of Level 1, 2, and 3 findings per mile of circuit in HFTD, and per total miles of circuit for each of the following inspection types: 1. Patrol inspections 2. Detailed inspections 3. Other inspection types
Vegetation clearance findings from inspection | 0.8% | 0.7% | 1.1% | 0.1% | 0.8% | Percentage of right-of-way with noncompliant clearance based on applicable rules and regulations at the time of inspection, as a percentage of all right-of-way inspected. *NOTE: “Noncompliant” - a tree observed during inspection to have less than the minimum clearance required (“memo” tree) "All right-of-way inspected” – total number of inventory trees % of noncompliance = number of memo trees observed divided by the total number of inventory trees.
Extent of grid modularization | 1. FTZ: 0.066 2. Non-FTZ: 0.059 | 1. FTZ: 0.071 2. Non-FTZ: 0.092 | 1. FTZ: 0.072 2. Non-FTZ: 0.094 | 1. HFTD: 0.072 2. Non-HFTD: 0.099 | 1. HFTD: 0.073 2. Non-HFTD: 0.100 | Number of sectionalizing devices per circuit mile plus number of automated grid control equipment in: 1. HFTD 2. Non-HFTD *NOTE: Per Total number of sectionalizing positions (OH and UG, UG can have between 2-5 per device) divided by total miles (OH and UG)
Data collection and reporting | NA | NA | NA | NA | 95% | Missing Table 31 and 50% of table 9. The submittal was calculated as providing data for 29.5/31 tables, or 95% complete.

## Table 2
TABLE 2: Recent Performance on Outcome Metrics, Annual and Normalized for Weather, Last 5 Years
Metric Type | # | Outcome metric name | Annual performance |  |  |  |  | Unit(s) | Comments
|  |  | 2015 | 2016 | 2017 | 2018 | 2019
1. Near misses | 1.a. | # of all events that could result in ignition, by type according to utility-provided list (Total) | 1509 | 1841 | 1751 | 1594 | 1558 | Number per year | (Such as unplanned outages, faults, conventional blown fuses, etc.)
| 1.b. | # of all events that could result in ignition, by type according to utility-provided list (Normalized) | 0.00032216 | 0.00081507 | 0.0013975 | 0.0019748 | 0.00074097 | Number per RFW circuit mile day per year
| 1.c. | Number of wires down (total) | 59 | 138 | 129 | 96 | 108 | Number of wires down per year | System wide
| 1.d. | Number of wires down(normalized) | 0 | 4e-05 | 4e-05 | 3e-05 | 5e-05 | Number per RFW circuit mile day per year
2. Utility inspection findings | 2.a. | Number of Level 1 findings that could increase the probability of ignition discovered per circuit mile inspected | 0.010 (ED) | 0.013(ED) | 0.004(ED) | 0.009 (ED) | 0.003(ED) | Average number of Level 1 findings that could increase the probability of ignition discovered by all inspections per circuit mile per year | Substation findings do not increase the probability of ignitions per circuit mile; Substation inspections are conducted primarily for reliability, they have incidental wildfire mitigation benefits.
| 2.b. | Number of Level 2 findings | 0.483 (ED) | 0.396(ED) | 0.229(ED) | 0.282(ED) | 0.253(ED) | Average number of Level 2 findings
| 2.c. | Number of Level 3 findings | 0 | 0 | 0 | 0 | 0 | Average number of Level 3 findings
3. Customer hours of PSPS and other | 3.a. | Customer hours of planned outages including PSPS (total) | 1010005 | 862687 | 1884251 | 2185302 | 2395433 | Total customer hours of planned outages per year
| 3.b. | Customer hours of planned outages including PSPS (normalized) | 0.1703 | 0.0006 | 7.1353 | 17.3915 | 30.3882 | Total customer hours of planned outages per RFW circuit mile day per year
| 3.c. | Customer hours of unplanned outages, not including PSPS (total) | 1504042 | 2058237 | 2090995 | 1887418 | 1617201 | Total customer hours of unplanned outages per year
| 3.d. | Customer hours of unplanned outages, not including PSPS (normalized) | 80.76 | 21.79 | 19.61 | 30.8 | 38.65 | Total customer hours of unplanned outages per RFW circuit mile day per year
| 3.e. | Increase in System Average Interruption Duration Index (SAIDI) | -12.55 | 22.75 | 31.48 | 3.53 | -2.94 | Change in minutes compared to the previous year
4. Utility ignited wildfire fatalities | 4.a. | Fatalities due to utility-ignited wildfire (total) | 0 | 0 | 0 | 0 | 0 | Number of fatalities per year | SDG&E is unaware of any utility-ignited wildfire fatalities resulting from utility wildfire mitigation initiatives in the period 2015-2019.
| 4.b. | Fatalities due to utility-ignited wildfire (normalized) | 0 | 0 | 0 | 0 | 0 | Number of fatalities per RFW circuit mile day per year
5. Accidental deaths resulting from utility wildfire mitigation initiatives | 5.a. | Deaths due to utility wildfire mitigation activities (total) | 0 | 0 | 0 | 0 | 0 | Number of fatalities per year | SDG&E is unaware of any accidental deaths resulting from utility wildfire mitigation initiatives in the period 2015-2019.
6. OSHA-reportable injuries from utility wildfire mitigation initiatives | 6.a. | OSHA-reportable injuries due to utility wildfire mitigation activities (total) | 0 | 1 | 0 | 0 | 0 | Number of OSHA-reportable injuries per year | One contractor OSHA-reportable injury in 2016 related to the FiRM (Fire Risk Mitigation) project. It is the responsibility of the contractor to report the incident to OSHA; SDG&E has no documentation to confirm such a report.
| 6.b. | OSHA-reportable injuries due to utility wildfire mitigation activities (normalized) | 0 | 0.001 | 0 | 0 | 0 | Number of OSHA-reportable injuries per year per 1000 line miles of grid
7. Value of assets destroyed by utility-ignited wildfire, listed by asset type | 7.a. | Value of assets destroyed by utility-ignited wildfire (total) | 0 | 0 | 0 | 2900 | 0 | Dollars of damage or destruction per year | Value is a round number including material only for one wood 45' pole, and 25kVA transformer. Rounded up, to compenstate for additonal conductor and connectors.
| 7.b. | Value of assets destroyed by utility-ignited wildfire (normalized) | 0 | 0 | 0 | 0.043729 | 0
8. Structures damaged or destroyed by utility-ignited wildfire | 8.a. | Number of structures destroyed by utility-ignited wildfire (total) | 0 | 0 | 0 | 1 | 0 | Number of structures destroyed per year
| 8.b. | Number of structures destroyed by utility-ignited wildfire (normalized) | 0 | 0 | 0 | 1.51e-05 | 0 | Number of structures destroyed per RFW circuit mile day per year
9. Acreage burned by utility-ignited wildfire | 9.a. | Acreage burned by utility-ignited wildfire (total) | 213 | 7 | 16 | 28 | 8 | Acres burned per year | If a fire meets the CPUC definitiof for recorable fire but does not grow beyond .25 acres it was assumed to be .1 acres for consistency
| 9.b. | Acreage burned by utility-ignited wildfire (normalized) | 0.2458 | 0.00022594 | 0.00018017 | 0.00042221 | 0.0002369 | Acres burned per RFW circuit mile day per year
10. Number of utility wildfire ignitions | 10.a. | Number of ignitions (total) according to existing ignition data reporting requirement | 32 | 30 | 23 | 26 | 21 | Number per year
| 10.b. | Number of ignitions (normalized) | 0.036928 | 0.00096832 | 0.00025899 | 0.00039206 | 0.00062187 | Number per RFW circuit mile day per year
| 10.c. | Number of ignitions in HFTD (subtotal) | 19 | 18 | 15 | 13 | 11 | Number in HFTD per year
| 10.c.ii. | Number of ignitions in HFTD Tier 2 | 13 | 11 | 7 | 7 | 8 | Number in HFTD Tier 2 per year
| 10.c.iii. | Number of ignitions in HFTD Tier 3 | 6 | 7 | 8 | 6 | 3 | Number in HFTD Tier 3 per year
| 10.d. | Number of ignitions in HFTD (subtotal, normalized) | 0.036928 | 0.03462 | 0.026542 | 0.030004 | 0.024234 | Number in HFTD per RFW circuit mile day per year
| 10.d.ii. | Number of ignitions in HFTD Tier 2 (normalized) | 0.015002 | 0.012694 | 0.008078 | 0.008078 | 0.009232 | Number in HFTD Tier 2 per RFW circuit mile day per year
| 10.d.iii. | Number of ignitions in HFTD Tier 3 (normalized) | 0.006924 | 4.0973e-07 | 9.0962e-08 | 1.2181e-07 | 2.7339e-07 | Number in HFTD Tier 3 per RFW circuit mile day per year
| 10.e. | Number of ignitions in non-HFTD (subtotal) | 13 | 12 | 8 | 13 | 10 | Number in non-HFTD per year
| 10.f. | Number of ignitions in non-HFTD (normalized) | 0.015002 | 0.00038733 | 9.0083e-05 | 0.00019603 | 0.00029613 | Number in non-HFTD per RFW circuit mile day per year
11. Critical infrastructure impacted | 11.a. | Critical infrastructure impacted by PSPS | NA | NA | NA | NA | 76236 | Number of critical infrastructure (in accordance with D.19-05-042) locations impacted per hour multiplied by hours offline per year
| 11.b. | Critical infrastructure impacted by PSPS (normalized) | NA | NA | NA | NA | 1.46 | Number of critical infrastructure (in accordance with D.19-05-042) locations impacted per hour multiplied by hours offline per RFW circuit mile day per year

## Table 3
TABLE 3: List and Description of Additional Metrics, Last 5 Years
Metric | Performance |  |  |  |  | Units | Third-party validation | Underlying assumptions
| 2015 | 2016 | 2017 | 2018 | 2019
Number of elevated or extreme FPI and RFW days | FPI: 108 RFW: 4 | FPI: 138 RFW: 20 | FPI: 169 RFW: 21 | FPI: 182 RFW: 12 | FPI: 137 RFW: 12 | Days | NA | Day ends at 2359L (11:59pm) and begins at 0000L (midnight)
Vegetation Caused Ignitions in HFTD | FPI: 3 RFW:0 | FPI: 1 RFW: 0 | FPI: 2 RFW: 1 | FPI: 0 RFW: 0 | FPI: 1 RFW: 0 | Days | NA
Vegetation Caused Outages within HFTD | FPI: 3 RFW: 0 | FPI: 7 RFW: 0 | FPI: 8 RFW: 2 | FPI: 4 RFW: 3 | FPI: 9 RFW: 0 | Days | NA
Equipment Caused Ignitions within HFTD | FPI: 2 RFW: 0 | FPI: 5 RFW: 0 | FPI: 4 RFW: 2 | FPI: 2 RFW: 1 | FPI: 2 RFW: 0 | Days | NA
Overhead Faults on Circuits within HFTD | FPI: 121 RFW: 0 | FPI: 110 RFW: 15 | FPI: 145 RFW: 29 | FPI: 134 RFW: 28 | FPI: 125 RFW:17 | Days | NA
Energized Wire Down Events within HFTD | FPI: 3 RFW: 0 | FPI: 7 RFW: 0 | FPI: 9 RFW: 0 | FPI:7 RFW: 1 | FPI:8 RFW: 1 | Days | NA
Number of Non-CALFIRE Rated Fuse Operations within HFTD | FPI: 96 RFW: 1 | FPI: 108 RFW:24 | FPI: 115 RFW: 16 | FPI: 131 RFW: 14 | FPI: 83 RFW: 9 | Days | NA

## Table 4
TABLE 4: List and Description of Program Targets, Last 5 Years
Program target | 2019 performance | Units | Underlying assumptions | Third-party validation
Changed operating procedures on days with elevated or higher FPI | 137 | FPI elevated or higher | Target is 100% of elevated or higher FPI days. Number of elevated or higher FPI days will vary depending on weather conditions. | No
Disable reclosing and enable sensitive protections on reclosers within HFTD on days with elevated or higher FPI | 137 | FPI elevated or higher |  | No
Electric crews accompanied by fire suppression crews on days with elevated or higher FPI. On extreme days, certain activities are stopped altogether within the HFTD. | 137 | FPI elevated or higher |  | No
Wildfire infrastructure teams join SDG&E electric crews to provide fire suppression capabilities during high risk work on days with elevated or higher FPI. Support re-energization during PSPS events. | 137 | FPI elevated or higher |  | No
Three aerial fire suppression resources available year-round | 279 | water drops | The metric for this program is the number of water drops per year, which shows frequency of use for aerial fire suppression resources. Number of gallons dropped is also recorded. A target metric is not provided since the number of fires that aerial fire suppression resources will combat per year is unknown. | No
Three aerial fire suppression resources available year-round | 220453 | gallons of water |  | No
Perform fuel management on BLM, priority 13, and tier 3 including CNF poles | 511 | poles treated | SDG&E's fuels management program removes, thins, or treats vegetation along SDG&E rights of way and adjacent fire-prone corridors. | No
15,000 QA/QC Distribution System Inspections | 15176 | poles inspected | SDG&E's QA/QC distribution system inspections are performed within the HFTD Tier 3 prior to fire season and exceed the requirements of GO 165. | No
47,850 Detailed Distribution System Inspections | 47850 | poles inspected | SDG&E's detailed distribution system inspections are conducted in compliance with GO 165. | No
300 Substation System Inspections | 301 | substations inspected | SDG&E's substation system inspections are conducted in compliance with GO 174. | No
6,730 Transmission System Inspections | 6730 | OH structures inspected | SDG&E's transmission system inspections are conducted in compliance with PRC § 4292 and 4293 and GO 95 and GO 128 rules. | No
10 miles of OH transmission hardened | 10 | miles hardened | SDG&E program targets are set with +/-20% range to allow for unforseen impacts from external forces. The program target here is the midpoint of that range, and the number of miles hardened is within the 20% threshold. | No
85 miles of OH distribution hardened | 83 | miles hardened | SDG&E program targets are set with +/-20% range to allow for unforseen impacts from external forces. The program target here is the midpoint of that range, and the number of miles hardened is within the 20% threshold. | No
1.5 miles underground line segments | 2.6 | miles undergrounded | Strategic undergrounding began as a small scale program to target areas of the HFTD with the most significant risk. In 2019, SDG&E exceeded the goal of 1.5 miles undergrounded significantly reducing ignition risks in those areas. | No
68 miles hardened within Cleveland National Forest | 61 | miles hardened | SDG&E program targets are set with +/-20% range to allow for unforseen impacts from external forces. The program target here is the midpoint of that range, and the number of miles hardened is within the 20% threshold. | No
85 miles of high-risk conductor replaced with high tensile strength conductor | 82 | miles replaced | SDG&E program targets are set with +/-20% range to allow for unforseen impacts from external forces. The program target here is the midpoint of that range, and the number of miles hardened is within the 20% threshold. | No
700 poles hardened | 695 | poles hardened | SDG&E program targets are set with +/-20% range to allow for unforseen impacts from external forces. The program target here is the midpoint of that range, and the number of poles hardened is within the 20% threshold. | No
2250 expulsion fuses replaced | 2490 | fuses replaced | SDG&E program targets are set with +/-20% range to allow for unforseen impacts from external forces. The program target here is the midpoint of that range, and the number of devices replaced is within the 20% threshold. | No
500 hotline clamps replaced | 660 | hotline clamps replaced | Hotline clamps are a recognized high-risk connector that can lead to a wire down event. The overall goal of this program is to replace all 8,500 hotline clamps within the SDG&E's HFTD by the year 2024. | No
5.7 miles of wire safety enhancements | 5.7 | miles enhanced | The WiSE program replaced small conductor with high failure rates within the wildland urban interface. | No
8 circuits enabled with falling conductor protection | 8 | circuits enabled | SDG&E expanded its deployment of advanced protection to eight distribution circuits in the backcountry and tested and validated the communication functionality of its proposed Distribution Communications Reliability Improvements. | No
7 switches installed | 7 | switches installed | SDG&E installed seven additional switches to further increase is sectionalizing capability within the HFTD. | No
Replace all poles found through the GO195 visual and instrusive inspections within the HFTD | 725 | poles replaced | SDG&E's pole replacement and reinforcement is conducted in compliance with GO 165. For poles identified for replacement in Tier 3 of the HFTD, SDG&E intends to accelerate the replacement faster than the six-month time frame require by the comission's general orders. | No
Fit all 9 Community Resource Centers with a transfer switch to facilitate backup generation | 9 | CRC transfer switches installed | This metric tracked the CRC's ability to connect to backup power generators during a PSPS event. | No
Offer backup generators to all identified medical baseline customers and train them on its use (79 identified) | 79 | medical baseline customers offered backup generators | The goal of the program was to offer generators and training on generator use to MBL customers. 14 MBL customers while offered, chose not to participate. | No
Maintain inventory of trees within SDG&E service territory | 460000 | trees in inventory | Tree inventory contains tree data for the entire service territory. | No
Enhanced 25-foot post prune clearance or complete removal of 81,000 trees along 28 circuits | 28 | Circuits with enhanced 25-foot clearance complete | SDG&E performs enhanced 25-foot clearance post-prune between trees and electric facilities within the HFTD. | No
Complete Quality Assurance of HFTD audits | 80% | percent complete | SDG&E conducts QA/QC audits on a random sample population of all work completed by its contractors to assess work quality and contractual adherance. | No
Hazard tree removal | 9884 | trees removed | SDG&E's tree removal program targets problematic species such as eucalyptus and palms. SDG&E offers free tree replacements if an existing tree cannot be maintained safely near power lines. | No
Hazard tree replacement | 260 | trees replaced |  | No
Mechanical brushing and chemical applications | 100% | percent complete | The current inventory of poles within the state responsibility area that require inspection and brush clearing is approximately 31,000 distribution poles with non-exempt subject hardware. For poles that require brushing as determined by the inspector, SDG&E performs three activities annually including mechanical brushing, chemical application, and a re-clearing of pole brushing. | No
Re-clear cycle | 100% | percent complete |  | No
Provide electric equipment training to CalFire personnel through joint inspections | 0 | joint inspections | SDG&E was unable to provide training this year due to unavailability of Cal Fire personnel. SDG&E intends to resume this activity in 2020. | No
Expand SDG&E's weather network | 191 | total weather stations | SDG&E's weather network is located strategically throughout its service territory. The weather information is used to calibrate models such as the FPI and the SDG&E Outage Prediction Model which gives SDG&E the ability to anticipate when critical fire weather conditions or strong storms are approaching the area, allowing proactive preparedness measures to be taken. | No
Publish fire simulations | 29 | fire simulations published | WRRM-Ops is capable of simulating the growth and potential impact of a wildfire anywhere in SDG&E's service territory should an ignition begin. | No
Install 500 wireless fault indicators | 594 | wireless fault indicators installed | SDG&E program targets are set with +/-20% range to allow for unforseen impacts from external forces. The program target here is the midpoint of that range, and the number of devices installed is within the 20% threshold. | No
Add 13 weather stations | 13 | weather stations | SDG&E continues to add new weather stations to strategic locations to provide more granular weather data. | No
Install software enhancements on weather stations to allow 30 second reads | 105 | weather stations with software installed | Software upgrades to existing weather stations to allow for more frequent weather data for increased situational awareness. | No
Utilize PSPS as a last resort mitigation during the most extreme weather events of the year | 3 | events including activations of PSPS protocols | SDG&E utilizes PSPS as a last resort mitigation during the most extreme weather events of the year. During the wind events of October 2019, SDG&E utilized PSPS on three occasions. | No
Implement notification in five languages for potential and impending PSPS events utilizing multiple channels of communication | 8 | languages implemented for PSPS notifications | SDG&E communicates with customers in advance of an event; upon starting safety inspections of affected power lines; and upon re-energization, as practicable. SDG&E communicates these notifications to customers in eight languages (English, Spanish, Mandarin, Cantonese, Vietnamese, Korean, Tagalog and Russian.) | No

## Table 5
TABLE 5: Accidental Deaths Due to Utility Wildfire Mitigation Initiatives, Last 5 Years
Activity | Victim | [14 empty] | Total
| Full-time employee |  |  |  |  | Contractor |  |  |  |  | Member of public
Year | 2015 | 2016 | 2017 | 2018 | 2019 | 2015 | 2016 | 2017 | 2018 | 2019 | 2015 | 2016 | 2017 | 2018 | 2019
Inspection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
Vegetation management | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
Utility fuel management | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid hardening | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1

## Table 6
TABLE 6: OSHA-Reportable Injuries Due to Utility Wildfire Mitigation Initiatives, Last 5 Years
Activity | Victim | [14 empty] | Total
| Full-time employee |  |  |  |  | Contractor |  |  |  |  | Member of public
Year | 2015 | 2016 | 2017 | 2018 | 2019 | 2015 | 2016 | 2017 | 2018 | 2019 | 2015 | 2016 | 2017 | 2018 | 2019
Inspection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vegetation management | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
Utility fuel management | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid hardening | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1

## Table 7
TABLE 7: Methodology for Potential Impact of Ignitions
List of all data inputs used in impact simulation | Sources of data inputs | Data selection and treatment methodologies | Assumptions, including SME input | Equation(s), functions, or other algorithms used to obtain output | Output type(s), e.g., wind speed model | Comments
Wind Speed | Wx Modeling | NAM, WRF, 2km grid | Best availiable Wx data | WRF | hourly for 84 hours - 2km grid in MPH | Wx = Weather NAM = North American Model WRF = Weather Research & Forecasting Model
Wind Direction | Wx Modeling | NAM, WRF, 2km grid | Best availiable Wx data | WRF | hourly for 84 hours - 2km grid in degrees
Temperature | Wx Modeling | NAM, WRF, 2km grid | Best availiable Wx data | WRF | hourly for 84 hours - 2km grid in F
Relative Humidity | Wx Modeling | NAM, WRF, 2km grid | Best availiable Wx data | WRF | hourly for 84 hours - 2km grid in %
Moisture 1hr (%) | FM Modeling | NAM, WRF, Nelson, 2km grid | Nelson is leading practice | Nelson Fuel Model | hourly for 84 hours - 2km grid in % | FM = Fuel Moisture
Moisture 10hr (%) | FM Modeling | NAM, WRF, Nelson, 2km grid | Nelson is leading practice | Nelson Fuel Model | hourly for 84 hours - 2km grid in %
Moisture 100hr (%) | FM Modeling | NAM, WRF, Nelson, 2km grid | Nelson is leading practice | Nelson Fuel Model | hourly for 84 hours - 2km grid in %
Live Fuel Moisture (%) | FM Modeling | NAM, WRF, AI, 2km grid | Leading state-of-science | Custom AI | hourly for 84 hours - 2km grid in %
Greeness | FM Modeling | NLDAS, 2km grid | Leading state-of-science | Custom Regression | hourly for 84 hours - 2km grid in %
Energy Release Component | FM Modeling | NAM, WRF, Nelson, 2km grid | NFDRS16 is leading practice | NFDRS | hourly for 84 hours - 2km grid in btu/sqft | FB = Fire Behavior
Flame Length | FB Modeling | Wildfire Analyst | Leading state-of-science | Rothermel | hourly for 84 hours - 2km grid in ft
Surface Fuel Height | Remote Sensing | N/A | Leading state-of-science | Satellite Image Analysis | static 25ft grid
Slope | Remote Sensing | N/A | Leading state-of-science | Satellite Image Analysis | static 25ft grid
Rate of Spread | FB Modeling | Wildfire Analyst | Leading state-of-science | Rothermel | hourly for 84 hours - 2km grid in (ch/h)
Fuel Type | Remote Sensing | Wildfire Analyst | Leading state-of-science | Satellite Image Analysis | static 25ft grid
Arrival Time | FB Modeling | Wildfire Analyst | Leading state-of-science | Rothermel | hourly for 84 hours - 2km grid in (h)
Flame Intensity | FB Modeling | Wildfire Analyst | Leading state-of-science | Rothermel | hourly for 84 hours - 2km grid in (btu/ft/s)
Structures | Land Use Model | Most recent | Additional structures added through anaysis | N/A | # of structures
Population | Census Data | Most Recent | N/A | N/A | # of population
Utility Assetts | GIS | N/A | Updated regularly | N/A | # and type

## Table 8
TABLE 8: Map File Requirements for Recent and Modelled Conditions of Utility Service Territory, Last 5 Years
Layer name | Measurements | Units | Attachment Location
Recent weather patterns | Average annual number of Red Flag Warning days per square mile across service territory | Area, days, square mile resolution | 6.1
| Average 95th and 99th percentile wind speed and prevailing direction (actual) | Area, miles per hour, at a square mile resolution or better, noting where measurements are actual or interpolated
Recent drivers of ignition probability | Date of recent ignitions categorized by ignition probability driver | Point, GPS coordinate, days, square mile resolution | 6.2
Recent use of PSPS | Duration of PSPS events and area of the grid affected in customer hours per year | Area, customer hours, square mile resolution | 6.3

## Table 9
TABLE 9: Map File Requirements for Baseline Condition of Utility Service Territory Projected for 2020
Layer name | Measurements / variables | Units | Appendix location
Current baseline state of service territory and utility equipment | Non-HFTD vs HFTD (Zone 1, Tier 2, Tier 3) regions of utility service territory | Area, square mile resolution per type | 6.4
| Urban vs. rural vs. highly rural regions of utility service territory | Area, square mile resolution per type
| WUI regions of utility service territory | Area, square mile resolution
| Number and location of critical facilities | Point, GPS coordinate
| Number and location of customers | Area, number of people, square mile resolution
| Number and location of customers belonging to access and functional needs populations | Area, number of people, square mile resolution
| Overhead transmission lines | Line, quarter mile resolution
| Overhead distribution lines | Line, quarter mile resolution
| Location of substations | Point, GPS coordinate
| Location of weather stations | Point, GPS coordinate
| All utility assets by asset type, model, age, specifications, and condition | Point, GPS coordinate
Location of planned utility equipment additions or removal | Non-HFTD vs HFTD (Zone 1, Tier 2, Tier 3) regions of utility service territory | Line, quarter mile resolution | 6.5
| Urban vs. rural vs. highly rural regions of utility service territory | Line, quarter mile resolution
| WUI regions of utility service territory | Line, quarter mile resolution
| Circuit miles of overhead transmission lines | Line, quarter mile resolution
| Circuit miles of overhead distribution lines | Line, quarter mile resolution
| Location of substations | Point, GPS coordinate
Planned 2020 WMP initiative activity per year | Location of 2020 WMP initiative activity for each activity as planned to be completed by the end of each year of the plan term | Line, quarter mile resolution | 7.6

## Table 10
TABLE 10: Weather Patterns, Last 5 Years
Weather measurement | 2015 | 2016 | 2017 | 2018 | 2019 | 5yr Historical Average | Unit(s)
Red Flag Warning days | 6816.99 | 25733.11 | 57729.96 | 45604.06 | 26532.72 | 32483.37 | RFW circuit mile days per year
Days rated at the top 30% of proprietary fire potential index or similar fire risk index measure | 0 | 18271 | 56522 | 38960 | 27531 | 28256.8 | Circuit mile days where proprietary measure rated above top 30% threshold1 per year
95th percentile wind conditions | 27449.61 | 30047.93 | 32220.56 | 30511.59 | 31338.92 | 30313.72 | Circuit mile days with wind gusts over 95th percentile historical (meaning the prior 10 years, 2005-2014) conditions per year
99th percentile wind conditions | 7788.81 | 4454.58 | 10260.31 | 9995.22 | 9283.79 | 8356.54 | Circuit mile days with wind gusts over 99th percentile historical (meaning the prior 10 years, 2005-2014) conditions per year
1 Threshold here defined as top 30% of FPI or equivalent scale (e.g., “Extreme” on SCE’s FPI; “extreme”, 15 or greater, on SDG&E’s FPI; and 4 or above on PG&E’s FPI), .
*Notes: - RFW days were calculated using the number of miles of transmission and distribution lines in the HFTD, multiplied by number of days per zone a RFW was in effect. - FPI days were calculated using the number of days per SDG&E district with an Extreme FPI, multiplied by the number of HFTD transmission and distribution miles within that district - Percentile wind conditions were calculated using the measured 95th and 99th percentile winds at SDG&E weather stations.

## Table 11
TABLE 11a Distribution: Key Recent Drivers of Ignition Probability, Last 5 Years
Incident type by ignition probability driver |  | Near misses tracked (y/n)? | Number of Incidents per year | [5 empty] | Avg % probability of ignition per incident | [5 empty] | Ignition per year caused by driver
|  |  | 2015 | 2016 | 2017 | 2018 | 2019 | Average | 2015 | 2016 | 2017 | 2018 | 2019 | Average | 2015 | 2016 | 2017 | 2018 | 2019 | Average
Contact from object | All types of object contact | Yes | 445 | 498 | 514 | 509 | 538 | 500.8 | 4.045% | 2.811% | 2.918% | 2.554% | 0.7435% | 2.556% | 18 | 14 | 15 | 13 | 4 | 12.8
| Animal contact | Yes | 73 | 79 | 83 | 81 | 98 | 82.8 | 0% | 2.532% | 1.205% | 1.235% | 1.02% | 1.208% | 0 | 2 | 1 | 1 | 1 | 1
| Balloon contact | Yes | 70 | 85 | 120 | 112 | 91 | 95.6 | 2.857% | 3.529% | 4.167% | 7.143% | 0% | 3.766% | 2 | 3 | 5 | 8 | 0 | 3.6
| Veg. contact | Yes | 32 | 52 | 39 | 27 | 50 | 40 | 21.88% | 7.692% | 7.692% | 11.11% | 0% | 8.5% | 7 | 4 | 3 | 3 | 0 | 3.4
| Vehicle contact | Yes | 203 | 198 | 212 | 215 | 222 | 210 | 2.956% | 2.02% | 1.887% | 0% | 1.351% | 1.619% | 6 | 4 | 4 | 0 | 3 | 3.4
| Other | Yes | 67 | 84 | 60 | 74 | 77 | 72.4 | 4.478% | 1.19% | 3.333% | 1.351% | 0% | 1.934% | 3 | 1 | 2 | 1 | 0 | 1.4
All types of equipment / facility failure | All types | Yes | 1106 | 1258 | 1094 | 1050 | 1067 | 1115 | 0.6329% | 0.9539% | 0.457% | 0.5714% | 0.9372% | 0.7175% | 7 | 12 | 5 | 6 | 10 | 8
| Capacitor bank failure | Yes | 14 | 7 | 5 | 16 | 10 | 10.4 | 0% | 14.29% | 0% | 0% | 0% | 1.923% | 0 | 1 | 0 | 0 | 0 | 0.2
| Conductor failure - all | Yes | 11 | 15 | 8 | 11 | 16 | 12.2 | 27.27% | 20% | 12.5% | 0% | 12.5% | 14.75% | 3 | 3 | 1 | 0 | 2 | 1.8
| Conductor failure - wires down | Yes | 31 | 52 | 30 | 39 | 44 | 39.2 | 9.677% | 5.769% | 3.333% | 0% | 4.545% | 4.592% | 3 | 3 | 1 | 0 | 2 | 1.8
| Fuse failure - all | Yes | 552 | 685 | 620 | 539 | 611 | 601.4 | 0% | 0% | 0.1613% | 0% | 0.1637% | 0.06651% | 0 | 0 | 1 | 0 | 1 | 0.4
All types of equipment / facility failure | Fuse failure - conventional blown fuse | Yes | 528 | 661 | 596 | 515 | 587 | 577.4 | 0% | 0% | 0.1678% | 0% | 0.1704% | 0.06928% | 0 | 0 | 1 | 0 | 1 | 0.4
| Lightning arrestor failure | Yes | 20 | 23 | 27 | 17 | 26 | 22.6 | 0% | 8.696% | 3.704% | 0% | 0% | 2.655% | 0 | 2 | 1 | 0 | 0 | 0.6
| Splice/Clamp/Connector | Yes | 35 | 40 | 24 | 35 | 31 | 33 | 5.714% | 7.5% | 4.167% | 0% | 3.226% | 4.242% | 2 | 3 | 1 | 0 | 1 | 1.4
| Switch failure | Yes | 14 | 21 | 19 | 22 | 15 | 18.2 | 7.143% | 0% | 0% | 4.545% | 6.667% | 3.297% | 1 | 0 | 0 | 1 | 1 | 0.6
| Transformer failure | Yes | 293 | 282 | 257 | 219 | 208 | 251.8 | 0.3413% | 0.3546% | 0% | 0.4566% | 0% | 0.2383% | 1 | 1 | 0 | 1 | 0 | 0.6
Wire-to-wire contact / contamination |  | Yes | 18 | 16 | 26 | 9 | 9 | 15.6 | 0% | 0% | 0% | 11.11% | 22.22% | 3.846% | 0 | 0 | 0 | 1 | 2 | 0.6
Vandalism/Theft |  | Yes | 1 | 1 | 1 | 1 | 1 | 1 | 0% | 100% | 100% | 0% | 0% | 40% | 0 | 1 | 1 | 0 | 0 | 0.4
Other |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | 1 | 0 | 0 | 1 | 0.4
TABLE 11b Transmission: Key Recent Drivers of Ignition Probability, Last 5 Years
Incident type by ignition probability driver |  | Near misses tracked (y/n)? | Number of Incidents per year | [5 empty] | Avg % probability of ignition per incident | [5 empty] | Ignition per year caused by driver
|  |  | 2015 | 2016 | 2017 | 2018 | 2019 | Average | 2015 | 2016 | 2017 | 2018 | 2019 | Average | 2015 | 2016 | 2017 | 2018 | 2019 | Average
Contact from object | All types of object contact | Yes | 35 | 34 | 34 | 32 | 18 | 30.6 | 11.43% | 2.941% | 2.941% | 15.62% | 5.556% | 7.843% | 4 | 1 | 1 | 5 | 1 | 2.4
| Animal contact | Yes | 15 | 5 | 7 | 1 | 6 | 6.8 | 20% | 0% | 0% | 100% | 0% | 11.76% | 3 | 0 | 0 | 1 | 0 | 0.8
| Balloon contact | Yes | 17 | 24 | 24 | 26 | 10 | 20.2 | 5.882% | 0% | 4.167% | 0% | 10% | 2.97% | 1 | 0 | 1 | 0 | 1 | 0.6
| Veg. contact | Yes | 1 | 1 | 0 | 0 | 0 | 0.4 | 0% | 0% | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0
| Vehicle contact | Yes | 1 | 3 | 1 | 4 | 1 | 2 | 0% | 0% | 0% | 75% | 0% | 30% | 0 | 0 | 0 | 3 | 0 | 0.6
| Other | Yes | 1 | 1 | 2 | 1 | 1 | 1.2 | 0% | 100% | 0% | 100% | 0% | 33.33% | 0 | 1 | 0 | 1 | 0 | 0.4
All types of equipment / facility failure | All types | Yes | 60 | 27 | 22 | 21 | 15 | 29 | 1.667% | 0% | 0% | 0% | 0% | 0.6897% | 1 | 0 | 0 | 0 | 0 | 0.2
| Capacitor bank failure | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0
| Conductor failure - all | Yes | 1 | 3 | 3 | 2 | 1 | 2 | 0% | 0% | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0
| Conductor failure - wires down | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0
| Fuse failure - all | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0
All types of equipment / facility failure | Fuse failure - conventional blown fuse | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0
| Lightning arrestor failure | Yes | 1 | 0 | 0 | 2 | 0 | 0.6 | 0% | 0% | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0
| Splice/Clamp/Connector | Yes | 1 | 1 | 0 | 1 | 0 | 0.6 | 100% | 0% | 0% | 0% | 0% | 33.33% | 1 | 0 | 0 | 0 | 0 | 0.2
| Switch failure | Yes | 4 | 1 | 1 | 0 | 1 | 1.4 | 0% | 0% | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0
| Transformer failure | Yes | 0 | 0 | 0 | 0 | 1 | 0.2 | 0% | 0% | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0
Wire-to-wire contact / contamination |  | Yes | 41 | 20 | 15 | 12 | 12 | 20 | 0% | 0% | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0
Vandalism/Theft |  | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0
Other |  | N/A | 12 | 2 | 3 | 4 | 0 | 4.2 | 0% | 50% | 0% | 0% | 0% | 9.524% | 0 | 1 | 0 | 0 | 1 | 0.4

## Table 12
TABLE 12: Recent Use of PSPS, Last 5 Years
PSPS characteristic | 2015 | 2016 | 2017 | 2018 | 2019 | Unit(s) | Calculations
Frequency of PSPS events (total) | 0 | 0 | 5 | 5 | 4 | Number of instances where utility operating protocol requires de-energization of a circuit or portion thereof to reduce ignition probability, per year | Count of unique PSPS outages (switch plans) per year
Frequency of PSPS events (normalized) | 0 | 0 | 0.00011468 | 0.00011468 | 0.000114 | Number of instances where utility operating protocol requires de-energization of a circuit or portion thereof in order to reduce ignition probability, per RFW circuit mile day per year | 1 RFW / # RFW days per year / total OH circuit miles
Scope of PSPS events (total) | 0 | 0 | 230 | 295 | 177 | Circuit-events, measured in number of events multiplied by number of circuits de-energized per year | (Number of PSPS events per year) X (sum of # unique circuits per PSPS event)
Scope of PSPS events (normalized) | 0 | 0 | 0.002 | 0.0048 | 0.0042 | Circuit-events, measured in number of events multiplied by number of circuits targeted for de- energization per RFW circuit mile day per year | 3 RFW / # RFW days per year / total OH circuit miles
Duration of PSPS events (total) | 0 | 0 | 744542.15 | 1061636.9667 | 1325490.4333 | Customer hours per year | Sum of Customer Minutes Interrupted (CMI) / 60
Duration of PSPS events (normalized) | 0 | 0 | 7 | 17 | 30 | Customer hours per RFW circuit mile day per year | 5 RFW / # RFW days per year / total OH circuit miles

## Table 13
TABLE 13: Current Baseline State of Service Territory and Utility Equipment
Land use | Characteristic tracked | In non- HFTD | In HFTD Zone 1 | In HFTD Tier 2 | In HFTD Tier 3 | Comments
Service Territory | Circuit miles | 11203 |  | 4047 | 2067 | Tracking is not completed by rural/highly rural
| Circuit miles in WUI | 6542 |  | 0 | 0
| Number of critical facilities | 8717 |  | 1268 | 515
| Number of critical facilities in WUI | 4409 |  | 0 | 0
| Number of customers | 1287181 |  | 172896 | 31181 | Number of Meters
| Number of customers in WUI | 619466 |  | 0 | 0
| Number of customers belonging to access and functional needs populations | 47263 |  | 7771 | 1939 | Errata: HFTD Tier 2 and HFTD Tier 3 amounts were swapped in SDG&E's 02/07/2020 submittal. To clarify, the data provided for AFN populations encompasses SDG&E's medical baseline customer accounts
| Number of customers belonging to access and functional needs populations in WUI | 27079 |  | 0 | 0
| Circuit miles of overhead transmission lines | 1308 |  | 794 | 308
| Circuit miles of overhead transmission lines in WUI | 470 |  | 0 | 0
| Circuit miles of overhead distribution lines | 3002 |  | 1828 | 1658
| Circuit miles of overhead distribution lines in WUI | 1308 |  | 0 | 0
| Number of substations | 155 |  | 42 | 13
| Number of substations in WUI | 64 |  | 0 | 0
In rural areas | Circuit miles
Circuit miles in WUI
Number of critical facilities
Number of critical facilities in WUI
Number of customers
Number of customers in WUI
Number of customers belonging to access and functional needs populations
Number of customers belonging to access and functional needs populations in WUI
Circuit miles of overhead transmission lines
Circuit miles of overhead transmission lines in WUI
Circuit miles of overhead distribution lines
Circuit miles of overhead distribution lines in WUI
Number of substations
Number of substations in WUI
In highly rural areas | Circuit miles
Circuit miles in WUI
Number of critical facilities
Number of critical facilities in WUI
Number of customers
Number of customers in WUI
Number of customers belonging to access and functional needs populations
Number of customers belonging to access and functional needs populations in WUI
Circuit miles of overhead transmission lines
Circuit miles of overhead transmission lines in WUI
Circuit miles of overhead distribution lines
Circuit miles of overhead distribution lines in WUI
Number of substations
Number of substations in WUI

## Table 14
TABLE 14: Summary Data on Weather Station Count
Weather station count type | Current Count | Unit(s) | Comments
Number of weather stations (total) | 191 | Total number located in service territory and operated by utility
Number of weather stations (normalized) | 0.023 | Total number located in service territory and operated by utility, divided by total number of circuit miles in utility service territory | Used OH circuit miles - T&D 8336 miles
Number of weather stations in non- HFTD (total) | 25 | Total number located in non-HFTD service territory and operated by utility
Number of weather stations in non-HFTD (normalized) | 0.007 | Total number located in non-HFTD service territory and operated by utility, divided by total number of circuit miles in non-HFTD service territory | Used OH circuit miles - T&D 3834 miles
Number of weather stations in HFTD Zone 1 (total) |  | Total number located in HFTD Zone 1 service territory and operated by utility
Number of weather stations in HFTD Zone 1 (normalized) |  | Total number located in HFTD Zone 1 service territory and operated by utility, divided by total number of circuit miles in HFTD Zone 1 service territory
Number of weather stations in HFTD Tier 2 (total) | 64 | Total number located in HFTD Tier 2 service territory and operated by utility
Number of weather stations in HFTD Tier 2 (normalized) | 0.025 | Total number located in HFTD Tier 2 service territory and operated by utility, divided by total number of circuit miles in HFTD Tier 2 service territory | Used OH circuit miles - T&D - 2550 miles
Number of weather stations in HFTD Tier 3 (total) | 102 | Total number located in HFTD Tier 3 service territory and operated by utility
Number of weather stations in HFTD Tier 3 (normalized) | 0.052 | Total number located in HFTD Tier 3 service territory and operated by utility, divided by total number of circuit miles in HFTD Tier 3 service territory | Used OH circuit miles - T&D - 1952 miles

## Table 15
TABLE 15: Summary Data on Fault Indicator Count
Fault indicator count type | Current Count | Unit(s) | Comments
Number of fault indicators (total) | 4735 | Total number located in service territory and operated by utility
Number of fault indicators (normalized) | 0.275 | Total number located in service territory and operated by utility, divided by total number of circuit miles in utility service territory
Number of fault indicators in non-HFTD (total) | 3817 | Total number located in non-HFTD service territory and operated by utility
Number of fault indicators in non-HFTD (normalized) | 0.344 | Total number located in non-HFTD service territory and operated by utility, divided by total number of circuit miles in non-HFTD service territory
Number of fault indicators in HFTD Zone 1 (total) |  | Total number located in HFTD Zone 1 service territory and operated by utility
Number of fault indicators in HFTD Zone 1 (normalized) |  | Total number located in HFTD Zone 1 service territory and operated by utility, divided by total number of circuit miles in HFTD Zone 1 service territory
Number of fault indicators in HFTD Tier 2 (total) | 648 | Total number located in HFTD Tier 2 service territory and operated by utility
Number of fault indicators in HFTD Tier 2 (normalized) | 0.16 | Total number located in HFTD Tier 2 service territory and operated by utility, divided by total number of circuit miles in HFTD Tier 2 service territory
Number of fault indicators in HFTD Tier 3 (total) | 270 | Total number located in HFTD Tier 3 service territory and operated by utility
Number of fault indicators in HFTD Tier 3 (normalized) | 0.13 | Total number located in HFTD Tier 3 service territory and operated by utility, divided by total number of circuit miles in HFTD Tier 3 service territory

## Table 16
TABLE 16: Location of Planned Utility Equipment Additions or Removal By End of 3-Year Plan Term
Land use | Characteristic tracked | Changes by end-2022
|  | In non-HFTD | In HFTD Zone 1 | In HFTD Tier 2 | In HFTD Tier 3
N/A | Circuit miles of overhead transmission lines | 0 |  | 59.1 | 36
| Circuit miles of overhead distribution lines | 16.5 |  | 116.1 | 242.4
| Circuit miles of overhead transmission lines in WUI | 0 |  | 0 | 0
| Circuit miles of overhead distribution lines in WUI | 16.5 |  | 0 | 0
| Number of substations | 0 |  | 0 | 0
| Number of substations in WUI | 0 |  | 0 | 0
| Number of weather stations | 59 |  | 64 | 102
| Number of weather stations in WUI | 59 |  | 0 | 0
In rural areas | Circuit miles of overhead transmission lines
Circuit miles of overhead distribution lines
Circuit miles of overhead transmission lines in WUI
Circuit miles of overhead distribution lines in WUI
Number of substations
Number of substations in WUI
Number of weather stations
Number of weather stations in WUI
In highly rural areas | Circuit miles of overhead transmission lines
Circuit miles of overhead distribution lines
Circuit miles of overhead transmission lines in WUI
Circuit miles of overhead distribution lines in WUI
Number of substations
Number of substations in WUI
Number of weather stations
Number of weather stations in WUI
Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV.

## Table 17
TABLE 17: Location of Planned Utility Infrastructure Upgrades
Land use | Characteristic tracked | In non-HFTD |  |  | In HFTD Zone 1 |  |  | In HFTD Tier 2 |  |  | In HFTD Tier 3
|  | 2020 | 2021 | 2022 | 2020 | 2021 | 2022 | 2020 | 2021 | 2022 | 2020 | 2021 | 2022
Total circuit miles planned for hardening each year, all types and locations |  | 5.5 | 5.5 | 5.5 |  |  |  | 72.5 | 54.9 | 47.8 | 162 | 66 | 50.4
Total number of substations planned for hardening each year, all locations |  | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
In urban areas | Circuit miles planned for grid hardening of overhead transmission lines | 0 | 0 | 0 |  |  |  | 21.5 | 23.4 | 14.2 | 29 | 7 | 0
| Circuit miles of overhead transmission lines in WUI to harden | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| Circuit miles of overhead distribution lines to harden | 5.5 | 5.5 | 5.5 |  |  |  | 51 | 31.5 | 33.6 | 133 | 59 | 50.4
| Circuit miles of overhead distribution lines in WUI to harden | 5.5 | 5.5 | 5.5 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| Circuit miles of overhead transmission lines in WUI to harden | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| Number of substations to harden | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| Number of substations in WUI to harden | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
In rural areas | Circuit miles of overhead transmission lines to harden
Circuit miles of overhead transmission lines in WUI to harden
Circuit miles of overhead distribution lines to harden
Circuit miles of overhead distribution lines in WUI to harden
Circuit miles of overhead transmission lines in WUI to harden
Number of substations to harden
Number of substations in WUI to harden
In highly rural areas | Circuit miles of overhead transmission lines to harden
Circuit miles of overhead transmission lines in WUI to harden
Circuit miles of overhead distribution lines to harden
Circuit miles of overhead distribution lines in WUI to harden
Circuit miles of overhead transmission lines in WUI to harden
Number of substations to harden
Number of substations in WUI to harden
Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV.

## Table 18
TABLE 18a Distribution: Key Drivers of Ignition Probability
Ignition probability drivers |  | Number of incidents per year (according to 5-year historical average) | Average likelihood of ignition per incident | Ignitions from this driver (according to 5-year historical average)
|  |  |  | Total | In non- HFTD | In HFTD Zone 1 | In HFTD Tier 2 | In HFTD Tier 3
Contact from object | All types of object contact | 503.4 | 2.543% | 12.8 | 5.8 |  | 4.2 | 2.8 | Transfer table 11 to this once Katie populates // CB to complete
| Animal contact | 83.8 | 1.193% | 1 | 0.4 |  | 0.4 | 0.2
| Balloon contact | 96.2 | 3.742% | 3.6 | 2.2 |  | 0.6 | 0.8
| Vegetation contact | 40 | 8.5% | 3.4 | 1.4 |  | 1 | 1
| Vehicle contact | 210.8 | 1.613% | 3.4 | 1.2 |  | 1.6 | 0.6
| Other | 72.6 | 1.928% | 1.4 | 0.6 |  | 0.6 | 0.2
All types of equipment / facility failure | All types | 1116.4 | 0.7166% | 8 | 3 |  | 2.4 | 2.6
| Capacitor bank failure | 10.4 | 1.923% | 0.2 | 0 |  | 0.2 | 0
| Conductor failure— all | 40.8 | 4.412% | 1.8 | 0.6 |  | 0.6 | 0.6
| Conductor failure— wires down | 39.6 | 4.545% | 1.8 | 0.6 |  | 0.6 | 0.6
| Fuse failure—all | 18.2 | 2.198% | 0.4 | 0.2 |  | 0 | 0.2
| Fuse failure—conventional blown fuse | 577.4 | 0.06928% | 0.4 | 0.2 |  | 0 | 0.2
| Lightning arrestor failure | 22.8 | 2.632% | 0.6 | 0 |  | 0.2 | 0.4
| Splice/Clamp/Connector Failure | 33.2 | 4.217% | 1.4 | 0.8 |  | 0.2 | 0.4
| Switch failure | 19 | 3.158% | 0.6 | 0 |  | 0.4 | 0.2
| Transformer failure | 251.8 | 0.3177% | 0.8 | 0.2 |  | 0.2 | 0.4
Wire-to-wire contact / contamination |  | 15.6 | 3.846% | 0.6 | 0.4 |  | 0.2 | 0
Other |  | NA | NA | 0.4 | 0.4 |  | 0 | 0
*Note: In SDG&E's Territory Zone 1 falls within Tiers 2 and 3. To avoid double counting all fires have been grouped into Tiers 2 and 3
TABLE 18b Transmission: Key Drivers of Ignition Probability
Ignition probability drivers |  | Number of incidents per year (according to 5-year historical average) | Average likelihood of ignition per incident | Ignitions from this driver (according to 5-year historical average)
|  |  |  | Total | In non- HFTD | In HFTD Zone 1 | In HFTD Tier 2 | In HFTD Tier 3
Contact from object | All types of object contact | 30.6 | 7.843% | 2.4 | 1.2 |  | 1.6 | 0.2
| Animal contact | 6.8 | 11.76% | 0.8 | 0.4 |  | 0.4 | 0
| Balloon contact | 20.2 | 2.97% | 0.6 | 0.2 |  | 0.4 | 0
| Vegetation contact | 0.4 | 0% | 0 | 0 |  | 0 | 0
| Vehicle contact | 2 | 30% | 0.6 | 0.4 |  | 0 | 0.2
| Other | 1.2 | 33.33% | 0.4 | 0 |  | 0.4 | 0
All types of equipment / facility failure | All types | 29 | 0.6897% | 0.2 | 0 |  | 0 | 0
| Capacitor bank failure | 0 | 0% | 0 | 0 |  | 0 | 0
| Conductor failure— all | 2 | 0% | 0 | 0 |  | 0 | 0
| Conductor failure— wires down | 0 | 0% | 0 | 0 |  | 0 | 0
| Fuse failure—all | 0 | 0% | 0 | 0 |  | 0 | 0
| Fuse failure—conventional blown fuse | 0 | 0% | 0 | 0 |  | 0 | 0
| Lightning arrestor failure | 0.6 | 0% | 0 | 0 |  | 0 | 0
| Splice/Clamp/Connector Failure | 0.6 | 33.33% | 0.2 | 0 |  | 0.2 | 0
| Switch failure | 1.4 | 0% | 0 | 0 |  | 0 | 0
| Transformer failure | 0.2 | 0% | 0 | 0 |  | 0 | 0
Wire-to-wire contact / contamination |  | 20 | 0% | 0 | 0 |  | 0 | 0
Other |  | 4.2 | 9.524% | 0.4 | 0.2 |  | 0.2 | 0

## Table 19
TABLE 19: Macro Trends Impacting Ignition Probability and/or Wildfire Consequence
Rank | Macro trends impacting utility ignited ignition probability and estimated wildfire consequence by year 10 | Comments
1 | Change in ignition probability and estimated wildfire consequence due to climate change | Climate change is already affecting California and San Diego County, and is driving higher wildfire risk for many reasons. Extended droughts
3 | Change in ignition probability and estimated wildfire consequence due to relevant invasive species, such as bark beetles | Invasive species such as the bark beetle are not as much of a concern in the San Diego region, but eucalyptus trees and some grasses can be considered invasive and drive vegetation risk for wildfires.
2 | Change in ignition probability and estimated wildfire consequence due to other drivers of change in fuel density and moisture | Fuel density and fuel changes as a result of climate change need more research, however fuel moisture will be an issue as lower relative humidity and drought as a result of climate change will created fuels that are at much higher risk of catastrophic fire
8 | Population changes (including Access and Functional Needs population) that could be impacted by utility ignition | AFN populations are a very high priority for SDG&E and there are many programs in place that build their resilience and wildfire safety. AFN population vulnerability remains a high priority, but is better addressed at this time than these other risks.
7 | Population changes in HFTD that could be impacted by utility ignition | There are two potential impacts of higher population in HFTDs. One impact is that more people will be living in areas with high-wildfire threat, but on the other hand, there is the potential of more urbanization, thus reducing the amount of people living in the WUI.
6 | Population changes in WUI that could be impacted by utility ignition | More people moving to WUI increases ignition probability because there is more infrastructure as well as more people in direct course of wildfire. This trend is changing the most quickly relative to others and thus will be the most important looking just ten years out.
5 | Utility infrastructure location in HFTD vs non-HFTD | The infrastructure in the HFTD vs. non-HFTD is a area of focus for SDG&E and there are major projects hardening infrastructure in HFTD’s.
4 | Utility infrastructure location in urban vs rural vs highly rural areas | There are WUI areas in San Diego that are not included as a part of the HFTDs that can be prone to wildfire and thus SDG&E infrastructure in these areas are targeted for risk mitigation.
*NOTE: Comment on difference in approach to serving customers in urban versus rural versus highly rural areas.

## Table 20
TABLE 20: Anticipated Characteristics of PSPS Use Over the Next 10 Years
Rank order 1-9 | PSPS characteristic | Significantly increase; increase; no change; decrease; significantly decrease | Comments
1 | Number of customers affected by PSPS events (total) | Significantly Decrease
2 | Number of customers affected by PSPS events (normalized by fire weather, e.g., Red Flag Warning line mile days) | Significantly Decrease
7 | Frequency of PSPS events in number of instances where utility operating protocol requires de-energization of a circuit or portion thereof to reduce ignition probability (total) | Decrease
8 | Frequency of PSPS events in number of instances where utility operating protocol requires de-energization of a circuit or portion thereof to reduce ignition probability (normalized by fire weather, e.g., Red Flag Warning line mile days) | Decrease
5 | Scope of PSPS events in circuit-events, measured in number of events multiplied by number of circuits targeted for de-energization (total) | Decrease
6 | Scope of PSPS events in circuit-events, measured in number of events multiplied by number of circuits targeted for de-energization (normalized by fire weather, e.g., Red Flag Warning line mile days) | Decrease
3 | Duration of PSPS events in customer hours (total) | Decrease
4 | Duration of PSPS events in customer hours (normalized by fire weather, e.g., Red Flag Warning line mile days) | Decrease

## Table 21
TABLE 21: Risk Assessment and Mapping Initiatives
Initiative Activity | Year | Total per initiative spend |  | Line Miles to be treated |  | Spend per treated line mile | Ignition probability drivers targeted | Risk reduction | Risk-spend efficiency | Other risk drivers addressed | Existing/new | Existing/ What Proceeding | If New: Memorandum account | In / Exceeding Compliance with regulations | Cite Associated rule | Comments
|  | Low | High | Low | High
Wildfire Risk Reduction Model | 2019 plan | 300 | 500 | NA | NA | 0.023152 | NA | This control was grouped with Public Safety Risk Reduction during high wildfire conditions for purposes of RSE calculations |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2019 actual | 270 |  | NA | NA | 0.0078139 | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020 | 1120 | 1680 | NA | NA | 0.081033 | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2021 | 1440 | 2160 | NA | NA | 0.10418 | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2022 | 1760 | 2640 | NA | NA | 0.12734 | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020-2022 Plan Total | 4320 | 6480 | NA | NA | 0.31255 | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
High Performance Computing Infrastructure | 2019 plan | NA | NA | NA | NA | NA | NA | This control was grouped with Public Safety Risk Reduction during high wildfire conditions for purposes of RSE calculations |  | NA | New | NA | NA | Meets and exceeds | P.U. Code § 451
| 2019 actual | NA |  | NA | NA | NA | NA |  |  | NA | New | NA | NA | Meets and exceeds | P.U. Code § 451
| 2020 | 0 | 0 | NA | NA | 0 | NA |  |  | NA | New | NA | FRMMA | Meets and exceeds | P.U. Code § 451
| 2021 | 0 | 0 | NA | NA | 0 | NA |  |  | NA | New | NA | FRMMA | Meets and exceeds | P.U. Code § 451
| 2022 | 7500 | 9500 | NA | NA | 0.49198 | NA |  |  | NA | New | NA | FRMMA | Meets and exceeds | P.U. Code § 451
| 2020-2022 Plan Total | 7500 | 9500 | NA | NA | 0.49198 | NA |  |  | NA | New | NA | FRMMA | Meets and exceeds | P.U. Code § 451

## Table22
TABLE 22: Situational Awareness and Forecasting Initiatives
Initiative Activity | Year | Total per initiative spend |  | Line Miles to be treated |  | Spend per treated line mile | Ignition probability drivers targeted | Risk reduction | Risk-spend efficiency | Other risk drivers addressed | Existing/new | Existing/ What Proceeding | If New: Memorandum account | In / Exceeding Compliance with regulations | Cite Associated rule | Comments
|  | Low | High | Low | High
Camera Networks and Advanced Weather Station Integration | 2019 plan | * | * | NA | NA | NA | Increased response speed to ignitions | This control was grouped with Strategy for Minimizing Public Safety Risk During High Wildfire Conditions for purposes of RSE calculations |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451 | *2019 WMP plan costs were combined with Fire Science and Climate Adaptation.
| 2019 actual | 559 |  | NA |  | 0.032355 |  |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020 | 700 | 850 | NA | NA | 0.044857 |  |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2021 | 700 | 850 | NA | NA | 0.044857 |  |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2022 | 700 | 850 | NA | NA | 0.044857 |  |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020-2022 Plan Total | 2100 | 2550 | NA | NA | 0.13457 |  |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
Wireless Fault Indicators | 2019 plan | 480 | 720 | NA | NA | 0.034728 | Mitigates customer impacts of sensitive settings | NA | NA | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2019 actual | 797 |  | NA |  | 0.023065 |  | NA | NA | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020 | 570 | 690 | NA | NA | 0.036465 |  | 0% | 0 | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2021 | 570 | 690 | NA | NA | 0.036465 |  | 0% | 0 | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2022 | 0 | 0 | NA | NA | 0 |  | 0% | 0 | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020-2022 Plan Total | 1140 | 1380 | NA | NA | 0.072929 |  | 0% | 0 | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
Fire Science and Climate Adaptation Department (O&M) | 2019 plan | 1600 | 2400 | NA | NA | 0.11576 | NA | This control was grouped with Strategy for Minimizing Public Safety Risk During High Wildfire Conditions for purposes of RSE calculations |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2019 actual | 862 |  | NA |  | 0.024946 | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020 | 2000 | 3000 | NA | NA | 0.1447 | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2021 | 2000 | 3000 | NA | NA | 0.1447 | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2022 | 2000 | 3000 | NA | NA | 0.1447 | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020-2022 Plan Total | 6000 | 9000 | NA | NA | 0.4341 | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
Fire Science and Climate Adaptation Department (Capital) | 2019 plan | NA | NA | NA | NA | NA | NA | This control was grouped with Strategy for Minimizing Public Safety Risk During High Wildfire Conditions for purposes of RSE calculations |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2019 actual | NA |  | NA |  | NA | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020 | 3600 | 5400 | NA | NA | 0.26046 | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2021 | 0 | 0 | NA | NA | 0 | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2022 | 0 | 0 | NA | NA | 0 | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020-2022 Plan Total | 3600 | 5400 | NA | NA | 0.26046 | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
Situational Awareness Dashboard (Capital) | 2019 plan | NA | NA | NA | NA | NA | NA | This control was grouped with Strategy for Minimizing Public Safety Risk During High Wildfire Conditions for purposes of RSE calculations |  | NA | NA | NA | NA | Meets and exceeds | P.U. Code § 451
| 2019 actual | NA |  | NA |  | NA | NA |  |  | NA | NA | NA | NA | Meets and exceeds | P.U. Code § 451
| 2020 | 1900 | 2300 | NA | NA | 0.12155 | NA |  |  | NA | New | NA | FRMMA | Meets and exceeds | P.U. Code § 451
| 2021 | 1900 | 2300 | NA | NA | 0.12155 | NA |  |  | NA | New | NA | FRMMA | Meets and exceeds | P.U. Code § 451
| 2022 | 1900 | 2300 | NA | NA | 0.12155 | NA |  |  | NA | New | NA | FRMMA | Meets and exceeds | P.U. Code § 451
| 2020-2022 Plan Total | 5700 | 6900 | NA | NA | 0.36465 | NA |  |  | NA | New | NA | FRMMA | Meets and exceeds | P.U. Code § 451
Situational Awareness Dashboard (O&M) | 2019 plan | NA | NA | NA | NA | NA | NA | This control was grouped with Strategy for Minimizing Public Safety Risk During High Wildfire Conditions for purposes of RSE calculations |  | NA | NA | NA | NA | Meets and exceeds | P.U. Code § 451
| 2019 actual | NA |  | NA |  | NA | NA |  |  | NA | NA | NA | NA | Meets and exceeds | P.U. Code § 451
| 2020 | 285 | 345 | NA | NA | 0.018232 | NA |  |  | NA | New | NA | FRMMA | Meets and exceeds | P.U. Code § 451
| 2021 | 285 | 345 | NA | NA | 0.018232 | NA |  |  | NA | New | NA | FRMMA | Meets and exceeds | P.U. Code § 451
| 2022 | 285 | 345 | NA | NA | 0.018232 | NA |  |  | NA | New | NA | FRMMA | Meets and exceeds | P.U. Code § 451
| 2020-2022 Plan Total | 855 | 1035 | NA | NA | 0.054697 | NA |  |  | NA | New | NA | FRMMA | Meets and exceeds | P.U. Code § 451
Operating Conditions | 2019 plan | Base | Base | NA | NA | NA | Crew and all ignition probability from faults | NA | NA | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2019 actual | Base | Base | NA | NA | NA |  | NA | NA | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020 | Base | Base | NA | NA | NA |  | NA | NA | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2021 | Base | Base | NA | NA | NA |  | NA | NA | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2022 | Base | Base | NA | NA | NA |  | NA | NA | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020-2022 Plan Total | Base | Base | NA | NA | NA |  | NA | NA | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
NMS Situational Awareness Upgrades | 2019 plan | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Meets and exceeds | P.U. Code § 451
| 2019 actual | NA |  | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Meets and exceeds | P.U. Code § 451
| 2020 | 475 | 575 | NA | NA | 0.030387 | NA | 0% | 0 | NA | New | NA | FRMMA | Meets and exceeds | P.U. Code § 451
| 2021 | 475 | 575 | NA | NA | 0.030387 | NA | 0% | 0 | NA | New | NA | FRMMA | Meets and exceeds | P.U. Code § 451
| 2022 | 475 | 575 | NA | NA | 0.030387 | NA | 0% | 0 | NA | New | NA | FRMMA | Meets and exceeds | P.U. Code § 451
| 2020-2022 Plan Total | 1425 | 1725 | NA | NA | 0.091162 | NA | 0% | 0 | NA | New | NA | FRMMA | Meets and exceeds | P.U. Code § 451

## Table22a
TABLE 22A: Situational Awareness and Forecasting Initiatives
Initiative Activity | Year | Weather Stations Installed
|  | Low | High
Camera Networks and Advanced Weather Station Integration | 2019 Plan | 11 | 15
| 2019 Actual | 13
| 2020 | 18 | 22
| 2021 | 18 | 22
| 2022 | 18 | 22
| 2020-20222 Plan Totals | 54 | 66
Initiative Activity | Year | Wireless Fault Indicators Installed
|  | Low | High
Wireless Fault Indicators | 2019 plan | 450 | 550
| 2019 actual | 594
| 2020 | 450 | 550
| 2021 | 450 | 550
| 2022 | 0 | 0
| 2020-2022 Plan Total | 900 | 1100

## Table23
TABLE 23: Grid Design and System Hardening Initiatives
Initiative Activity | Year | Total per initiative spend |  | Line Miles to be treated |  | Spend per treated line mile | Ignition probability drivers targeted | Risk reduction | Risk-spend efficiency | Other risk drivers addressed | Existing/new | Existing/ What Proceeding | If New: Memorandum account | In / Exceeding Compliance with regulations | Cite Associated rule | Comments
|  | Low | High | Low | High
SCADA Capacitor Program | 2019 plan | NA | NA | NA | NA | NA | Equipment failure, capacitor | NA | NA | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2019 actual | NA |  | NA |  | NA |  | NA | NA | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020 | 1425 | 1725 | NA | NA | 0.091162 |  | 0.2567% | 140.3838 | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2021 | 1425 | 1725 | NA | NA | 0.091162 |  | 0.01953% | 10.369 | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2022 | 1805 | 2185 | NA | NA | 0.11547 |  | 0.02474% | 10.067 | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020-2022 Plan Total | 4655 | 5635 | NA | NA | 0.29779 |  | 0.301% | 48.8146 | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
Advanced Protection | 2019 plan | 2400 | 3600 | NA | NA | 0.17364 | Reduces % chance fault becomes an ignition | NA | NA | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2019 actual | 3400 |  | NA | NA | 0.19679 |  | NA | NA | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020 | 4800 | 5800 | NA | NA | 0.30677 |  | 1.675% | 24.7608 | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2021 | 8200 | 10000 | NA | NA | 0.52671 |  | 1.848% | 24.7608 | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2022 | 8200 | 10000 | NA | NA | 0.52671 |  | 2.304% | 24.7608 | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020-2022 Plan Total | 21200 | 25800 | NA | NA | 1.3602 |  | 5.828% | 24.7608 | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
Distribution Overhead Fire Hardening (OH) | 2019 plan | 65700 | 85100 | 112.8 | 146.7 | 581.1175 | Equipment Failure All | NA | NA | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2019 actual | 120611 |  | 122.9 |  | 981.3751 |  | NA | NA | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020 | 69600 | 104400 | 81.6 | 122.4 | 852.9412 |  | 1.228% | 22.5103 | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2021 | 9600 | 14400 | 11.2 | 16.8 | 857.1429 |  | 0.2067% | 22.5103 | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2022 | 5760 | 8640 | 6.72 | 10.08 | 857.1429 |  | 0.1413% | 22.5103 | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020-2022 Plan Total | 84960 | 127440 | 99.52 | 149.28 | 853.6977 |  | 1.58% | 22.5103 | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
Distribution Overhead Fire Hardening (Covered Conductor) | 2019 plan | 0 | 0 | 0 | 0 | 0 | Equipment Failure All, Foreign Object in Line, all but large vegetation, vehicle contacts | NA | NA | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2019 actual | 0 |  | 0 |  | NA |  | NA | NA | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020 | 856.8 | 1285.2 | 0.8 | 1.2 | 1071 |  | 0.05079% | 20.7444 | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2021 | 8640 | 12960 | 8 | 12 | 1080 |  | 0.1972% | 20.7444 | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2022 | 8640 | 12960 | 8 | 12 | 1080 |  | 0.1765% | 20.7444 | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020-2022 Plan Total | 18136.8 | 27205.2 | 16.8 | 25.2 | 1079.5714 |  | 0.4245% | 20.7444 | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
Pole Replacement and Reinforcement | 2019 plan | 10600 | 16000 | NA | NA | 0.76981 | Equipment failure, all except for wires | NA | NA | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2019 actual | 11705 |  | NA |  | 0.33875 |  | NA | NA | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020 | 9561 | 11575 | NA | NA | 0.61168 |  | 1.179% | 24.6869 | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2021 | 9561 | 11575 | NA | NA | 0.61168 |  | 1.062% | 24.6869 | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2022 | 9561 | 11575 | NA | NA | 0.61168 |  | 0.8794% | 24.6869 | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020-2022 Plan Total | 28683 | 34725 | NA | NA | 1.835 |  | 3.121% | 24.6869 | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
Expulsion Fuse Replacement Program | 2019 plan | 7800 | 11600 | NA | NA | 0.56144 | Fuse Operation | NA | NA | NA | New | NA | FRMMA | Meets and exceeds | P.U. Code § 451
| 2019 actual | 3716 |  | NA |  | 0.10754 |  | NA | NA | NA | New | NA | FRMMA | Meets and exceeds | P.U. Code § 451
| 2020 | 2989.6 | 4484.4 | NA | NA | 0.2163 |  | 0.2414% | 107.7455 | NA | New | NA | FRMMA | Meets and exceeds | P.U. Code § 451
| 2021 | 3986.4 | 5979.6 | NA | NA | 0.28842 |  | 0.07542% | 24.5071 | NA | New | NA | FRMMA | Meets and exceeds | P.U. Code § 451
| 2022 | 1522.4 | 2283.6 | NA | NA | 0.11015 |  | 0.02894% | 23.9086 | NA | New | NA | FRMMA | Meets and exceeds | P.U. Code § 451
| 2020-2022 Plan Total | 8498.4 | 12747.6 | NA | NA | 0.61486 |  | 0.3458% | 52.9875 | NA | New | NA | FRMMA | Meets and exceeds | P.U. Code § 451
PSPS Enhancements - Sectionalizing Devices | 2019 plan | 400 | 700 | NA | NA | 0.031834 | PSPS impacts | NA | NA | Reliability | New | NA | FRMMA | Meets and exceeds | P.U. Code § 451
| 2019 actual | 1303 |  | NA | NA | 0.037709 |  | NA | NA | Reliability | New | NA | FRMMA | Meets and exceeds | P.U. Code § 451
| 2020 | 400 | 700 | NA | NA | 0.031834 |  | 0 | 0 | Reliability | New | NA | FRMMA | Meets and exceeds | P.U. Code § 451
| 2021 | 400 | 700 | NA | NA | 0.031834 |  | 0 | 0 | Reliability | New | NA | FRMMA | Meets and exceeds | P.U. Code § 451
| 2022 | 400 | 700 | NA | NA | 0.031834 |  | 0 | 0 | Reliability | New | NA | FRMMA | Meets and exceeds | P.U. Code § 451
| 2020-2022 Plan Total | 1200 | 2100 | NA | NA | 0.095503 |  | 0 | 0 | Reliability | New | NA | FRMMA | Meets and exceeds | P.U. Code § 451
Hotline Clamp Replacement Program | 2019 plan | 1200 | 1800 | NA | NA | 0.086821 | Equipment failure, Wire Down | NA | NA | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2019 actual | 921.9214 |  | NA |  | 0.026681 |  | NA | NA | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020 | 2400 | 3600 | NA | NA | 0.17364 |  | 0.1185% | 65.8789 | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2021 | 2400 | 3600 | NA | NA | 0.17364 |  | 0.1185% | 63.9601 | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2022 | 2400 | 3600 | NA | NA | 0.17364 |  | 0.0157% | 8.2253 | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020-2022 Plan Total | 7200 | 10800 | NA | NA | 0.52092 |  | 0.2527% | 46.0214 | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
Microgrids | 2019 plan | 2400 | 3600 | NA | NA | 0.17364 | PSPS impacts | NA | NA | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2019 actual | 188 |  | NA | NA | 0.0054408 |  | NA | NA | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020 | 10260 | 12420 | NA | NA | 0.65636 |  | 0 | 0 | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2021 | 7600 | 9200 | NA | NA | 0.4862 |  | 0 | 0 | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2022 | 7600 | 9200 | NA | NA | 0.4862 |  | 0 | 0 | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020-2022 Plan Total | 25460 | 30820 | NA | NA | 1.6288 |  | 0 | 0 | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
Customer Resilliancy Programs | 2019 plan | 500 | 900 | NA | NA | 0.040516 | PSPS impacts | This control was grouped with Strategy for Minimizing Public Safety Risk During High Wildfire Conditions for purposes of RSE calculations |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2019 actual | 1458 |  | NA | NA | 0.042195 |  |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020 | 4950 | 5470 | NA | NA | 0.30156 |  |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2021 | 5472 | 6472 | NA | NA | 0.34566 |  |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2022 | 7530 | 8730 | NA | NA | 0.47057 |  |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020-2022 Plan Total | 17952 | 20672 | NA | NA | 1.1178 |  |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
Generator Grant Program - Expanded | 2019 plan | NA | NA | NA | NA | NA | PSPS impacts | NA | NA | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2019 actual | NA |  | NA | NA | NA |  | NA | NA | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020 | 200 | 300 | NA | NA | 0.01447 |  | 0 | 0 | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2021 | 200 | 300 | NA | NA | 0.01447 |  | 0 | 0 | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2022 | 200 | 300 | NA | NA | 0.01447 |  | 0 | 0 | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020-2022 Plan Total | 600 | 900 | NA | NA | 0.04341 |  | 0 | 0 | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
Whole Home Generators | 2019 plan | NA | NA | NA | NA | NA | PSPS impacts | NA | NA | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451 | Errata: whole home generator cost forecast was incorrect in SDG&E's 02/07/2020 submittal
| 2019 actual | NA |  | NA | NA | NA |  | NA | NA | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020 | 2400 | 3600 | NA | NA | 0.17364 |  | 0 | 0 | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2021 | 2400 | 3600 | NA | NA | 0.17364 |  | 0 | 0 | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2022 | 2400 | 3600 | NA | NA | 0.17364 |  | 0 | 0 | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020-2022 Plan Total | 7200 | 10800 | NA | NA | 0.52092 |  | 0 | 0 | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
Undergrounding of Electric Lines and/or Equipment | 2019 plan | 1200 | 1800 | 1.2 | 1.8 | 1000 | All equipment failure and foreign object in lines | NA | NA | Reliability | Existing | NA | FRMMA | Meets and exceeds | P.U. Code § 451
| 2019 actual | 4727 |  | 2.6 |  | 1818.0769 |  | NA | NA | Reliability | Existing | NA | FRMMA | Meets and exceeds | P.U. Code § 451
| 2020 | 24800 | 37200 | 8 | 12 | 3100 |  | 0.4563% | 21.5642 | Reliability | New | NA | FRMMA | Meets and exceeds | P.U. Code § 451
| 2021 | 125600 | 188400 | 40 | 60 | 3140 |  | 2.154% | 21.5642 | Reliability | New | NA | FRMMA | Meets and exceeds | P.U. Code § 451
| 2022 | 150400 | 225600 | 48 | 72 | 3133.3333 |  | 2.572% | 21.5642 | Reliability | New | NA | FRMMA | Meets and exceeds | P.U. Code § 451
| 2020-2022 Plan Total | 300800 | 451200 | 96 | 144 | 3133.3333 |  | 5.18% | 21.5642 | Reliability | New | NA | FRMMA | Meets and exceeds | P.U. Code § 451
Overhead Transmission and Distribution Fire Hardening (Transmission OH) | 2019 plan | FERC | FERC | 6 | 8 | NA | Equipment Failure All | NA | NA | Reliability | Existing | FERC TO5Filing | NA | Meets and exceeds | G.O. 95
| 2019 actual | FERC |  | 7 |  | NA |  | NA | NA | Reliability | Existing | FERC TO5Filing | NA | Meets and exceeds | G.O. 95
| 2020 | FERC | FERC | 17.1 | 21.4 | NA |  | NA FERC | NA FERC | Reliability | Existing | FERC TO5Filing | NA | Meets and exceeds | G.O. 95
| 2021 | FERC | FERC | 21.2 | 27.6 | NA |  | NA FERC | NA FERC | Reliability | Existing | FERC TO5Filing | NA | Meets and exceeds | G.O. 95
| 2022 | FERC | FERC | 16.4 | 20.5 | NA |  | NA FERC | NA FERC | Reliability | Existing | FERC TO5Filing | NA | Meets and exceeds | G.O. 95
| 2020-2022 Plan Total | FERC | FERC | 54.7 | 69.5 | NA |  | NA FERC | NA FERC | Reliability | Existing | FERC TO5Filing | NA | Meets and exceeds | G.O. 95
Overhead Transmission and Distribution Fire Hardening (Transmission UG) | 2019 plan | FERC | FERC | 2 | 4 | NA | All equipment failure and foreign object in lines | NA | NA | Reliability | Existing | FERC TO5Filing | NA | Meets and exceeds | G.O. 95
| 2019 actual | FERC |  | 3 |  | NA |  | NA | NA | Reliability | Existing | FERC TO5Filing | NA | Meets and exceeds | G.O. 95
| 2020 | FERC | FERC | 0 | 0 | NA |  | NA FERC | NA FERC | Reliability | Existing | FERC TO5Filing | NA | Meets and exceeds | G.O. 95
| 2021 | FERC | FERC | 4.8 | 7.2 | NA |  | NA FERC | NA FERC | Reliability | Existing | FERC TO5Filing | NA | Meets and exceeds | G.O. 95
| 2022 | FERC | FERC |  |  | NA |  | NA FERC | NA FERC | Reliability | Existing | FERC TO5Filing | NA | Meets and exceeds | G.O. 95
| 2020-2022 Plan Total | FERC | FERC | 4.8 | 7.2 | NA |  | NA FERC | NA FERC | Reliability | Existing | FERC TO5Filing | NA | Meets and exceeds | G.O. 95
Overhead Transmission and Distribution Fire Hardening (Distribution Underbuilt) | 2019 plan | 4400 | 6600 | 8 | 12 | NA | Equipment Failure All | NA | NA | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | G.O. 95
| 2019 actual | 2964 |  | 10 |  | NA |  | NA | NA | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | G.O. 95
| 2020 | 5219 | 6523 | 10.9 | 13.6 | 479.2653 |  | NA FERC | NA FERC | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | G.O. 95
| 2021 | 12236 | 15294 | 19.4 | 24.2 | 631.422 |  | NA FERC | NA FERC | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | G.O. 95
| 2022 | 5396 | 6744 | 7 | 8.8 | 768.3544 |  | NA FERC | NA FERC | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | G.O. 95
| 2020-2022 Plan Total | 22851 | 28561 | 37.3 | 46.6 | 612.7771 |  | NA FERC | NA FERC | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | G.O. 95
CNF Fire Hardening (Transmission OH) | 2019 plan | FERC | FERC | 25 | 31 | NA | Equipment Failure All | NA | NA | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2019 actual | FERC |  | 25 |  | NA |  | NA | NA | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020 | FERC | FERC | 23.2 | 34.8 | NA |  | NA FERC | NA FERC | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2021 | FERC | FERC | 0 | 0 | NA |  | NA FERC | NA FERC | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2022 | FERC | FERC | 0 | 0 | NA |  | NA FERC | NA FERC | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020-2022 Plan Total | FERC | FERC | 23.2 | 34.8 | NA |  | NA FERC | NA FERC | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
CNF Fire Hardening (Distribution OH Associated with Transmission) | 2019 plan | 47700 | 58300 | 20 | 24 | 2409.0909 | Equipment Failure All | NA | NA | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2019 actual | 12793 |  | 26.4 |  | 484.5833 |  | NA | NA | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020 | 14000 | 21000 | 20 | 30 | 660 |  | NA FERC | NA FERC | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2021 | 0 | 0 | 0 | 0 | 0 |  | NA FERC | NA FERC | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2022 | 0 | 0 | 0 | 0 | 0 |  | NA FERC | NA FERC | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020-2022 Plan Total | 14000 | 21000 | 20 | 30 | 700 |  | NA FERC | NA FERC | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
CNF Fire Hardening (Distribution OH) | 2019 plan | 47700 | 58300 | 20 | 24 | 2409.0909 | Equipment Failure All | NA | NA | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2019 actual | 28190 |  | 26.4 |  | 1067.803 |  | NA | NA | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020 | 14000 | 21000 | 20 | 30 | 660.7143 |  | 1.075% | 24.2372 | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2021 | 8570 | 10570 | 0 | 2 | 9570 |  | 0.02707% | 24.2372 | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2022 | 0 | 0 | 0 | 0 | 0 |  | 0% | 0 | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020-2022 Plan Total | 22570 | 31570 | 20 | 32 | 1041.1538 |  | 1.102% | 24.2372 | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
CNF Fire Hardening (Distribution UG) | 2019 plan | NA |  | 15 | 19 | NA | All equipment failure and foreign object in lines | NA | NA | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2019 actual | 27664 |  | 8.7 |  | NA |  | NA | NA | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020 | 24000 | 36000 | 11.2 | 16.8 | 2142.8571 |  | See CNF OH | See CNF OH | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2021 | 0 | 1860 | 0 | 1 | 1860 |  | See CNF OH | See CNF OH | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2022 | 0 | 0 | 0 | 0 | NA |  | See CNF OH | See CNF OH | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020-2022 Plan Total | 24000 | 37860 | 11.2 | 17.8 | 2133.1034 |  | See CNF OH | See CNF OH | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
Lightning Arrestor Replacement Program | 2019 plan | NA | NA | NA | NA | NA | NA | NA | NA | NA | Existing | TY 2019 GRC | FRMMA | Meets and exceeds | P.U. Code § 451
| 2019 actual | NA |  | NA | NA | NA | NA | NA | NA | NA | Existing | TY 2019 GRC | FRMMA | Meets and exceeds | P.U. Code § 451
| 2020 | 0 | 0 | NA | NA | 0 | NA | 0 | 0 | NA | Existing | TY 2019 GRC | FRMMA | Meets and exceeds | P.U. Code § 451
| 2021 | 950 | 1150 | NA | NA | 0.060774 | NA | 0.6076% | 259.6849 | NA | Existing | TY 2019 GRC | FRMMA | Meets and exceeds | P.U. Code § 451
| 2022 | 1900 | 2300 | NA | NA | 0.12155 | NA | 0.6076% | 259.6849 | NA | Existing | TY 2019 GRC | FRMMA | Meets and exceeds | P.U. Code § 451
| 2020-2022 Plan Total | 2850 | 3450 | NA | NA | 0.18232 | NA | 0.6076% | 259.6849 | NA | Existing | TY 2019 GRC | FRMMA | Meets and exceeds | P.U. Code § 451
LTE Communication Network | 2019 plan | 8800 | 13200 | NA | NA | 0.63668 | NA | This was grouped with Advanced Protection for the purposes of RSE calculation |  | NA | Existing | TY 2019 GRC | FRMMA | Meets and exceeds | P.U. Code § 451
| 2019 actual | 7086 |  | NA | NA | 0.20507 | NA |  |  | NA | Existing | TY 2019 GRC | FRMMA | Meets and exceeds | P.U. Code § 451
| 2020 | 25200 | 37800 | NA | NA | 1.8232 | NA |  |  | NA | Existing | TY 2019 GRC | FRMMA | Meets and exceeds | P.U. Code § 451
| 2021 | 25200 | 37800 | NA | NA | 1.8232 | NA |  |  | NA | Existing | TY 2019 GRC | FRMMA | Meets and exceeds | P.U. Code § 451
| 2022 | 33200 | 49800 | NA | NA | 2.402 | NA |  |  | NA | Existing | TY 2019 GRC | FRMMA | Meets and exceeds | P.U. Code § 451
| 2020-2022 Plan Total | 83600 | 125400 | NA | NA | 6.0485 | NA |  |  | NA | Existing | TY 2019 GRC | FRMMA | Meets and exceeds | P.U. Code § 451

## Table23a
TABLE 23A: Grid Design and System Hardening Initiatives
Initiative Activity | Year | SCADA Caps installed
|  | Low | High
SCADA Capacitor Program | 2019 Plan | NA | NA
| 2019 Actual | NA
| 2020 | 27 | 33
| 2021 | 27 | 33
| 2022 | 34 | 42
| 2020-20222 Plan Totals | 88 | 108
Initiative Activity | Year | Circuits Enabled |  | Substations Enabled
|  | Low | High | Low | High
Advanced Protection | 2019 Plan | 6 | 10 | New Metric for post-2019 work
| 2019 Actual | 8
| 2020 | 6 | 10 | 4 | 8
| 2021 | 7 | 11 | 6 | 10
| 2022 | 12 | 18 | 4 | 8
| 2020-20222 Plan Totals | 25 | 39 | 14 | 26
OH Hardening 2019 Program Summary |  | Total per initiative spend |  | Line Miles to be treated
|  | Low | High | Low | High
2019 Plan | FiRM | 49500 | 60500 | 81 | 99
| PRiME | 14400 | 21600 | 27.7879 | 41.6818
| WiSE | 1800 | 3000 | 4 | 6
| Total | 65700 | 85100 | 112.7879 | 146.6818
2019 Actual | FiRM | 89300 |  | 83
| PRiME | 30880 |  | 34.2235
| WiSE | 4698 |  | 5.7
| Total | 124878 |  | 122.9235
Initiative Activity | Year | Poles Replaced
|  | Low | High
Pole Replacement and Reinforcement | 2019 Plan | 659 | 1023
| 2019 Actual | 725
| 2020 | 600 | 740
| 2021 | 600 | 740
| 2022 | 600 | 740
| 2020-20222 Plan Totals | 1800 | 2220
Initiative Activity | Year | Total Fuses Replaced
|  | Low | High
Expulsion Fuse Replacement Program | 2019 Plan | 1800 | 2700
| 2019 Actual | 2490
| 2020 | 2400 | 3600
| 2021 | 3200 | 4800
| 2022 | 1228 | 1842
| 2020-20222 Plan Totals | 6828 | 10242
Initiative Activity | Year | Sectionalizing Devices Installed
|  | Low | High
PSPS Enhancements - Sectionalizing Devices | 2019 Plan | 6 | 8
| 2019 Actual | 7
| 2020 | 8 | 12
| 2021 | 8 | 12
| 2022 | 8 | 12
| 2020-20222 Plan Totals | 24 | 36
Initiative Activity | Year | Total Hot Line Clamps Replaced
|  | Low | High
Hot Line Clamp Replacement Program | 2019 Plan | 400 | 600
| 2019 Actual | 660
| 2020 | 1320 | 1980
| 2021 | 1320 | 1980
| 2022 | 1320 | 1980
| 2020-20222 Plan Totals | 3960 | 5940
Initiative Activity | Year | Micro Grids Installed |  | Comments
|  | Low | High
Micro Grids | 2019 Plan | 0 | 1 | *Substantial progress was made on the Cameron Quarters Micro Grid Project, it will be completed in 2020.
| 2019 Actual | *0
| 2020 | 2 | 4
| 2021 | 2 | 4
| 2022 | 0 | 2
| 2020-20222 Plan Totals | 4 | 10
Initiative Activity | Year | Generators Provided |  | Community Resource Centers |  | Community and Critical Infrastructure Generator Lease
|  | Low | High | Low | High | Low | High
Customer Resilliancy Programs | 2019 Plan | 50 | 80 | 8 | 11 | NA | NA
| 2019 Actual | 65 |  | 8 |  | NA
| 2020 | 1000 | 1500 | 8 | 10 | 3 | 5
| 2021 | 1200 | 1800 | 10 | 12 | 3 | 5
| 2022 | 1600 | 2160 | 10 | 14 | 3 | 5
| 2020-20222 Plan Totals | 3800 | 5460 | 28 | 36 | 9 | 15
Initiative Activity | Year | Generators Provided
|  | Low | High
Generator Grant Program Expanded | 2019 Plan | NA | NA
| 2019 Actual | NA
| 2020 | 104 | 156
| 2021 | 104 | 156
| 2022 | 104 | 156
| 2020-20222 Plan Totals | 312 | 468
Initiative Activity | Year | Generators Provided
|  | Low | High
Whole House Generators | 2019 Plan | NA | NA
| 2019 Actual | NA
| 2020 | 240 | 360
| 2021 | 240 | 360
| 2022 | 240 | 360
| 2020-20222 Plan Totals | 720 | 1080
Initiative Activity | Year | Lightning Arrestors Replaced
|  | Low | High
Lightning Arrestor Replacement Program | 2019 Plan | NA | NA
| 2019 Actual | NA
| 2020 | 0 | 0
| 2021 | 836 | 1012
| 2022 | 1672 | 2024
| 2020-20222 Plan Totals | 2508 | 3036
Initiative Activity | Year | Base Stations Installed
|  | Low | High
LTE Communication Network | 2019 Plan | NA
2019 Actual
| 2020 | 20 | 30
| 2021 | 52 | 78
| 2022 | 68 | 102
| 2020-20222 Plan Totals | 140 | 210

## Table24
TABLE 24: Asset Management and Inspections Initiatives
Initiative Activity | Year | Total per initiative spend |  | Line Miles to be treated |  | Spend per treated line mile | Ignition probability drivers targeted | Risk reduction | Risk-spend efficiency | Other risk drivers addressed | Existing/new | Existing/ What Proceeding | If New: Memorandum account | In / Exceeding Compliance with regulations | Cite Associated rule | Comments
|  | Low | High | Low | High
SDG&E Corrective Maintenance Program (HFTD) | 2019 plan | Base | Base | NA | NA | NA | All equipment failure related (less hot connections) | NA | NA | Reliability | Existing | TY 2019 GRC | NA | Meets | GO165 | *SDG&E's corrective maintenance program inspection costs were not broken out in the previous WMP. SDG&E plans to track inspection costs within the HFTD going forward.
| 2019 actual | *Base |  | NA |  | NA |  | NA | NA | Reliability | Existing | TY 2019 GRC | NA | Meets | GO165
| 2020 | 1241.6 | 1862.4 | NA | NA | 0.08983 |  | NA | NA | Reliability | Existing | TY 2019 GRC | NA | Meets | GO165
| 2021 | 1009.6 | 1514.4 | NA | NA | 0.073045 |  | NA | NA | Reliability | Existing | TY 2019 GRC | NA | Meets | GO165
| 2022 | 505.6 | 758.4 | NA | NA | 0.03658 |  | NA | NA | Reliability | Existing | TY 2019 GRC | NA | Meets | GO165
| 2020-2022 Plan Total | 2756.8 | 4135.2 | NA | NA | 0.19946 |  | NA | NA | Reliability | Existing | TY 2019 GRC | NA | Meets | GO165
Transmission System Inspections | 2019 plan | FERC | FERC | NA | NA | NA | All equipment failure | NA | NA | Reliability | Existing | FERC TO5Filing | NA | Meets and exceeds | California Public Resources Code (PRC) §§ 4292 and 4293, as well as GO 95 and GO 128 rules.
| 2019 actual | FERC |  | NA | NA | NA |  | NA | NA | Reliability | Existing | FERC TO5Filing | NA | Meets and exceeds
| 2020 | FERC | FERC | NA | NA | NA |  | NA | NA | Reliability | Existing | FERC TO5Filing | NA | Meets and exceeds
| 2021 | FERC | FERC | NA | NA | NA |  | NA | NA | Reliability | Existing | FERC TO5Filing | NA | Meets and exceeds
| 2022 | FERC | FERC | NA | NA | NA |  | NA | NA | Reliability | Existing | FERC TO5Filing | NA | Meets and exceeds
| 2020-2022 Plan Total | FERC | FERC | NA | NA | NA |  | NA | NA | Reliability | Existing | FERC TO5Filing | NA | Meets and exceeds
Infrared Corona | 2019 plan | NA | NA | NA | NA | NA | Hot Connection Equipment Failure | * |  | Reliability | NA | NA | FRMMA | Exceeds | GO165 | *RSE values for SDG&E's enhanced inspection programs were grouped in the November RAMP filing
| 2019 actual | 98 |  | NA |  | NA |  |  |  | Reliability | NA | NA | FRMMA | Exceeds | GO165
| 2020 | 221 | 268 | NA | NA | 0.014152 |  |  |  | Reliability | New | NA | FRMMA | Exceeds | GO165
| 2021 | 221 | 268 | NA | NA | 0.014152 |  |  |  | Reliability | New | NA | FRMMA | Exceeds | GO165
| 2022 | 221 | 268 | NA | NA | 0.014152 |  |  |  | Reliability | New | NA | FRMMA | Exceeds | GO165
| 2020-2022 Plan Total | 663 | 804 | NA | NA | 0.042455 |  |  |  | Reliability | New | NA | FRMMA | Exceeds | GO165
HFTD Tier 3 Inspections | 2019 plan | *Base | Base | NA | NA | NA | All equipment failure related (less hot connections) | * |  | Reliability | Existing | TY 2019 GRC | NA | Exceeds | GO165 | *RSE values for SDG&E's enhanced inspection programs were grouped in the November RAMP filing
| 2019 actual | Base |  | NA | NA | NA |  |  |  | Reliability | Existing | TY 2019 GRC | NA | Exceeds | GO165
| 2020 | 333 | 403 | NA | NA | 0.0213 |  |  |  | Reliability | Existing | TY 2019 GRC | NA | Exceeds | GO165
| 2021 | 333 | 403 | NA | NA | 0.0213 |  |  |  | Reliability | Existing | TY 2019 GRC | NA | Exceeds | GO165
| 2022 | 333 | 403 | NA | NA | 0.0213 |  |  |  | Reliability | Existing | TY 2019 GRC | NA | Exceeds | GO165
| 2020-2022 Plan Total | 999 | 1209 | NA | NA | 0.0639 |  |  |  | Reliability | Existing | TY 2019 GRC | NA | Exceeds | GO165
Drone Inspections (capital) | 2019 plan | NA | NA | NA | NA | NA | All equipment failure related (less hot connections) | * |  | Reliability | NA | NA | NA | Meets and exceeds | GO 165, GO 95 | *RSE values for SDG&E's enhanced inspection programs were grouped in the November RAMP filing, RSE value is listed in Pole Replacement and Reinforcement
| 2019 actual | NA |  | NA |  | NA |  |  |  | Reliability | New | NA | FRMMA | Meets and exceeds | GO 165, GO 95
| 2020 | 2880 | 4320 | NA | NA | 0.20837 |  |  |  | Reliability | New | NA | FRMMA | Meets and exceeds | GO 165, GO 95
| 2021 | 1944 | 2916 | NA | NA | 0.14065 |  |  |  | Reliability | New | NA | FRMMA | Meets and exceeds | GO 165, GO 95
| 2022 | 1944 | 2916 | NA | NA | 0.14065 |  |  |  | Reliability | New | NA | FRMMA | Meets and exceeds | GO 165, GO 95
| 2020-2022 Plan Total | 6768 | 10152 | NA | NA | 0.48967 |  |  |  | Reliability | New | NA | FRMMA | Meets and exceeds | GO 165, GO 95
Drone Inspections (O&M) *Flights & Assessments | 2019 plan | NA | NA | NA | NA | NA | All equipment failure related (less hot connections) | * |  | Reliability | NA | NA | NA | Meets and exceeds | GO 165, GO 95 | *RSE values for SDG&E's enhanced inspection programs were grouped in the November RAMP filing, RSE value is listed in Pole Replacement and Reinforcement
| 2019 actual | 13474 |  | NA |  | NA |  |  |  | Reliability | New | NA | FRMMA | Meets and exceeds | GO 165, GO 95
| 2020 | 21000 | 25700 | NA | NA | 1.3515 |  |  |  | Reliability | New | NA | FRMMA | Meets and exceeds | GO 165, GO 95
| 2021 | 19200 | 22400 | NA | NA | 1.2039 |  |  |  | Reliability | New | NA | FRMMA | Meets and exceeds | GO 165, GO 95
| 2022 | 12500 | 17800 | NA | NA | 0.87689 |  |  |  | Reliability | New | NA | FRMMA | Meets and exceeds | GO 165, GO 95
| 2020-2022 Plan Total | 52700 | 65900 | NA | NA | 3.4323 |  |  |  | Reliability | New | NA | FRMMA | Meets and exceeds | GO 165, GO 95
Drone Inspections (O&M) *Enigineering & Construction | 2019 plan | NA | NA | NA | NA | NA | All equipment failure related (less hot connections) | * |  | Reliability | NA | NA | NA | Meets and exceeds | GO 165, GO 95 | *RSE values for SDG&E's enhanced inspection programs were grouped in the November RAMP filing, RSE value is listed in Pole Replacement and Reinforcement
| 2019 actual | NA |  | NA |  | NA |  |  |  | Reliability | New | NA | FRMMA | Meets and exceeds | GO 165, GO 95
| 2020 | 25500 | 28800 | NA | NA | 1.5715 |  |  |  | Reliability | New | NA | FRMMA | Meets and exceeds | GO 165, GO 95
| 2021 | 23000 | 25600 | NA | NA | 1.4065 |  |  |  | Reliability | New | NA | FRMMA | Meets and exceeds | GO 165, GO 95
| 2022 | 18200 | 21350 | NA | NA | 1.1446 |  |  |  | Reliability | New | NA | FRMMA | Meets and exceeds | GO 165, GO 95
| 2020-2022 Plan Total | 66700 | 75750 | NA | NA | 4.1225 |  |  |  | Reliability | New | NA | FRMMA | Meets and exceeds | GO 165, GO 95
Circuit Ownership | 2019 plan | NA | NA | NA | NA | NA | All equipment failure related (less hot connections) | * |  | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451 | *RSE values for SDG&E's enhanced inspection programs were grouped in the November RAMP filing, RSE value is listed in Pole Replacement and Reinforcement
| 2019 actual | NA |  | NA |  | NA |  |  |  | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020 | 475 | 575 | NA | NA | 0.030387 |  |  |  | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2021 | 475 | 575 | NA | NA | 0.030387 |  |  |  | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2022 | 475 | 575 | NA | NA | 0.030387 |  |  |  | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020-2022 Plan Total | 1425 | 1725 | NA | NA | 0.091162 |  |  |  | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
Substation System Inspections | 2019 plan | Base | Base | NA | NA | NA | All equipment failure | NA | NA | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | GO174
| 2019 actual | Base |  | NA | NA | NA |  | NA | NA | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | GO174
| 2020 | Base | Base | NA | NA | NA |  | NA | NA | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | GO174
| 2021 | Base | Base | NA | NA | NA |  | NA | NA | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | GO174
| 2022 | Base | Base | NA | NA | NA |  | NA | NA | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | GO174
| 2020-2022 Plan Total | Base | Base | NA | NA | NA |  | NA | NA | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | GO174

## Table24a
TABLE 24A: Asset Management and Inspections Initiatives
Initiative Activity | Year | 5 year Detailed Inspections |  | Annual Patrols |  | Wood Pole Intrusive Inspections
|  | Low | High | Low | High | Low | High
SDG&E Corrective Maintenance Program (HFTD) | 2019 Plan | 16000 | 17000 | 85000 | 87000 | 18000 | 20000
| 2019 Actual | 16329 |  | 86401 |  | 19729
| 2020 | 17000 | 18000 | 85000 | 87000 | 17000 | 19000
| 2021 | 22000 | 23000 | 85000 | 87000 | 7000 | 9000
| 2022 | 18000 | 19000 | 85000 | 87000 | 300 | 500
| 2020-20222 Plan Totals | 57000 | 60000 | 255000 | 261000 | 24300 | 28500
Initiative Activity | Year | Transmission Visual Inspections |  | Transmission Infrared Inspections |  | Transmission Detailed Inspections |  | Additional Transmission Aerial 69kV Tier 3 Visual Inspection
|  | Low | High | Low | High | Low | High | Low | High
Transmission System Inspections | 2019 Plan | 94 | 140 | 90 | 136 | 29 | 45 | 21 | 33
| 2019 Actual | 116 |  | 112 |  | 37 |  | 27
| 2020 | 94 | 140 | 90 | 136 | 33 | 49 | 21 | 33
| 2021 | 94 | 140 | 90 | 136 | 30 | 46 | 21 | 33
| 2022 | 94 | 140 | 90 | 136 | 30 | 46 | 21 | 33
| 2020-20222 Plan Totals | 282 | 420 | 270 | 408 | 93 | 141 | 63 | 99
Initiative Activity | Year | Infrared/Corona Inspections
|  | Low | High
Infrared Corona | 2019 Plan | NA | NA
| 2019 Actual | NA
| 2020 | 7000 | 10000
| 2021 | 7000 | 10000
| 2022 | 7000 | 10000
| 2020-20222 Plan Totals | 21000 | 30000
Initiative Activity | Year | QA/QC Inspections
|  | Low | High
HFTD Tier 3 Inspections | 2019 Plan | 11000 | 12000
| 2019 Actual | 15176
| 2020 | 11000 | 12000
| 2021 | 11000 | 12000
| 2022 | 12000 | 13000
| 2020-20222 Plan Totals | 34000 | 37000
Initiative Activity | Year | Drone Inspections Completed
|  | Low | High
Drone Inspections | 2019 Plan | 9000 | 11000
| 2019 Actual | 10400
| 2020 | 28000 | 38000
| 2021 | 18000 | 21500
| 2022 | 15000 | 18000
| 2020-20222 Plan Totals | 61000 | 77500
Initiative Activity | Year | Substation Inspections
|  | Low | High
Substation System Inspections | 2019 Plan | 300 | 360
| 2019 Actual | 301
| 2020 | 300 | 360
| 2021 | 300 | 360
| 2022 | 300 | 360
| 2020-20222 Plan Totals | 900 | 1080

## Table25
TABLE 25: Vegetation Management and Inspections Initiatives
Initiative Activity | Year | Total per initiative spend |  | Line Miles to be treated |  | Spend per treated line mile | Ignition probability drivers targeted | Risk reduction | Risk-spend efficiency | Other risk drivers addressed | Existing/new | Existing/ What Proceeding | If New: Memorandum account | In / Exceeding Compliance with regulations | Cite Associated rule | Comments
|  | Low | High | Low | High
Tree Trimming | 2019 plan | *Base | Base | NA | NA | NA | Vegetation Contact | NA | NA | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451 | *In SDGE's 2019 WMP, Tree Trimming was listed as part of base business and costs for the program were not provided. Going forward, SDG&E will be providing these costs.
| 2019 actual | 33957 |  | NA |  | NA |  | NA | NA | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020 | 22220 | 33330 | NA | NA | 1.6076 |  | 50% | 122.46 | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2021 | 22220 | 33330 | NA | NA | 1.6076 |  | 50% | 122.46 | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2022 | 22220 | 33330 | NA | NA | 1.6076 |  | 50% | 122.46 | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020-2022 Plan Total | 66660 | 99990 | NA | NA | 4.8229 |  | 50% | 122.46 | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
Fuels Management Program | 2019 plan | 400 | 600 | NA | NA | 0.02894 | Reduces chance fault becomes an ignition, reduces initial propagation | NA | NA | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2019 actual | 5093 |  | NA |  | 0.14739 |  | NA | NA | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020 | 4000 | 6000 | NA | NA | 0.2894 |  | 0.38% | 5.1703 | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2021 | 4000 | 6000 | NA | NA | 0.2894 |  | 0.38% | 5.1703 | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2022 | 4000 | 6000 | NA | NA | 0.2894 |  | 0.38% | 5.1703 | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020-2022 Plan Total | 12000 | 18000 | NA | NA | 0.86821 |  | 0.38% | 5.1703 | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
Enhanced Inspections Patrols and Trimming | 2019 plan | 2400 | 3600 | NA | NA | 0.17364 | Vegetation Contact | NA | NA | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2019 actual | 7396 |  | NA |  | 0.21404 |  | NA | NA | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020 | 18882 | 28324 | NA | NA | 1.3662 |  | 5% | 14.41 | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2021 | 18882 | 28324 | NA | NA | 1.3662 |  | 5% | 14.41 | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2022 | 18882 | 28324 | NA | NA | 1.3662 |  | 5% | 14.41 | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020-2022 Plan Total | 56646 | 84972 | NA | NA | 4.0985 |  | 5% | 14.41 | Reliability | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
Pole Brushing | 2019 plan | *Base | Base | NA | NA | NA | Reduces chances that a fault will lead to an ignition | NA | NA | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451 | *In SDGE's 2019 WMP, Pole Brushing was listed as part of base business and costs for the program were not provided. Going forward, SDG&E will be providing these costs.
| 2019 actual | 3884 |  | NA |  | NA |  | NA | NA | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020 | 4754 | 7131 | NA | NA | 0.34395 |  | NA | NA | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2021 | 4754 | 7131 | NA | NA | 0.34395 |  | NA | NA | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2022 | 4754 | 7131 | NA | NA | 0.34395 |  | NA | NA | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020-2022 Plan Total | 14262 | 21393 | NA | NA | 1.0319 |  | NA | NA | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451

## Table25a
TABLE 25A: Vegetation Management and Inspections Initiatives
Initiative Activity | Year | Trees Inspected
|  | Low | High
Tree Trimming | 2019 Plan | 450000 | 460000
| 2019 Actual | 453330
| 2020 | 450000 | 460000
| 2021 | 450000 | 460000
| 2022 | 450000 | 460000
| 2020-2022 Plan Totals | 1350000 | 1380000
Initiative Activity | Year | Trees Trimmed to 25' clearance or removed
|  | Low | High
Enhanced Inspections Patrols and Trimming | 2019 Plan | 7000 | 8000
| 2019 Actual | 8310
| 2020 | 14000 | 20000
| 2021 | 14000 | 20000
| 2022 | 14000 | 20000
| 2020-2022 Plan Totals | 42000 | 60000
Initiative Activity | Year | Poles Brushed
|  | Low | High
Pole Brushing | 2019 Plan | 32000 | 39000
| 2019 Actual | 34000
| 2020 | 32000 | 39000
| 2021 | 32000 | 39000
| 2022 | 32000 | 39000
| 2020-2022 Plan Totals | 96000 | 117000
Initiative Activity | Year | Poles cleared
|  | Low | High
Fuels Management | 2019 Plan | 400 | 600
| 2019 Actual | 511
| 2020 | 400 | 600
| 2021 | 400 | 600
| 2022 | 400 | 600
| 2020-2022 Plan Totals | 1200 | 1800

## Table26
TABLE 26: Grid Operations and Protocols Initiatives
Initiative Activity | Year | Total per initiative spend |  | Line Miles to be treated |  | Spend per treated line mile | Ignition probability drivers targeted | Risk reduction | Risk-spend efficiency | Other risk drivers addressed | Existing/new | Existing/ What Proceeding | If New: Memorandum account | In / Exceeding Compliance with regulations | Cite Associated rule | Comments
|  | Low | High | Low | High
Recloser Protocols | 2019 plan | *Base | Base | NA | NA | NA | Reduces chance of fault leading to an ignition | NA | NA | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2019 actual | Base |  | NA |  | NA |  | NA | NA | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020 | Base | Base | NA | NA | NA |  | NA | NA | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2021 | Base | Base | NA | NA | NA |  | NA | NA | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2022 | Base | Base | NA | NA | NA |  | NA | NA | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020-2022 Plan Total | Base | Base | NA | NA | NA |  | NA | NA | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
Wildfire Infrastructure Protection Teams | 2019 plan | 700 | 1100 | NA | NA | 0.052092 | Employee Caused Ignitions | NA | NA | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451 | CFR cost estimates can fluctuate based on the actual conditions that accompany fire season. The Primary contract calls for 8 CFRs a day but in reality there are usually more ordered. Additionally, CFRs used during Extreme weather events and other fire related activations are not included in the above estimates
| 2019 actual | 1790 |  | NA |  | 0.10361 |  | NA | NA | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020 | 1334.4 | 2001.6 | NA | NA | 0.096545 |  | 0.76% | 31 | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2021 | 1334.4 | 2001.6 | NA | NA | 0.096545 |  | 0.76% | 31 | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2022 | 1334.4 | 2001.6 | NA | NA | 0.096545 |  | 0.76% | 31 | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020-2022 Plan Total | 4003.2 | 6004.8 | NA | NA | 0.28963 |  | 0.76% | 31 | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
Other Special Work Procedures | 2019 plan | Base | Base | NA | NA | NA | Employee Caused Ignitions | NA | NA | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2019 actual | Base |  | NA |  | NA |  | NA | NA | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020 | Base | Base | NA | NA | NA |  | NA | NA | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2021 | Base | Base | NA | NA | NA |  | NA | NA | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2022 | Base | Base | NA | NA | NA |  | NA | NA | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020-2022 Plan Total | Base | Base | NA | NA | NA |  | NA | NA | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
Strategy for Minimizing Public Safety Risk During High Wildfire Conditions | 2019 plan | Base | Base | NA | NA | NA | All | NA | NA | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code §§ 399.2(a) and 451, D.12-04-024, and Commission Resolution ESRB-8.
| 2019 actual | Base |  | NA |  | NA | All | NA | NA | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code §§ 399.2(a) and 451, D.12-04-024, and Commission Resolution ESRB-8.
| 2020 | Base | Base | NA | NA | NA | All | 50% | 117.9787 | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code §§ 399.2(a) and 451, D.12-04-024, and Commission Resolution ESRB-8.
| 2021 | Base | Base | NA | NA | NA | All | 50% | 117.9787 | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code §§ 399.2(a) and 451, D.12-04-024, and Commission Resolution ESRB-8.
| 2022 | Base | Base | NA | NA | NA | All | 50% | 117.9787 | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code §§ 399.2(a) and 451, D.12-04-024, and Commission Resolution ESRB-8.
| 2020-2022 Plan Total | Base | Base | NA | NA | NA | All | 50% | 117.9787 | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code §§ 399.2(a) and 451, D.12-04-024, and Commission Resolution ESRB-8.
Mitigating the Public Safety Impact of PSPS Protocols | 2019 plan | Base | Base | NA | NA | NA | NA | This control was grouped with Strategy for Minimizing Public Safety Risk During High Wildfire Conditions for purposes of RSE calculations |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 399.2(a) and 451, D.12-04-024, and Commission Resolution ESRB-8
| 2019 actual | Base |  | NA | NA | NA | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 399.2(a) and 451, D.12-04-024, and Commission Resolution ESRB-8
| 2020 | Base | Base | NA | NA | NA | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 399.2(a) and 451, D.12-04-024, and Commission Resolution ESRB-8
| 2021 | Base | Base | NA | NA | NA | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 399.2(a) and 451, D.12-04-024, and Commission Resolution ESRB-8
| 2022 | Base | Base | NA | NA | NA | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 399.2(a) and 451, D.12-04-024, and Commission Resolution ESRB-8
| 2020-2022 Plan Total | Base | Base | NA | NA | NA | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 399.2(a) and 451, D.12-04-024, and Commission Resolution ESRB-8
Communication Practices (Capital) | 2019 plan | NA | NA | NA | NA | NA | NA | This control was grouped with Strategy for Minimizing Public Safety Risk During High Wildfire Conditions for purposes of RSE calculations |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 399.2(a) and 451, D.12-04-024, and Commission Resolution ESRB-8
| 2019 actual | NA |  | NA | NA | NA | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 399.2(a) and 451, D.12-04-024, and Commission Resolution ESRB-8
| 2020 | 2000 | 4000 | NA | NA | 0.174 | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 399.2(a) and 451, D.12-04-024, and Commission Resolution ESRB-8
| 2021 | 0 | 0 | NA | NA | 0 | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 399.2(a) and 451, D.12-04-024, and Commission Resolution ESRB-8
| 2022 | 0 | 0 | NA | NA | 0 | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 399.2(a) and 451, D.12-04-024, and Commission Resolution ESRB-8
| 2020-2022 Plan Total | 2000 | 4000 | NA | NA | 0.174 | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 399.2(a) and 451, D.12-04-024, and Commission Resolution ESRB-8
Communication Practices (O&M) | 2019 plan | 2000 | 3000 | NA | NA | 0.145 | NA | This control was grouped with Strategy for Minimizing Public Safety Risk During High Wildfire Conditions for purposes of RSE calculations |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 399.2(a) and 451, D.12-04-024, and Commission Resolution ESRB-8
| 2019 actual | 3057 |  | NA |  | 0.17694 | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 399.2(a) and 451, D.12-04-024, and Commission Resolution ESRB-8
| 2020 | 4458 | 5397 | NA | NA | 0.285 | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 399.2(a) and 451, D.12-04-024, and Commission Resolution ESRB-8
| 2021 | 4458 | 5397 | NA | NA | 0.285 | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 399.2(a) and 451, D.12-04-024, and Commission Resolution ESRB-8
| 2022 | 4458 | 5397 | NA | NA | 0.285 | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 399.2(a) and 451, D.12-04-024, and Commission Resolution ESRB-8
| 2020-2022 Plan Total | 13374 | 16191 | NA | NA | 0.856 | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 399.2(a) and 451, D.12-04-024, and Commission Resolution ESRB-8
Aviation Firefighting Program (Capital) | 2019 plan | NA | NA | NA | NA | NA | Fire Suppression | NA | NA | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2019 actual | NA |  | NA |  | NA |  | NA | NA | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020 | 5760 | 8640 | NA | NA | 0.41674 |  | See Aviation Firefighting Program (O&M) |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2021 | 11520 | 17280 | NA | NA | 0.83348 |  |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2022 | 0 | 0 | NA | NA | 0 |  |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020-2022 Plan Total | 17280 | 25920 | NA | NA | 1.2502 |  |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
Aviation Firefighting Program (O&M) | 2019 plan | 6000 | 9000 | NA | NA | 0.4341 | Fire Suppression | NA | NA | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2019 actual | 3938 |  | NA |  | 0.11397 |  | NA | NA | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020 | 7202 | 8719 | NA | NA | 0.46076 |  | 5% | 31.48 | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2021 | 7202 | 8719 | NA | NA | 0.46076 |  | 5% | 31.48 | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2022 | 7202 | 8719 | NA | NA | 0.46076 |  | 5% | 31.48 | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020-2022 Plan Total | 21606 | 26157 | NA | NA | 1.3823 |  | 5% | 31.48 | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
Industrial Fire Brigade | 2019 plan | Base | Base | NA | NA | NA | Fire Suppression | NA | NA | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2019 actual | Base |  | NA | NA | NA |  | NA | NA | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020 | 270.4 | 405.6 | NA | NA | 0.019564 |  | 0.114% | 22.9452 | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2021 | 270.4 | 405.6 | NA | NA | 0.019564 |  | 0.114% | 22.9452 | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2022 | 270.4 | 405.6 | NA | NA | 0.019564 |  | 0.114% | 22.9452 | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020-2022 Plan Total | 811.2 | 1216.8 | NA | NA | 0.058691 |  | 0.114% | 22.9452 | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451

## Table27
TABLE 27: Data Governance Initiatives
Initiative Activity | Year | Total per initiative spend |  | Line Miles to be treated |  | Spend per treated line mile | Ignition probability drivers targeted | Risk reduction | Risk-spend efficiency | Other risk drivers addressed | Existing/new | Existing/ What Proceeding | If New: Memorandum account | In / Exceeding Compliance with regulations | Cite Associated rule | Comments
|  | Low | High | Low | High
Geographic Information Systems | 2019 plan | Base | Base | NA | NA | NA | NA | NA | NA | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2019 actual | Base |  | NA |  | NA | NA | NA | NA | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020 | Base | Base | NA | NA | NA | NA | NA | NA | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2021 | Base | Base | NA | NA | NA | NA | NA | NA | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2022 | Base | Base | NA | NA | NA | NA | NA | NA | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020-2022 Plan Total | Base | Base | NA | NA | NA | NA | NA | NA | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
Ignition Management Program | 2019 plan | Base | Base | NA | NA | NA | NA | This was grouped with OH hardening (BC and CC) and Undergrounding for the purpose of calculating RSE's |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2019 actual | NA |  | NA |  | NA | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020 | 285 | 345 | NA | NA | 0.018232 | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2021 | 285 | 345 | NA | NA | 0.018232 | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2022 | 258 | 345 | NA | NA | 0.017451 | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020-2022 Plan Total | 828 | 1035 | NA | NA | 0.053916 | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451

## Table28
TABLE 28: Resource Allocation Methodology Initiatives
Initiative Activity | Year | Total per initiative spend (Capital) |  | Line Miles to be treated |  | Spend per treated line mile | Ignition probability drivers targeted | Risk reduction | Risk-spend efficiency | Other risk drivers addressed | Existing/new | Existing/ What Proceeding | If New: Memorandum account | In / Exceeding Compliance with regulations | Cite Associated rule | Comments
|  | Low | High | Low | High
Asset Management (capital) | 2019 plan | NA | NA | NA | NA | NA | NA | This was grouped with OH hardening (BC and CC) and Undergrounding for the purpose of calculating RSE's |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2019 actual | NA |  | NA | NA | NA | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020 | 8774 | 10621 | NA | NA | 0.5613 | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2021 | 2500 | 5000 | NA | NA | 0.21705 | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2022 | 3000 | 7500 | NA | NA | 0.30387 | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020-2022 Plan Total | 14274 | 23121 | NA | NA | 1.0822 | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
Asset Management (O&M) | 2019 plan | 1200 | 1800 | NA | NA | 0.086821 | NA | This was grouped with OH hardening (BC and CC) and Undergrounding for the purpose of calculating RSE's |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2019 actual | 107 |  | NA |  | 0.0030966 | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020 | 400 | 500 | NA | NA | 0.026046 | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2021 | 500 | 600 | NA | NA | 0.031834 | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2022 | 500 | 600 | NA | NA | 0.031834 | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020-2022 Plan Total | 1400 | 1700 | NA | NA | 0.089715 | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
Wildfire Mitigation Personnel | 2019 plan | NA | NA | NA | NA | NA | NA | This was grouped with OH hardening (BC and CC) and Undergrounding for the purpose of calculating RSE's |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2019 actual | NA |  | NA |  | NA | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020 | 1663 | 2013 | NA | NA | 0.10638 | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2021 | 1663 | 2013 | NA | NA | 0.10638 | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2022 | 1663 | 2013 | NA | NA | 0.10638 | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020-2022 Plan Total | 4989 | 6039 | NA | NA | 0.31915 | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
PSPS Mitigation Engineering Team | 2019 plan | NA | NA | NA | NA | NA | NA | This was grouped with OH hardening (BC and CC) and Undergrounding for the purpose of calculating RSE's |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451 | * Costs for this team have been grouped with Wildfire Mitigation Personnel
| 2019 actual | NA |  | NA |  | NA | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020 | * |  | NA | NA | NA | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2021 |  |  | NA | NA | NA | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2022 |  |  | NA | NA | NA | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020-2022 Plan Total |  |  | NA | NA | NA | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451

## Table29
TABLE 29: Emergency Planning and Preparedness Initiatives
Initiative Activity | Year | Total per initiative spend |  | Line Miles to be treated |  | Spend per treated line mile | Ignition probability drivers targeted | Risk reduction | Risk-spend efficiency | Other risk drivers addressed | Existing/new | Existing/ What Proceeding | If New: Memorandum account | In / Exceeding Compliance with regulations | Cite Associated rule | Comments
|  | Low | High | Low | High
Customer Support in Emergencies | 2019 plan | * |  | NA | NA | NA | NA | This control was grouped with Strategy for Minimizing Public Safety Risk During High Wildfire Conditions for purposes of RSE calculations |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451 | * Costs for this program are included in Emergency Management Operations
| 2019 actual |  |  | NA |  | NA | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020 |  |  | NA | NA | NA | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2021 |  |  | NA | NA | NA | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2022 |  |  | NA | NA | NA | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020-2022 Plan Total |  |  | NA | NA | NA | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
Disaster and Emergency Preparedness Plan | 2019 plan | * |  | NA | NA | NA | NA | This control was grouped with Strategy for Minimizing Public Safety Risk During High Wildfire Conditions for purposes of RSE calculations |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451 | * Costs for this program are included in Emergency Management Operations
| 2019 actual |  |  | NA |  | NA | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020 |  |  | NA | NA | NA | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2021 |  |  | NA | NA | NA | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2022 |  |  | NA | NA | NA | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020-2022 Plan Total |  |  | NA | NA | NA | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
Emergency Management Operations (O&M) | 2019 plan | 4000 | 6000 | NA | NA | 0.2894 | NA | This control was grouped with Strategy for Minimizing Public Safety Risk During High Wildfire Conditions for purposes of RSE calculations |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2019 actual | 4727 |  | NA |  | 0.1368 | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020 | 4088 | 4654 | NA | NA | 0.253 | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2021 | 4088 | 4654 | NA | NA | 0.253 | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2022 | 4088 | 4654 | NA | NA | 0.253 | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020-2022 Plan Total | 12264 | 13962 | NA | NA | 0.75899 | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
Emergency Management Operations (Capital) | 2019 plan | NA | NA | NA | NA | NA | NA | This control was grouped with Strategy for Minimizing Public Safety Risk During High Wildfire Conditions for purposes of RSE calculations |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2019 actual | NA |  | NA |  | NA | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020 | 3600 | 5400 | NA | NA | 0.26046 | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2021 | 0 | 0 | NA | NA | 0 | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2022 | 0 | 0 | NA | NA | 0 | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451
| 2020-2022 Plan Total | 3600 | 5400 | NA | NA | 0.26046 | NA |  |  | NA | Existing | TY 2019 GRC | NA | Meets and exceeds | P.U. Code § 451

## Table 30
TABLE 30
Initiative Activity | Year | Total per initiative spend |  | Line Miles to be treated |  | Spend per treated line mile | Ignition probability drivers targeted | Risk reduction | Risk-spend efficiency | Other risk drivers addressed | Existing/new | Existing/ What Proceeding | If New: Memorandum account | In / Exceeding Compliance with regulations | Cite Associated rule | Comments
|  | Low | High | Low | High
Community Engagement - See Table 26 Customer Communications and Mitigating the Public Safety Impact of PSPS Protocols

## Table 31
TABLE 31: Change in Drivers of Ignition Probability Taking Into Account Planned Initiatives, For Each Year of Plan
Incident type by ignition probability driver |  | Near misses tracked (y/n)? | Number of Incidents per year |  |  | Avg % probability of ignition per incident |  |  | Number of Ignitions per year
|  |  | 2020 | 2021 | 2022 | 2020 | 2021 | 2022 | 2020 | 2021 | 2022
Contact from object | All types of object contact | Yes | bar: Number of Incidents per year 2020 to Number of Ignitions per year 2022
| Animal contact | Yes | bar: Number of Incidents per year 2020 to Number of Ignitions per year 2022
| Balloon contact | Yes | bar: Number of Incidents per year 2020 to Number of Ignitions per year 2022
| Veg. contact | Yes | bar: Number of Incidents per year 2020 to Number of Ignitions per year 2022
| Vehicle contact | Yes | bar: Number of Incidents per year 2020 to Number of Ignitions per year 2022
All types of equipment / facility failure | All types | Yes | bar: Number of Incidents per year 2020 to Number of Ignitions per year 2022
| Capacitor bank failure | Yes | bar: Number of Incidents per year 2020 to Number of Ignitions per year 2022
| Conductor failure - all | Yes | bar: Number of Incidents per year 2020 to Number of Ignitions per year 2022
| Conductor failure - wires down | Yes | bar: Number of Incidents per year 2020 to Number of Ignitions per year 2022
| Fuse failure - all | Yes | bar: Number of Incidents per year 2020 to Number of Ignitions per year 2022
| Fuse failure - conventional blown fuse | Yes | bar: Number of Incidents per year 2020 to Number of Ignitions per year 2022
| Lightning arrestor failure | Yes | bar: Number of Incidents per year 2020 to Number of Ignitions per year 2022
| Splice/Clamp/Connector | Yes | bar: Number of Incidents per year 2020 to Number of Ignitions per year 2022
| Switch failure | Yes | bar: Number of Incidents per year 2020 to Number of Ignitions per year 2022
| Transformer failure | Yes | bar: Number of Incidents per year 2020 to Number of Ignitions per year 2022
Wire-to-wire contact / contamination |  | Yes | bar: Number of Incidents per year 2020 to Number of Ignitions per year 2022
Vandalism/Theft |  | Yes | bar: Number of Incidents per year 2020 to Number of Ignitions per year 2022
Other