## Sheet1
Cause_Description | Fraction All Outages | Fraction OH Outages
Microgrid Failure (generator/inverter/battery/control system/ultra-capacitor/transformer) | 0.04988% | 0.09294%
Faulted cable | 16.16% | 3.16%
Transformer (station) failure/contact | 11.07% | 3.996%
Tee failure | 4.589% | 0%
Crossarm failure/contact | 2.843% | 5.3%
Pole - contact/damage/broke/rotted/on fire | 2.544% | 4.74%
Conductor contact/failure/overload/wire slap | 1.895% | 3.532%
UG connector failure (splice/rack/tap/shoofly/sleeve/probe/LBE/bushing) | 1.746% | 0.3717%
OH connector failure (jumper/splice/squeeze-on) | 1.696% | 3.067%
Cutout failure | 1.596% | 2.881%
Hardware failure | 0.8978% | 0.7435%
Arrester failure | 0.8479% | 1.58%
Switch failure/contact | 0.798% | 1.115%
Fuse - overload/inadequate size/fatigue | 0.7481% | 1.022%
Capacitor/cap bank failure | 0.5985% | 1.115%
Flashover due to contamination/overload/tracking | 0.5985% | 0.4647%
Fuse holder/fuse cabinet | 0.5486% | 0.09294%
Pothead failure | 0.5486% | 1.022%
Disconnect Failure | 0.2993% | 0.5576%
Insulator/pin failure | 0.2993% | 0.5576%
Terminator failure/contact | 0.1496% | 0%
Ground bank failure/contact | 0.04988% | 0.09294%
Primary wire down | 0.04988% | 0.09294%
Recloser/service restorer failure/contact | 0.04988% | 0%
Regulator failure/contact | 0.04988% | 0.09294%
SCADA malfunction | 0.04988% | 0.09294%
Balloon contact | 4.738% | 8.829%
Bird contact | 4.389% | 8.178%
Animal contact | 1.047% | 1.115%
Tree/branch or palm trunk fell on line or equipment | 0.7481% | 1.301%
Foreign object | 0.4988% | 0.8364%
Detached palm frond contact | 0.2494% | 0.4647%
Vandalism/sabotage | 0.1995% | 0%
Flashover due to vegetation/bird-branch drop | 0.1496% | 0.2788%
Aircraft | 0.04988% | 0.09294%
Damage by gunshot | 0.04988% | 0.09294%
Tree contact due to growth/encroachment | 0.04988% | 0.09294%
Deenergized for safety | 0.9476% | 0.9294%
Go-back (additional outage taken to complete repairs) | 0.9975% | 0.3717%
Customer trouble/request | 1.546% | 0.7435%
Switching/mapping error/tagged incorrectly | 0.6983% | 0.3717%
Protection misoperation (UFO, settings, fuse miscoordination) | 0.399% | 0.5576%
SCE/Other Entity failure | 0.399% | 0.7435%
Load Imbalance | 0.2494% | 0.1859%
Voltage dip | 0.09975% | 0%
Fire/smoke | 0.09975% | 0.1859%
SDG&E contractor crew error | 0.5985% | 0.9294%
SDG&E Crew error | 0.3491% | 0.2788%
SDG&E contractor heavy equipment contact/dig-in | 0.09975% | 0%
SDG&E Crew Personnel contact | 0.04988% | 0.09294%
Vehicle contact | 11.32% | 10.04%
Heavy equipment contact/dig-in | 1.147% | 0.2788%
Line fault/tree trimming | 0.3491% | 0.6506%
Undetermined | 11.12% | 16.73%
Undetermined (severe weather) | 3.791% | 5.297%
Lightning/arrester/xfmr failure (severe weather) | 1.845% | 2.788%
Wire slap/pole down/wire down (severe weather) | 0.5985% | 1.115%
Tree/branch or palm trunk fell on line or equipment (severe weather) | 0.1995% | 0.3717%
Detached palm frond contact (severe weather) | 0.04988% | 0.09294%
Foreign object (severe weather) | 0.04988% | 0.09294%
Tree sway contact due to high wind (severe weather) | 0.04988% | 0.09294%