## Raw Data
Outage_ID | failure_time | h_years_calc | uh_years_calc | Hardened Faults | Zone | HardenedDate | Occurrence_Date | Cause_Category | Cause | Secondary_Cause | Cause_Description | schematicssomlabeltext | DamagedDevice | hyear | oyear
010729E5031 | Before | 1.6521 | 20.3589 | 1 | Tier 2 | 2021-05-07 | 2001-07-29 | Equipment | 502 |  | Arrester (lightning) failure | #2 5/2 AWAC AL | LIGHTNING ARRESTER | 2021 | 2001
010815E5027 | Before | 3.3014 | 18.7096 | 1 | Tier 2 | 2019-09-13 | 2001-08-15 | Equipment | 508 |  | Flashover/equip contam/overload | #2 5/2 AWAC AL |  | 2019 | 2001
010818E5014 | Before | 3.3014 | 18.7096 | 1 | Tier 2 | 2019-09-13 | 2001-08-18 | Equipment | 508 |  | Flashover/equip contam/overload | #2 5/2 AWAC AL |  | 2019 | 2001
010902E5016 | Before | 0.7863 | 21.2247 | 1 | Tier 3 | 2022-03-19 | 2001-09-02 | Weather | 410 |  | Lightning Arrester/Transformer failure | #2 5/2 AWAC AL |  | 2022 | 2001
010902E5028 | Before | 4.5945 | 17.4164 | 1 | Tier 3 | 2018-05-29 | 2001-09-02 | Weather | 410 |  | Lightning Arrester/Transformer failure | #2 5/2 AWAC AL |  | 2018 | 2001
010903E5009 | Before | 5.6027 | 16.4082 | 1 | Tier 3 | 2017-05-26 | 2001-09-03 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2017 | 2001
010929E5040 | Before | 2.9589 | 19.0521 | 1 | Tier 2 | 2020-01-16 | 2001-09-29 | Equipment | 522 |  | Fuse overloaded/inadequate fuse size | 336.4 ACSR AL | FUSE | 2020 | 2001
011001E5002 | Before | 3.0137 | 18.9973 | 1 | Tier 2 | 2019-12-27 | 2001-10-01 | Weather | 404 |  | Circ. Flashover/storm/high winds/undet. | 336 ACSR AL |  | 2019 | 2001
011001E5002 | Before | 3.0137 | 18.9973 | 1 | Tier 2 | 2019-12-27 | 2001-10-01 | Weather | 404 |  | Circ. Flashover/storm/high winds/undet. | 336.4 ACSR AL |  | 2019 | 2001
011024E5003 | Before | 3.0137 | 18.9973 | 1 | Tier 3 | 2019-12-27 | 2001-10-24 | Foreign Object | 308 |  | Bird contact | 336 ACSR AL |  | 2019 | 2001
011028E7501 | Before | 4.2658 | 17.7452 | 1 | Tier 2 | 2018-09-26 | 2001-10-28 | Equipment | 516 |  | Connector/jumper/splice/elbow/rack | #2 5/2 AWAC AL |  | 2018 | 2001
011124E5080 | Before | 4.5699 | 17.4411 | 1 | Tier 2 | 2018-06-07 | 2001-11-24 | Weather | 408 | 520 | Ice or snow/Equipment failure | #2 5/2 AWAC AL | FUSE | 2018 | 2001
011209E5030 | Before | 3.0247 | 18.9863 | 1 | Tier 3 | 2019-12-23 | 2001-12-09 | Weather | 426 |  | Tree fell on line due to storm/wind | #2 5/2 AWAC AL |  | 2019 | 2001
011212E5018 | Before | 2.9589 | 19.0521 | 1 | Tier 2 | 2020-01-16 | 2001-12-12 | Equipment | 522 |  | Fuse overloaded/inadequate fuse size | 336.4 ACSR AL | FUSE | 2020 | 2001
011212E7602 | Before | 5 | 17.011 | 1 | Tier 2 | 2018-01-01 | 2001-12-12 | Customer Contact | 710 | 532 | Vehicle contact | 3/0 ACSR AL | POLE | 2018 | 2001
020211E5005 | Before | 3.6274 | 18.3836 | 1 | Tier 2 | 2019-05-17 | 2002-02-11 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2019 | 2002
020211E5005 | Before | 2.3397 | 19.6712 | 1 | Tier 2 | 2020-08-29 | 2002-02-11 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2020 | 2002
020216E5025 | Before | 5.337 | 16.674 | 1 | Tier 3 | 2017-08-31 | 2002-02-16 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2017 | 2002
020216E5025 | Before | 5.337 | 16.674 | 1 | Tier 3 | 2017-08-31 | 2002-02-16 | Customer Contact | 710 | 532 | Vehicle contact | 336 ACSR AL | POLE | 2017 | 2002
020629E5024 | Before | 0.7863 | 21.2247 | 1 | Tier 3 | 2022-03-19 | 2002-06-29 | Equipment | 522 |  | Fuse overloaded/inadequate fuse size | #2 5/2 AWAC AL | FUSE | 2022 | 2002
020712E5031 | Before | 3 | 19.011 | 1 | Tier 3 | 2020-01-01 | 2002-07-12 | Weather | 410 | 550 | Lightning Arrester/Transformer failure | #2 5/2 AWAC AL | TRANSFORMER | 2020 | 2002
020712E5031 | Before | 3 | 19.011 | 1 | Tier 3 | 2020-01-01 | 2002-07-12 | Weather | 410 | 550 | Lightning Arrester/Transformer failure | #2 ACSR AL | TRANSFORMER | 2020 | 2002
020727E5032 | Before | 1.0356 | 20.9753 | 1 | Tier 2 | 2021-12-18 | 2002-07-27 | Customer Contact | 710 | 532 | Vehicle contact | #2 3/4 AWAC AL | POLE | 2021 | 2002
020727E5032 | Before | 1.0356 | 20.9753 | 1 | Tier 2 | 2021-12-18 | 2002-07-27 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2021 | 2002
020812E7202 | Before | 5.6219 | 16.389 | 1 | Tier 2 | 2017-05-19 | 2002-08-12 | Equipment | 513 |  | Conductor failure/wire down | #2 5/2 AWAC AL | OH CONDUCTOR | 2017 | 2002
020812E7203 | Before | 5.6219 | 16.389 | 1 | Tier 2 | 2017-05-19 | 2002-08-12 | Equipment | 513 |  | Conductor failure/wire down | #2 5/2 AWAC AL | OH CONDUCTOR | 2017 | 2002
020904E5002 | Before | 7.1534 | 14.8575 | 1 | Tier 3 | 2015-11-07 | 2002-09-04 | Equipment | 550 |  | Transformer faulted/mechanical | #2 5/2 AWAC AL | TRANSFORMER | 2015 | 2002
021107E5005 | Before | 1.2466 | 20.7644 | 1 | Tier 3 | 2021-10-02 | 2002-11-07 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2021 | 2002
021110E7501 | Before | 5 | 17.011 | 1 | Tier 3 | 2018-01-01 | 2002-11-10 | Equipment | 554 |  | Crossarm failure | #2 5/2 AWAC AL | CROSSARM | 2018 | 2002
021125E5127 | Before | 3.0247 | 18.9863 | 1 | Tier 3 | 2019-12-23 | 2002-11-25 | Weather | 426 |  | Tree fell on line due to storm/wind | #2 5/2 AWAC AL |  | 2019 | 2002
021125E5135 | Before | 7.9041 | 14.1068 | 1 | Tier 2 | 2015-02-06 | 2002-11-25 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2015 | 2002
021126E5001 | Before | 3.2685 | 18.7425 | 1 | Tier 2 | 2019-09-25 | 2002-11-26 | Weather | 426 |  | Tree fell on line due to storm/wind | #2 5/2 AWAC AL | POLE | 2019 | 2002
021128E7101 | Before | 3.0356 | 18.9753 | 1 | Tier 3 | 2019-12-19 | 2002-11-28 | Weather | 404 |  | Circ. Flashover/storm/high winds/undet. | #2 5/2 AWAC AL | FUSE | 2019 | 2002
021129E5148 | Before | 3.9753 | 18.0356 | 1 | Tier 2 | 2019-01-10 | 2002-11-29 | Weather | 412 | 513 | Wind - wires slap/pole down | #2 5/2 AWAC AL | OH CONDUCTOR | 2019 | 2002
021129E5148 | Before | 3.9753 | 18.0356 | 1 | Tier 2 | 2019-01-10 | 2002-11-29 | Weather | 412 | 513 | Wind - wires slap/pole down | #2 5/2 AWAC AL | OH CONDUCTOR | 2019 | 2002
021130E5168 | Before | 6 | 16.011 | 1 | Tier 2 | 2017-01-01 | 2002-11-30 | Customer Contact | 710 | 532 | Vehicle contact | #2 ACSR AL | POLE | 2017 | 2002
021211E5034 | Before | 4.8384 | 17.1726 | 1 | Tier 3 | 2018-03-01 | 2002-12-11 | Equipment | 554 |  | Crossarm failure | 336 ACSR AL | CROSSARM | 2018 | 2002
030106E5019 | Before | 5.5096 | 16.5014 | 1 | Tier 3 | 2017-06-29 | 2003-01-06 | Weather | 412 | 513 | Wind - wires slap/pole down | #2 5/2 AWAC AL | OH CONDUCTOR | 2017 | 2003
030106E5019 | Before | 5.5096 | 16.5014 | 1 | Tier 3 | 2017-06-29 | 2003-01-06 | Weather | 412 | 513 | Wind - wires slap/pole down | #2 5/2 AWAC AL | OH CONDUCTOR | 2017 | 2003
030106E5054 | Before | 5.3397 | 16.6712 | 1 | Tier 3 | 2017-08-30 | 2003-01-06 | Weather | 404 | 554 | Circ. Flashover/storm/high winds/undet. | 336 ACSR AL | CROSSARM | 2017 | 2003
030107E5742 | Before | 9.0767 | 12.9342 | 1 | Tier 2 | 2013-12-05 | 2003-01-07 | Weather | 404 |  | Circ. Flashover/storm/high winds/undet. | #2 ACSR AL |  | 2013 | 2003
030107E7604 | Before | 3.3041 | 18.7068 | 1 | Tier 2 | 2019-09-12 | 2003-01-07 | Weather | 404 |  | Circ. Flashover/storm/high winds/undet. | 336 ACSR AL | FUSE | 2019 | 2003
030109E5119 | Before | 3.1753 | 18.8356 | 1 | Tier 2 | 2019-10-29 | 2003-01-09 | Equipment | 534 |  | Pothead failure | 336 ACSR AL | POTHEAD | 2019 | 2003
030126E5003 | Before | 5 | 17.011 | 1 | Tier 3 | 2018-01-01 | 2003-01-26 | Customer Contact | 710 | 532 | Vehicle contact | #2 ACSR AL | POLE | 2018 | 2003
030303E7601 | Before | 4.8384 | 17.1726 | 1 | Tier 3 | 2018-03-01 | 2003-03-03 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2018 | 2003
030303E7601 | Before | 6 | 16.011 | 1 | Tier 3 | 2017-01-01 | 2003-03-03 | Customer Contact | 710 | 532 | Vehicle contact | #2 ACSR AL | POLE | 2017 | 2003
030309E5009 | Before | 3.9753 | 18.0356 | 1 | Tier 2 | 2019-01-10 | 2003-03-09 | Tree Contact | 322 | 513 | Tree fell on line | #2 5/2 AWAC AL | OH CONDUCTOR | 2019 | 2003
030309E5009 | Before | 3.9753 | 18.0356 | 1 | Tier 2 | 2019-01-10 | 2003-03-09 | Tree Contact | 322 | 513 | Tree fell on line | #2 5/2 AWAC AL | OH CONDUCTOR | 2019 | 2003
030329E7104 | Before | 7.1151 | 14.8959 | 1 | Tier 3 | 2015-11-21 | 2003-03-29 | Equipment | 532 |  | Pole broke/rotted/on fire | #2 5/2 AWAC AL | POLE | 2015 | 2003
030413E5004 | Before | 6.4658 | 15.5452 | 1 | Tier 3 | 2016-07-15 | 2003-04-13 | Equipment | 534 |  | Pothead failure | #2 5/2 AWAC AL | POTHEAD | 2016 | 2003
030414E5004 | Before | 6.4658 | 15.5452 | 1 | Tier 3 | 2016-07-15 | 2003-04-14 | Equipment | 534 |  | Pothead failure | #2 5/2 AWAC AL | POTHEAD | 2016 | 2003
030606E5006 | Before | 4 | 18.011 | 1 | Tier 3 | 2019-01-01 | 2003-06-06 | Customer Contact | 710 | 532 | Vehicle contact | #2 ACSR AL | POLE | 2019 | 2003
030729E7601 | Before | 6.8356 | 15.1753 | 1 | Tier 3 | 2016-03-02 | 2003-07-29 | Tree Contact | 322 | 214 | Tree fell on line | #2 5/2 AWAC AL | OH CONDUCTOR | 2016 | 2003
030824E5063 | Before | 4.5178 | 17.4932 | 1 | Tier 2 | 2018-06-26 | 2003-08-24 | Equipment | 534 |  | Pothead failure | #2 5/2 AWAC AL | POTHEAD | 2018 | 2003
030827E5057 | Before | 5.3726 | 16.6384 | 1 | Tier 3 | 2017-08-18 | 2003-08-27 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2017 | 2003
030827E5057 | Before | 5.1123 | 16.8986 | 1 | Tier 3 | 2017-11-21 | 2003-08-27 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2017 | 2003
030902E5072 | Before | 5.3397 | 16.6712 | 1 | Tier 3 | 2017-08-30 | 2003-09-02 | Weather | 410 |  | Lightning Arrester/Transformer failure | 336 ACSR AL | JUMPER | 2017 | 2003
030904E5033 | Before | 3.0137 | 18.9973 | 1 | Tier 3 | 2019-12-27 | 2003-09-04 | Weather | 410 | 520 | Lightning Arrester/Transformer failure | 336 ACSR AL | FUSE | 2019 | 2003
030927E5026 | Before | 8.9616 | 13.0493 | 1 | Tier 3 | 2014-01-16 | 2003-09-27 | Equipment | 518 |  | Cutout failure | #2 ACSR AL | CUTOUT | 2014 | 2003
031105E5027 | Before | 5.6521 | 16.3589 | 1 | Tier 3 | 2017-05-08 | 2003-11-05 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2017 | 2003
031114E5046 | Before | 5.6521 | 16.3589 | 1 | Tier 3 | 2017-05-08 | 2003-11-14 | Customer Contact | 702 | 510 | Heavy equp contact/digin | #2 5/2 AWAC AL | OH CONDUCTOR | 2017 | 2003
031123E7801 | Before | 7.0795 | 14.9315 | 1 | Tier 3 | 2015-12-04 | 2003-11-23 | Equipment | 554 |  | Crossarm failure | 1/0 15kV Spacer Cable AL | CROSSARM | 2015 | 2003
031127E5001 | Before | 7.6027 | 14.4082 | 1 | Tier 3 | 2015-05-27 | 2003-11-27 | Weather | 412 | 513 | Wind - wires slap/pole down | #2 5/2 AWAC AL | OH CONDUCTOR | 2015 | 2003
031127E5001 | Before | 7.6027 | 14.4082 | 1 | Tier 3 | 2015-05-27 | 2003-11-27 | Weather | 412 | 513 | Wind - wires slap/pole down | #2 5/2 AWAC AL | OH CONDUCTOR | 2015 | 2003
031205E5048 | Before | 6.789 | 15.2219 | 1 | Tier 3 | 2016-03-19 | 2003-12-05 | Equipment | 513 |  | Conductor failure/wire down | #2 5/2 AWAC AL | OH CONDUCTOR | 2016 | 2003
031225E5141 | Before | 1.6521 | 20.3589 | 1 | Tier 2 | 2021-05-07 | 2003-12-25 | Weather | 410 |  | Lightning Arrester/Transformer failure | #2 5/2 AWAC AL | LIGHTNING ARRESTER | 2021 | 2003
031226E7704 | Before | 5.6438 | 16.3671 | 1 | Tier 3 | 2017-05-11 | 2003-12-26 | Equipment | 532 |  | Pole broke/rotted/on fire | 336 ACSR AL | POLE | 2017 | 2003
040116E7701 | Before | 1.9973 | 20.0137 | 1 | Tier 2 | 2021-01-01 | 2004-01-16 | Equipment | 522 |  | Fuse overloaded/inadequate fuse size | 336.4 ACSR AL | FUSE | 2021 | 2004
040119E5005 | Before | 7.3863 | 14.6247 | 1 | Tier 3 | 2015-08-14 | 2004-01-19 | Equipment | 502 |  | Arrester (lightning) failure | #2 5/2 AWAC AL | LIGHTNING ARRESTER | 2015 | 2004
040205E7701 | Before | 5.0767 | 16.9342 | 1 | Tier 3 | 2017-12-04 | 2004-02-05 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2017 | 2004
040511E5017 | Before | 4.6301 | 17.3808 | 1 | Tier 2 | 2018-05-16 | 2004-05-11 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2018 | 2004
040704E5021 | Before | 6.7315 | 15.2795 | 1 | Tier 3 | 2016-04-09 | 2004-07-04 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2016 | 2004
040813E5042 | Before | 3.7425 | 18.2685 | 1 | Tier 2 | 2019-04-05 | 2004-08-13 | Weather | 410 | 550 | Lightning Arrester/Transformer failure | #2 5/2 AWAC AL | TRANSFORMER | 2019 | 2004
040813E7602 | Before | 7.3479 | 14.663 | 1 | Tier 3 | 2015-08-28 | 2004-08-13 | Weather | 410 | 550 | Lightning Arrester/Transformer failure | #2 5/2 AWAC AL | TRANSFORMER | 2015 | 2004
040813E7706 | Before | 7.3479 | 14.663 | 1 | Tier 3 | 2015-08-28 | 2004-08-13 | Weather | 410 | 550 | Lightning Arrester/Transformer failure | #2 5/2 AWAC AL | TRANSFORMER | 2015 | 2004
041020E5098 | Before | 3.9753 | 18.0356 | 1 | Tier 3 | 2019-01-10 | 2004-10-20 | Weather | 412 | 513 | Wind - wires slap/pole down | #2 5/2 AWAC AL | OH CONDUCTOR | 2019 | 2004
041020E5098 | Before | 3.9753 | 18.0356 | 1 | Tier 3 | 2019-01-10 | 2004-10-20 | Weather | 412 | 513 | Wind - wires slap/pole down | #2 5/2 AWAC AL | OH CONDUCTOR | 2019 | 2004
041020E7701 | Before | 3.4192 | 18.5918 | 1 | Tier 2 | 2019-08-01 | 2004-10-20 | Equipment | 504 |  | Capacitor failure | 636 ACSR AL | CAP BANK | 2019 | 2004
041020E7701 | Before | 4 | 18.011 | 1 | Tier 2 | 2019-01-01 | 2004-10-20 | Equipment | 504 |  | Capacitor failure | 636 ACSR AL | CAP BANK | 2019 | 2004
041023E7701 | Before | 7.6767 | 14.3342 | 1 | Tier 3 | 2015-04-30 | 2004-10-23 | Equipment | 515 |  | OH connector failure (jumper/splice/squeeze-on) | #2 5/2 AWAC AL | JUMPER | 2015 | 2004
041026E7602 | Before | 6.1836 | 15.8274 | 1 | Tier 3 | 2016-10-26 | 2004-10-26 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2016 | 2004
041101E5103 | Before | 6.7781 | 15.2329 | 1 | Tier 3 | 2016-03-23 | 2004-11-01 | Equipment | 554 |  | Crossarm failure | #2 5/2 AWAC AL | CROSSARM | 2016 | 2004
041121E5093 | Before | 2.1863 | 19.8247 | 1 | Tier 3 | 2020-10-24 | 2004-11-21 | Weather | 420 | 510 | Tree contact due to storm/high wind | #2 5/2 AWAC AL | OH CONDUCTOR | 2020 | 2004
041121E5111 | Before | 2.474 | 19.537 | 1 | Tier 2 | 2020-07-11 | 2004-11-21 | Weather | 412 |  | Wind - wires slap/pole down | 336 ACSR AL | OH CONDUCTOR | 2020 | 2004
041122E5035 | Before | 2.8384 | 19.1726 | 1 | Tier 3 | 2020-02-29 | 2004-11-22 | Customer Contact | 710 | 526 | Vehicle contact | #2 5/2 AWAC AL | OH CONDUCTOR | 2020 | 2004
041210E7702 | Before | 7.7315 | 14.2795 | 1 | Tier 3 | 2015-04-10 | 2004-12-10 | Equipment | 554 |  | Crossarm failure | #2 5/2 AWAC AL | CROSSARM | 2015 | 2004
041216E7701 | Before | 4.8384 | 17.1726 | 1 | Tier 3 | 2018-03-01 | 2004-12-16 | Weather | 412 | 513 | Wind - wires slap/pole down | #2 5/2 AWAC AL | OH CONDUCTOR | 2018 | 2004
041216E7701 | Before | 4.8384 | 17.1726 | 1 | Tier 3 | 2018-03-01 | 2004-12-16 | Weather | 412 | 513 | Wind - wires slap/pole down | #2 5/2 AWAC AL | OH CONDUCTOR | 2018 | 2004
041229E7505 | Before | 0.17808 | 21.8329 | 1 | Tier 2 | 2022-10-27 | 2004-12-29 | Weather | 426 | 214 | Tree fell on line due to storm/wind | #2 ACSR AL | OH CONDUCTOR | 2022 | 2004
050107E8203 | Before | 5.7096 | 16.3014 | 1 | Tier 3 | 2017-04-17 | 2005-01-07 | Customer Contact | 710 | 532 | Vehicle contact | 1/0 4/3 AWAC AL | POLE | 2017 | 2005
050107E8203 | Before | 4.5918 | 17.4192 | 1 | Tier 3 | 2018-05-30 | 2005-01-07 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2018 | 2005
050113E5056 | Before | 10.0027 | 12.0082 | 1 | Tier 2 | 2013-01-01 | 2005-01-13 | Customer Contact | 704 | 513 | Line fault/tree trimming | #2 ACSR AL | OH CONDUCTOR | 2013 | 2005
050224E5095 | Before | 4.5671 | 17.4438 | 1 | Tier 2 | 2018-06-08 | 2005-02-24 | Weather | 410 | 550 | Lightning Arrester/Transformer failure | #2 5/2 AWAC AL | TRANSFORMER | 2018 | 2005
050224E7601 | Before | 6.4658 | 15.5452 | 1 | Tier 3 | 2016-07-15 | 2005-02-24 | Weather | 410 | 518 | Lightning Arrester/Transformer failure | #2 5/2 AWAC AL | CUTOUT | 2016 | 2005
050225E5102 | Before | 4.5178 | 17.4932 | 1 | Tier 2 | 2018-06-26 | 2005-02-25 | Customer Contact | 710 | 515 | Vehicle contact | #2 5/2 AWAC AL | JUMPER | 2018 | 2005
050309E5056 | Before | 10.0027 | 12.0082 | 1 | Tier 2 | 2013-01-01 | 2005-03-09 | Equipment | 550 |  | Transformer faulted/mechanical | #2 ACSR AL | TRANSFORMER | 2013 | 2005
050319E5003 | Before | 6.789 | 15.2219 | 1 | Tier 3 | 2016-03-19 | 2005-03-19 | Equipment | 532 |  | Pole broke/rotted/on fire | 1/0 15kV Spacer Cable AL | POLE | 2016 | 2005
050328E5056 | Before | 1.5534 | 20.4575 | 1 | Tier 2 | 2021-06-12 | 2005-03-28 | Equipment | 518 |  | Cutout failure | #2 5/2 AWAC AL | SWITCH | 2021 | 2005
050328E5056 | Before | 2.6849 | 19.326 | 1 | Tier 2 | 2020-04-25 | 2005-03-28 | Equipment | 518 |  | Cutout failure | #2 5/2 AWAC AL | SWITCH | 2020 | 2005
050408E5017 | Before | 4.4384 | 17.5726 | 1 | Tier 2 | 2018-07-25 | 2005-04-08 | Customer Contact | 704 | 510 | Line fault/tree trimming | #2 5/2 AWAC AL | OH CONDUCTOR | 2018 | 2005
050422E5002 | Before | 4.6329 | 17.3781 | 1 | Tier 2 | 2018-05-15 | 2005-04-22 | Equipment | 550 |  | Transformer faulted/mechanical | #2 5/2 AWAC AL | TRANSFORMER | 2018 | 2005
050507E5001 | Before | 0.74521 | 21.2658 | 1 | Tier 3 | 2022-04-03 | 2005-05-07 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2022 | 2005
050515E5001 | Before | 5.3726 | 16.6384 | 1 | Tier 3 | 2017-08-18 | 2005-05-15 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2017 | 2005
050712E7601 | Before | 7.5315 | 14.4795 | 1 | Tier 3 | 2015-06-22 | 2005-07-12 | Equipment | 554 | 214 | Crossarm failure | #2 5/2 AWAC AL | CROSSARM | 2015 | 2005
050725E7103 | Before | 7.1288 | 14.8822 | 1 | Tier 3 | 2015-11-16 | 2005-07-25 | Equipment | 532 | 214 | Pole broke/rotted/on fire | #2 5/2 AWAC AL | POLE | 2015 | 2005
050806E5041 | Before | 4.7096 | 17.3014 | 1 | Tier 3 | 2018-04-17 | 2005-08-06 | Weather | 410 | 530 | Lightning Arrester/Transformer failure | #2 5/2 AWAC AL | INSULATOR | 2018 | 2005
050811E7109 | Before | 6.1836 | 15.8274 | 1 | Tier 3 | 2016-10-26 | 2005-08-11 | Equipment | 518 |  | Cutout failure | #2 5/2 AWAC AL | CUTOUT | 2016 | 2005
050811E7109 | Before | 5.6685 | 16.3425 | 1 | Tier 3 | 2017-05-02 | 2005-08-11 | Equipment | 518 |  | Cutout failure | #2 5/2 AWAC AL | CUTOUT | 2017 | 2005
050815E7102 | Before | 4.4438 | 17.5671 | 1 | Tier 2 | 2018-07-23 | 2005-08-15 | Weather | 410 | 550 | Lightning Arrester/Transformer failure | #2 5/2 AWAC AL | TRANSFORMER | 2018 | 2005
050824E7101 | Before | 1.9973 | 20.0137 | 1 | Tier 2 | 2021-01-01 | 2005-08-24 | Customer Contact | 710 | 554 | Vehicle contact | 4/0 B.STRD CU | CROSSARM | 2021 | 2005
050825E7601 | Before | 5.6274 | 16.3836 | 1 | Tier 3 | 2017-05-17 | 2005-08-25 | Equipment | 554 |  | Crossarm failure | #2 5/2 AWAC AL | CROSSARM | 2017 | 2005
050829E5002 | Before | 6.7315 | 15.2795 | 1 | Tier 3 | 2016-04-09 | 2005-08-29 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2016 | 2005
050907E5020 | Before | 1.0164 | 20.9945 | 1 | Tier 2 | 2021-12-25 | 2005-09-07 | Customer Contact | 710 | 532 | Vehicle contact | #2 3/4 AWAC AL | POLE | 2021 | 2005
050919E7104 | Before | 2.6466 | 19.3644 | 1 | Tier 2 | 2020-05-09 | 2005-09-19 | Equipment | 540 |  | Regulator faulted/mechanical | #2 5/2 AWAC AL | REGULATOR | 2020 | 2005
050920E5155 | Before | 3.7425 | 18.2685 | 1 | Tier 2 | 2019-04-05 | 2005-09-20 | Weather | 410 | 550 | Lightning Arrester/Transformer failure | #2 5/2 AWAC AL | TRANSFORMER | 2019 | 2005
050920E7605 | Before | 6.2219 | 15.789 | 1 | Tier 3 | 2016-10-12 | 2005-09-20 | Weather | 404 | 518 | Circ. Flashover/storm/high winds/undet. | #2 5/2 AWAC AL | CUTOUT | 2016 | 2005
050920E7605 | Before | 7.3397 | 14.6712 | 1 | Tier 3 | 2015-08-31 | 2005-09-20 | Weather | 404 | 518 | Circ. Flashover/storm/high winds/undet. | #2 5/2 AWAC AL | CUTOUT | 2015 | 2005
050923E5020 | Before | 7.4521 | 14.5589 | 1 | Tier 3 | 2015-07-21 | 2005-09-23 | Equipment | 550 |  | Transformer faulted/mechanical | #2 5/2 AWAC AL | TRANSFORMER | 2015 | 2005
050926E7102 | Before | 3.7425 | 18.2685 | 1 | Tier 2 | 2019-04-05 | 2005-09-26 | Equipment | 550 |  | Transformer faulted/mechanical | #2 5/2 AWAC AL | TRANSFORMER | 2019 | 2005
051007E7101 | Before | 7.789 | 14.2219 | 1 | Tier 2 | 2015-03-20 | 2005-10-07 | Customer Contact | 710 | 214 | Vehicle contact | #2 ACSR AL | POLE | 2015 | 2005
051011E5027 | Before | 2.2247 | 19.7863 | 1 | Tier 3 | 2020-10-10 | 2005-10-11 | Foreign Object | 308 | 513 | Bird contact | #2 5/2 AWAC AL | OH CONDUCTOR | 2020 | 2005
051011E5027 | Before | 2.2247 | 19.7863 | 1 | Tier 3 | 2020-10-10 | 2005-10-11 | Foreign Object | 308 | 513 | Bird contact | #2 5/2 AWAC AL | OH CONDUCTOR | 2020 | 2005
051019E5020 | Before | 1.5589 | 20.4521 | 1 | Tier 2 | 2021-06-10 | 2005-10-19 | Equipment | 550 |  | Transformer faulted/mechanical | 336 ACSR AL | TRANSFORMER | 2021 | 2005
051106E7103 | Before | 5.6027 | 16.4082 | 1 | Tier 3 | 2017-05-26 | 2005-11-06 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2017 | 2005
051110E7602 | Before | 6.1836 | 15.8274 | 1 | Tier 3 | 2016-10-26 | 2005-11-10 | Equipment | 518 |  | Cutout failure | #2 5/2 AWAC AL | CUTOUT | 2016 | 2005
051110E7602 | Before | 5.6685 | 16.3425 | 1 | Tier 3 | 2017-05-02 | 2005-11-10 | Equipment | 518 |  | Cutout failure | #2 5/2 AWAC AL | CUTOUT | 2017 | 2005
051113E7101 | Before | 7.4356 | 14.5753 | 1 | Tier 3 | 2015-07-27 | 2005-11-13 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2015 | 2005
060103E5007 | Before | 2.2822 | 19.7288 | 1 | Tier 3 | 2020-09-19 | 2006-01-03 | Foreign Object | 308 | 510 | Bird contact | 336 ACSR AL | OH CONDUCTOR | 2020 | 2006
060103E5007 | Before | 2.2822 | 19.7288 | 1 | Tier 3 | 2020-09-19 | 2006-01-03 | Foreign Object | 308 | 510 | Bird contact | 336 ACSR AL | OH CONDUCTOR | 2020 | 2006
060115E5023 | Before | 5.3753 | 16.6356 | 1 | Tier 2 | 2017-08-17 | 2006-01-15 | Weather | 426 | 513 | Tree fell on line due to storm/wind | #2 5/2 AWAC AL | OH CONDUCTOR | 2017 | 2006
060126E7601 | Before | 7.4329 | 14.5781 | 1 | Tier 3 | 2015-07-28 | 2006-01-26 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2015 | 2006
060208E5062 | Before | 4 | 18.011 | 1 | Tier 3 | 2019-01-01 | 2006-02-08 | Customer Contact | 710 | 532 | Vehicle contact | 3/0 ACSR AL | POLE | 2019 | 2006
060302E5012 | Before | 2.6466 | 19.3644 | 1 | Tier 2 | 2020-05-09 | 2006-03-02 | Equipment | 536 |  | Recloser/breaker faulted/mechanical | #2 5/2 AWAC AL | SERVICE RESTORER | 2020 | 2006
060310E5015 | Before | 0.74521 | 21.2658 | 1 | Tier 3 | 2022-04-03 | 2006-03-10 | Weather | 408 | 513 | Ice or snow/Equipment failure | #2 5/2 AWAC AL | OH CONDUCTOR | 2022 | 2006
060311E5057 | Before | 9.8603 | 12.1507 | 1 | Tier 2 | 2013-02-22 | 2006-03-11 | Weather | 412 |  | Wind - wires slap/pole down | 336.4 ACSR AL | OH CONDUCTOR | 2013 | 2006
060311E5102 | Before | 6.2055 | 15.8055 | 1 | Tier 3 | 2016-10-18 | 2006-03-11 | Weather | 412 |  | Wind - wires slap/pole down | 336 ACSR AL | OH CONDUCTOR | 2016 | 2006
060311E7119 | Before | 7.0329 | 14.9781 | 1 | Tier 2 | 2015-12-21 | 2006-03-11 | Weather | 410 | 412 | Lightning Arrester/Transformer failure | #2 5/2 AWAC AL | OH CONDUCTOR | 2015 | 2006
060312E7102 | Before | 6.0438 | 15.9671 | 1 | Tier 3 | 2016-12-16 | 2006-03-12 | Weather | 412 |  | Wind - wires slap/pole down | #2 5/2 AWAC AL | OH CONDUCTOR | 2016 | 2006
060316E7601 | Before | 9.1589 | 12.8521 | 1 | Tier 2 | 2013-11-05 | 2006-03-16 | Equipment | 513 |  | Conductor failure/wire down | 636 ACSR AL | OH CONDUCTOR | 2013 | 2006
060329E7601 | Before | 6.8712 | 15.1397 | 1 | Tier 2 | 2016-02-18 | 2006-03-29 | Equipment | 508 | 214 | Flashover/equip contam/overload | 636 ACSR AL | CAP BANK | 2016 | 2006
060405E5002 | Before | 9.0767 | 12.9342 | 1 | Tier 2 | 2013-12-05 | 2006-04-05 | Weather | 412 |  | Wind - wires slap/pole down | #2 ACSR AL | OH CONDUCTOR | 2013 | 2006
060406E7602 | Before | 9.8438 | 12.1671 | 1 | Tier 2 | 2013-02-28 | 2006-04-06 | Equipment | 540 | 214 | Regulator faulted/mechanical | 3/0 ACSR AL | REGULATOR | 2013 | 2006
060406E7602 | Before | 9.8438 | 12.1671 | 1 | Tier 2 | 2013-02-28 | 2006-04-06 | Equipment | 540 | 214 | Regulator faulted/mechanical | 336.4 ACSR AL | REGULATOR | 2013 | 2006
060421E5038 | Before | 7.6767 | 14.3342 | 1 | Tier 3 | 2015-04-30 | 2006-04-21 | Equipment | 554 |  | Crossarm failure | #2 5/2 AWAC AL | CROSSARM | 2015 | 2006
060715E5011 | Before | 4.4384 | 17.5726 | 1 | Tier 2 | 2018-07-25 | 2006-07-15 | Equipment | 520 |  | Fuse holder/fuse cabinet failed | 336 ACSR AL | FUSE | 2018 | 2006
060823E5010 | Before | 8.0027 | 14.0082 | 1 | Tier 3 | 2015-01-01 | 2006-08-23 | Equipment | 515 | 513 | OH connector failure (jumper/splice/squeeze-on) | #2 ACSR AL | CONNECTOR | 2015 | 2006
060903E7801 | Before | 6.6137 | 15.3973 | 1 | Tier 3 | 2016-05-22 | 2006-09-03 | Weather | 410 |  | Lightning Arrester/Transformer failure | #2 5/2 AWAC AL | LIGHTNING ARRESTER | 2016 | 2006
060905E5038 | Before | 8.0301 | 13.9808 | 1 | Tier 2 | 2014-12-22 | 2006-09-05 | Equipment | 515 |  | OH connector failure (jumper/splice/squeeze-on) | #2 5/2 AWAC AL | JUMPER | 2014 | 2006
060908E5007 | Before | 3.6274 | 18.3836 | 1 | Tier 2 | 2019-05-17 | 2006-09-08 | Equipment | 536 |  | Recloser/breaker faulted/mechanical | #2 5/2 AWAC AL | SERVICE RESTORER | 2019 | 2006
060908E5007 | Before | 2.3397 | 19.6712 | 1 | Tier 2 | 2020-08-29 | 2006-09-08 | Equipment | 536 |  | Recloser/breaker faulted/mechanical | #2 5/2 AWAC AL | SERVICE RESTORER | 2020 | 2006
061010E5034 | Before | 3.6274 | 18.3836 | 1 | Tier 2 | 2019-05-17 | 2006-10-10 | Equipment | 536 |  | Recloser/breaker faulted/mechanical | #2 5/2 AWAC AL | SERVICE RESTORER | 2019 | 2006
061010E5034 | Before | 2.3397 | 19.6712 | 1 | Tier 2 | 2020-08-29 | 2006-10-10 | Equipment | 536 |  | Recloser/breaker faulted/mechanical | #2 5/2 AWAC AL | SERVICE RESTORER | 2020 | 2006
061025E7802 | Before | 6.4658 | 15.5452 | 1 | Tier 3 | 2016-07-15 | 2006-10-25 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2016 | 2006
061031E7703 | Before | 5.2274 | 16.7836 | 1 | Tier 3 | 2017-10-10 | 2006-10-31 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2017 | 2006
061209E5056 | Before | 8.0027 | 14.0082 | 1 | Tier 2 | 2015-01-01 | 2006-12-09 | Equipment | 518 | 504 | Cutout failure | 2/0 B.STRD CU | CUTOUT | 2015 | 2006
061225E5013 | Before | 4.4384 | 17.5726 | 1 | Tier 2 | 2018-07-25 | 2006-12-25 | Foreign Object | 310 | 513 | Damage by gunshot | 336 ACSR AL | OH CONDUCTOR | 2018 | 2006
061225E5013 | Before | 4.4384 | 17.5726 | 1 | Tier 2 | 2018-07-25 | 2006-12-25 | Foreign Object | 310 | 513 | Damage by gunshot | 336 ACSR AL | OH CONDUCTOR | 2018 | 2006
061227E5022 | Before | 5.2274 | 16.7836 | 1 | Tier 3 | 2017-10-10 | 2006-12-27 | Customer Contact | 710 | 526 | Vehicle contact | #2 5/2 AWAC AL | GUY WIRE | 2017 | 2006
061227E5112 | Before | 1.8904 | 20.1205 | 1 | Tier 3 | 2021-02-09 | 2006-12-27 | Weather | 426 |  | Tree fell on line due to storm/wind | #2 5/2 AWAC AL | OH CONDUCTOR | 2021 | 2006
070108E7801 | Before | 3.3233 | 18.6877 | 1 | Tier 3 | 2019-09-05 | 2007-01-08 | Equipment | 550 |  | Transformer faulted/mechanical | #2 5/2 AWAC AL | TRANSFORMER | 2019 | 2007
070111E7601 | Before | 8.3699 | 13.6411 | 1 | Tier 3 | 2014-08-20 | 2007-01-12 | Equipment | 530 | 532 | Insulator/pin failure/wire floating | #2 5/2 AWAC AL | INSULATOR | 2014 | 2007
070112E5012 | Before | 8.8356 | 13.1753 | 1 | Tier 3 | 2014-03-03 | 2007-01-12 | Weather | 412 | 513 | Wind - wires slap/pole down | #2 5/2 AWAC AL | OH CONDUCTOR | 2014 | 2007
070112E5012 | Before | 8.8356 | 13.1753 | 1 | Tier 3 | 2014-03-03 | 2007-01-12 | Weather | 412 | 513 | Wind - wires slap/pole down | #2 5/2 AWAC AL | OH CONDUCTOR | 2014 | 2007
070125E5001 | Before | 5.8932 | 16.1178 | 1 | Tier 3 | 2017-02-09 | 2007-01-25 | Equipment | 520 |  | Fuse holder/fuse cabinet failed | #2 5/2 AWAC AL | FUSE | 2017 | 2007
070207E7801 | Before | 4.3342 | 17.6767 | 1 | Tier 3 | 2018-09-01 | 2007-02-07 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2018 | 2007
070207E7801 | Before | 4.4356 | 17.5753 | 1 | Tier 3 | 2018-07-26 | 2007-02-07 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2018 | 2007
070213E5055 | Before | 2.8384 | 19.1726 | 1 | Tier 3 | 2020-02-29 | 2007-02-13 | Customer Contact | 710 | 526 | Vehicle contact | #2 5/2 AWAC AL | GUY WIRE | 2020 | 2007
070224E7302 | Before | 4.6301 | 17.3808 | 1 | Tier 3 | 2018-05-16 | 2007-02-24 | Equipment | 550 | 214 | Transformer faulted/mechanical | #2 5/2 AWAC AL | TRANSFORMER | 2018 | 2007
070313E7802 | Before | 7.6767 | 14.3342 | 1 | Tier 3 | 2015-04-30 | 2007-03-13 | Equipment | 554 | 214 | Crossarm failure | #2 5/2 AWAC AL | CROSSARM | 2015 | 2007
070322E7702 | Before | 5.7041 | 16.3068 | 1 | Tier 3 | 2017-04-19 | 2007-03-22 | Weather | 410 | 550 | Lightning Arrester/Transformer failure | #2 5/2 AWAC AL | TRANSFORMER | 2017 | 2007
070329E5034 | Before | 1.5726 | 20.4384 | 1 | Tier 3 | 2021-06-05 | 2007-03-29 | Equipment | 502 |  | Arrester (lightning) failure | 336 ACSR AL | LIGHTNING ARRESTER | 2021 | 2007
070329E5034 | Before | 1.5726 | 20.4384 | 1 | Tier 3 | 2021-06-05 | 2007-03-29 | Equipment | 502 |  | Arrester (lightning) failure | 336.4 ACSR AL | LIGHTNING ARRESTER | 2021 | 2007
070424E5054 | Before | 5.6521 | 16.3589 | 1 | Tier 3 | 2017-05-08 | 2007-04-24 | Equipment | 550 |  | Transformer faulted/mechanical | #2 5/2 AWAC AL | TRANSFORMER | 2017 | 2007
070516E7801 | Before | 7.4329 | 14.5781 | 1 | Tier 3 | 2015-07-28 | 2007-05-16 | Equipment | 554 | 214 | Crossarm failure | #2 5/2 AWAC AL | CROSSARM | 2015 | 2007
070518E5048 | Before | 3.4192 | 18.5918 | 1 | Tier 2 | 2019-08-01 | 2007-05-18 | Equipment | 515 |  | OH connector failure (jumper/splice/squeeze-on) | #2 5/2 AWAC AL | CONNECTOR | 2019 | 2007
070702E5041 | Before | 8.6247 | 13.3863 | 1 | Tier 2 | 2014-05-19 | 2007-07-02 | Customer Contact | 710 | 526 | Vehicle contact | #2 ACSR AL | GUY WIRE | 2014 | 2007
070702E5041 | Before | 9.0027 | 13.0082 | 1 | Tier 2 | 2014-01-01 | 2007-07-02 | Customer Contact | 710 | 526 | Vehicle contact | #2 ACSR AL | GUY WIRE | 2014 | 2007
070702E7701 | Before | 3.0795 | 18.9315 | 1 | Tier 3 | 2019-12-03 | 2007-07-02 | Equipment | 550 |  | Transformer faulted/mechanical | #2 ACSR AL | TRANSFORMER | 2019 | 2007
070729E5015 | Before | 3.0356 | 18.9753 | 1 | Tier 3 | 2019-12-19 | 2007-07-29 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2019 | 2007
070809E7802 | Before | 0.74521 | 21.2658 | 1 | Tier 3 | 2022-04-03 | 2007-08-09 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2022 | 2007
070816E7701 | Before | 3.9342 | 18.0767 | 1 | Tier 2 | 2019-01-25 | 2007-08-16 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2019 | 2007
070822E5063 | Before | 1.074 | 20.937 | 1 | Tier 3 | 2021-12-04 | 2007-08-22 | Customer Contact | 704 | 513 | Line fault/tree trimming | 636 ACSR AL | OH CONDUCTOR | 2021 | 2007
070901E5077 | Before | 3.0137 | 18.9973 | 1 | Tier 3 | 2019-12-27 | 2007-09-01 | Equipment | 522 |  | Fuse overloaded/inadequate fuse size | 336 ACSR AL | FUSE | 2019 | 2007
070901E5099 | Before | 4.5671 | 17.4438 | 1 | Tier 2 | 2018-06-08 | 2007-09-01 | Equipment | 522 |  | Fuse overloaded/inadequate fuse size | 336 ACSR AL | FUSE | 2018 | 2007
070902E5012 | Before | 4 | 18.011 | 1 | Tier 2 | 2019-01-01 | 2007-09-02 | Customer Contact | 710 | 532 | Vehicle contact | #2 ACSR AL | POLE | 2019 | 2007
070902E5150 | Before | 6.7315 | 15.2795 | 1 | Tier 3 | 2016-04-09 | 2007-09-02 | Tree Contact | 322 | 513 | Tree fell on line | #2 5/2 AWAC AL | OH CONDUCTOR | 2016 | 2007
070902E5150 | Before | 6.7315 | 15.2795 | 1 | Tier 3 | 2016-04-09 | 2007-09-02 | Tree Contact | 322 | 513 | Tree fell on line | #2 5/2 AWAC AL | OH CONDUCTOR | 2016 | 2007
070911E5020 | Before | 3.0356 | 18.9753 | 1 | Tier 3 | 2019-12-19 | 2007-09-11 | Equipment | 518 |  | Cutout failure | 336 ACSR AL | CUTOUT | 2019 | 2007
071022E5009 | Before | 6.4521 | 15.5589 | 1 | Tier 3 | 2016-07-20 | 2007-10-22 | Weather | 404 | 532 | Circ. Flashover/storm/high winds/undet. | #2 5/2 AWAC AL | POLE | 2016 | 2007
071022E5018 | Before | 7.5096 | 14.5014 | 1 | Tier 3 | 2015-06-30 | 2007-10-22 | Miscellaneous | 206 | 513 | Fire | #2 5/2 AWAC AL | OH CONDUCTOR | 2015 | 2007
071022E7803 | Before | 7.6027 | 14.4082 | 1 | Tier 3 | 2015-05-27 | 2007-10-22 | Weather | 404 | 513 | Circ. Flashover/storm/high winds/undet. | #2 5/2 AWAC AL | OH CONDUCTOR | 2015 | 2007
071105E5010 | Before | 6.4521 | 15.5589 | 1 | Tier 3 | 2016-07-20 | 2007-11-05 | Equipment | 504 |  | Capacitor failure | #2 5/2 AWAC AL | CAP BANK | 2016 | 2007
071123E5001 | Before | 5.2274 | 16.7836 | 1 | Tier 3 | 2017-10-10 | 2007-11-23 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2017 | 2007
071130E5007 | Before | 2.1096 | 19.9014 | 1 | Tier 2 | 2020-11-21 | 2007-11-30 | Equipment | 554 |  | Crossarm failure | #2 5/2 AWAC AL | CROSSARM | 2020 | 2007
071231E7701 | Before | 7.4329 | 14.5781 | 1 | Tier 3 | 2015-07-28 | 2007-12-31 | Weather | 412 |  | Wind - wires slap/pole down | #2 5/2 AWAC AL | OH CONDUCTOR | 2015 | 2007
080208E5003 | Before | 4 | 18.011 | 1 | Tier 3 | 2019-01-01 | 2008-02-08 | Customer Contact | 710 | 526 | Vehicle contact | #2 ACSR AL | GUY WIRE | 2019 | 2008
080212E7701 | Before | 0.74521 | 21.2658 | 1 | Tier 3 | 2022-04-03 | 2008-02-12 | Customer Contact | 710 | 532 | Vehicle contact | #2 3/4 AWAC AL | POLE | 2022 | 2008
080212E7702 | Before | 0.74521 | 21.2658 | 1 | Tier 3 | 2022-04-03 | 2008-02-12 | Customer Contact | 710 | 532 | Vehicle contact | #2 3/4 AWAC AL | POLE | 2022 | 2008
080220E7701 | Before | 3.3014 | 18.7096 | 1 | Tier 2 | 2019-09-13 | 2008-02-20 | Equipment | 550 | 214 | Transformer faulted/mechanical | #2 5/2 AWAC AL | TRANSFORMER | 2019 | 2008
080303E5023 | Before | 8.9616 | 13.0493 | 1 | Tier 3 | 2014-01-16 | 2008-03-03 | Weather | 412 | 513 | Wind - wires slap/pole down | #2 ACSR AL | OH CONDUCTOR | 2014 | 2008
080303E5023 | Before | 8.9616 | 13.0493 | 1 | Tier 3 | 2014-01-16 | 2008-03-03 | Weather | 412 | 513 | Wind - wires slap/pole down | #2 ACSR AL | OH CONDUCTOR | 2014 | 2008
080306E7701 | Before | 6 | 16.011 | 1 | Tier 3 | 2017-01-01 | 2008-03-06 | Equipment | 550 |  | Transformer faulted/mechanical | #2 ACSR AL | TRANSFORMER | 2017 | 2008
080512E7501 | Before | 9.0027 | 13.0082 | 1 | Tier 3 | 2014-01-01 | 2008-05-12 | Equipment | 504 |  | Capacitor failure | #2 5/2 AWAC AL | CAP BANK | 2014 | 2008
080512E7501 | Before | 4 | 18.011 | 1 | Tier 3 | 2019-01-01 | 2008-05-12 | Equipment | 504 |  | Capacitor failure | #2 5/2 AWAC AL | CAP BANK | 2019 | 2008
080522E7801 | Before | 4.8384 | 17.1726 | 1 | Tier 3 | 2018-03-01 | 2008-05-22 | Weather | 410 | 534 | Lightning Arrester/Transformer failure | #2 5/2 AWAC AL | POTHEAD | 2018 | 2008
080622E5002 | Before | 3.9753 | 18.0356 | 1 | Tier 2 | 2019-01-10 | 2008-06-22 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2019 | 2008
080709E7602 | Before | 1.0164 | 20.9945 | 1 | Tier 2 | 2021-12-25 | 2008-07-09 | Equipment | 515 |  | OH connector failure (jumper/splice/squeeze-on) | #2 3/4 AWAC AL | JUMPER | 2021 | 2008
080807E7701 | Before | 7.589 | 14.4219 | 1 | Tier 3 | 2015-06-01 | 2008-08-07 | Equipment | 550 |  | Transformer faulted/mechanical | #2 5/2 AWAC AL | TRANSFORMER | 2015 | 2008
080825E7701 | Before | 1.9753 | 20.0356 | 1 | Tier 3 | 2021-01-09 | 2008-08-25 | Equipment | 542 | 214 | Regulator overloaded/electrical | 336 ACSR AL | REGULATOR | 2021 | 2008
080904E7601 | Before | 5.0767 | 16.9342 | 1 | Tier 3 | 2017-12-04 | 2008-09-04 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2017 | 2008
080912E7701 | Before | 4.5918 | 17.4192 | 1 | Tier 3 | 2018-05-30 | 2008-09-12 | Equipment | 554 |  | Crossarm failure | #2 5/2 AWAC AL | CROSSARM | 2018 | 2008
080912E7701 | Before | 4.5918 | 17.4192 | 1 | Tier 3 | 2018-05-30 | 2008-09-12 | Equipment | 554 |  | Crossarm failure | #2 5/2 AWAC AL | CROSSARM | 2018 | 2008
080917E7802 | Before | 4.7425 | 17.2685 | 1 | Tier 3 | 2018-04-05 | 2008-09-17 | Equipment | 530 | 554 | Insulator/pin failure/wire floating | #2 5/2 AWAC AL | CROSSARM | 2018 | 2008
080918E5032 | Before | 9.0027 | 13.0082 | 1 | Tier 2 | 2014-01-01 | 2008-09-18 | Foreign Object | 315 | 510 | Balloon contact | 3/0 ACSR AL | OH CONDUCTOR | 2014 | 2008
080920E7601 | Before | 7.3863 | 14.6247 | 1 | Tier 3 | 2015-08-14 | 2008-09-19 | Tree Contact | 322 | 513 | Tree fell on line | #2 5/2 AWAC AL | OH CONDUCTOR | 2015 | 2008
080920E7601 | Before | 7.3863 | 14.6247 | 1 | Tier 3 | 2015-08-14 | 2008-09-19 | Tree Contact | 322 | 513 | Tree fell on line | #2 5/2 AWAC AL | OH CONDUCTOR | 2015 | 2008
080921E7603 | Before | 8.4137 | 13.5973 | 1 | Tier 3 | 2014-08-04 | 2008-09-21 | Foreign Object | 308 | 513 | Bird contact | #2 5/2 AWAC AL | OH CONDUCTOR | 2014 | 2008
080921E7603 | Before | 8.4137 | 13.5973 | 1 | Tier 3 | 2014-08-04 | 2008-09-21 | Foreign Object | 308 | 513 | Bird contact | #2 5/2 AWAC AL | OH CONDUCTOR | 2014 | 2008
081006E5029 | Before | 7.3918 | 14.6192 | 1 | Tier 3 | 2015-08-12 | 2008-10-06 | Crew Contact | 626 | 550 | SDG&E Contr. Line fault/tree trimming | #2 5/2 AWAC AL | TRANSFORMER | 2015 | 2008
081104E7701 | Before | 5.1123 | 16.8986 | 1 | Tier 3 | 2017-11-21 | 2008-11-04 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2017 | 2008
081121E5014 | Before | 3.9753 | 18.0356 | 1 | Tier 2 | 2019-01-10 | 2008-11-21 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2019 | 2008
081130E5004 | Before | 1.5534 | 20.4575 | 1 | Tier 2 | 2021-06-12 | 2008-11-30 | Equipment | 550 |  | Transformer faulted/mechanical | #2 5/2 AWAC AL | TRANSFORMER | 2021 | 2008
081210E5071 | Before | 7.6767 | 14.3342 | 1 | Tier 3 | 2015-04-30 | 2008-12-10 | Equipment | 518 |  | Cutout failure | #2 5/2 AWAC AL | CUTOUT | 2015 | 2008
081217E5054 | Before | 8.8356 | 13.1753 | 1 | Tier 3 | 2014-03-03 | 2008-12-17 | Weather | 412 |  | Wind - wires slap/pole down | #2 5/2 AWAC AL | OH CONDUCTOR | 2014 | 2008
081217E7701 | Before | 5.4164 | 16.5945 | 1 | Tier 3 | 2017-08-02 | 2008-12-17 | Weather | 426 | 513 | Tree fell on line due to storm/wind | #2 5/2 AWAC AL | OH CONDUCTOR | 2017 | 2008
090110E5050 | Before | 7.1151 | 14.8959 | 1 | Tier 3 | 2015-11-21 | 2009-01-10 | Weather | 412 | 513 | Wind - wires slap/pole down | #2 5/2 AWAC AL | OH CONDUCTOR | 2015 | 2009
090110E5050 | Before | 7.1151 | 14.8959 | 1 | Tier 3 | 2015-11-21 | 2009-01-10 | Weather | 412 | 513 | Wind - wires slap/pole down | #2 5/2 AWAC AL | OH CONDUCTOR | 2015 | 2009
090110E7601 | Before | 7.4658 | 14.5452 | 1 | Tier 3 | 2015-07-16 | 2009-01-10 | Equipment | 530 | 510 | Insulator/pin failure/wire floating | #2 5/2 AWAC AL | OH CONDUCTOR | 2015 | 2009
090211E7802 | Before | 4.3644 | 17.6466 | 1 | Tier 2 | 2018-08-21 | 2009-02-11 | Equipment | 502 | 214 | Arrester (lightning) failure | #2 5/2 AWAC AL | LIGHTNING ARRESTER | 2018 | 2009
090316E5020 | Before | 3 | 19.011 | 1 | Tier 2 | 2020-01-01 | 2009-03-16 | Equipment | 515 |  | OH connector failure (jumper/splice/squeeze-on) | 636 ACSR AL | JUMPER | 2020 | 2009
090416E5035 | Before | 3.1753 | 18.8356 | 1 | Tier 2 | 2019-10-29 | 2009-04-16 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2019 | 2009
090416E5035 | Before | 3.1753 | 18.8356 | 1 | Tier 2 | 2019-10-29 | 2009-04-16 | Customer Contact | 710 | 532 | Vehicle contact | 336 ACSR AL | POLE | 2019 | 2009
090519E5051 | Before | 2.6849 | 19.326 | 1 | Tier 2 | 2020-04-25 | 2009-05-19 | Equipment | 515 | 513 | OH connector failure (jumper/splice/squeeze-on) | #2 5/2 AWAC AL | JUMPER | 2020 | 2009
090525E5001 | Before | 6.7342 | 15.2767 | 1 | Tier 3 | 2016-04-08 | 2009-05-25 | Foreign Object | 308 | 513 | Bird contact | #2 5/2 AWAC AL | OH CONDUCTOR | 2016 | 2009
090525E5001 | Before | 6.7342 | 15.2767 | 1 | Tier 3 | 2016-04-08 | 2009-05-25 | Foreign Object | 308 | 513 | Bird contact | #2 5/2 AWAC AL | OH CONDUCTOR | 2016 | 2009
090529E7801 | Before | 5.1123 | 16.8986 | 1 | Tier 3 | 2017-11-21 | 2009-05-29 | Customer Contact | 710 | 513 | Vehicle contact | #2 5/2 AWAC AL | OH CONDUCTOR | 2017 | 2009
090602E5034 | Before | 7.7918 | 14.2192 | 1 | Tier 3 | 2015-03-19 | 2009-06-02 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2015 | 2009
090625E5004 | Before | 4.5671 | 17.4438 | 1 | Tier 2 | 2018-06-08 | 2009-06-25 | Equipment | 515 |  | OH connector failure (jumper/splice/squeeze-on) | #2 5/2 AWAC AL | JUMPER | 2018 | 2009
090625E5004 | Before | 4.5671 | 17.4438 | 1 | Tier 2 | 2018-06-08 | 2009-06-25 | Equipment | 515 |  | OH connector failure (jumper/splice/squeeze-on) | 336 ACSR AL | JUMPER | 2018 | 2009
090626E5083 | Before | 3.3041 | 18.7068 | 1 | Tier 2 | 2019-09-12 | 2009-06-26 | Customer Contact | 704 | 513 | Line fault/tree trimming | #2 3/4 AWAC AL | OH CONDUCTOR | 2019 | 2009
090827E7602 | Before | 8.3123 | 13.6986 | 1 | Tier 3 | 2014-09-10 | 2009-08-27 | Equipment | 516 | 550 | Connector/jumper/splice/elbow/rack | #2 ACSR AL | BUSHING | 2014 | 2009
090830E7603 | Before | 4 | 18.011 | 1 | Tier 3 | 2019-01-01 | 2009-08-30 | Customer Contact | 710 | 532 | Vehicle contact | #2 ACSR AL | POLE | 2019 | 2009
090906E7801 | Before | 5.2384 | 16.7726 | 1 | Tier 3 | 2017-10-06 | 2009-09-06 | Equipment | 513 |  | Conductor failure/wire down | #2 5/2 AWAC AL | OH CONDUCTOR | 2017 | 2009
091019E7702 | Before | 5.7041 | 16.3068 | 1 | Tier 2 | 2017-04-19 | 2009-10-19 | Crew Contact | 632 | 515 | SDG&E Contr. Crew error | #2 5/2 AWAC AL | JUMPER | 2017 | 2009
091019E7702 | Before | 5.7041 | 16.3068 | 1 | Tier 3 | 2017-04-19 | 2009-10-19 | Crew Contact | 632 | 515 | SDG&E Contr. Crew error | #2 5/2 AWAC AL | JUMPER | 2017 | 2009
091021E5068 | Before | 5.2274 | 16.7836 | 1 | Tier 3 | 2017-10-10 | 2009-10-21 | Customer Contact | 710 | 520 | Vehicle contact | #2 5/2 AWAC AL | FUSE | 2017 | 2009
091029E5131 | Before | 2.8384 | 19.1726 | 1 | Tier 3 | 2020-02-29 | 2009-10-29 | Customer Contact | 710 | 526 | Vehicle contact | #2 5/2 AWAC AL | GUY WIRE | 2020 | 2009
091113E7601 | Before | 1.8027 | 20.2082 | 1 | Tier 3 | 2021-03-13 | 2009-11-13 | Equipment | 532 | 206 | Pole broke/rotted/on fire | #2 5/2 AWAC AL | POLE | 2021 | 2009
091113E7601 | Before | 6.5068 | 15.5041 | 1 | Tier 3 | 2016-06-30 | 2009-11-13 | Equipment | 532 | 206 | Pole broke/rotted/on fire | #2 5/2 AWAC AL | POLE | 2016 | 2009
091113E7601 | Before | 6 | 16.011 | 1 | Tier 3 | 2017-01-01 | 2009-11-13 | Equipment | 532 | 206 | Pole broke/rotted/on fire | #2 ACSR AL | POLE | 2017 | 2009
091207E5580 | Before | 2.474 | 19.537 | 1 | Tier 2 | 2020-07-11 | 2009-12-07 | Weather | 412 | 513 | Wind - wires slap/pole down | 336 ACSR AL | OH CONDUCTOR | 2020 | 2009
091207E5580 | Before | 2.474 | 19.537 | 1 | Tier 2 | 2020-07-11 | 2009-12-07 | Weather | 412 | 513 | Wind - wires slap/pole down | 336 ACSR AL | OH CONDUCTOR | 2020 | 2009
091207E7806 | Before | 7.6603 | 14.3507 | 1 | Tier 2 | 2015-05-06 | 2009-12-07 | Weather | 412 | 510 | Wind - wires slap/pole down | 336.4 ACSR AL | OH CONDUCTOR | 2015 | 2009
091207E7806 | Before | 7.6603 | 14.3507 | 1 | Tier 2 | 2015-05-06 | 2009-12-07 | Weather | 412 | 510 | Wind - wires slap/pole down | 336.4 ACSR AL | OH CONDUCTOR | 2015 | 2009
091209E7802 | Before | 7.6603 | 14.3507 | 1 | Tier 2 | 2015-05-06 | 2009-12-09 | Weather | 412 | 510 | Wind - wires slap/pole down | 336.4 ACSR AL | OH CONDUCTOR | 2015 | 2009
091209E7802 | Before | 7.6603 | 14.3507 | 1 | Tier 2 | 2015-05-06 | 2009-12-09 | Weather | 412 | 510 | Wind - wires slap/pole down | 336.4 ACSR AL | OH CONDUCTOR | 2015 | 2009
091227E7601 | Before | 7.7836 | 14.2274 | 1 | Tier 2 | 2015-03-22 | 2009-12-27 | Equipment | 513 |  | Conductor failure/wire down | #2 5/2 AWAC AL | OH CONDUCTOR | 2015 | 2009
100119E7502 | Before | 5.4164 | 16.5945 | 1 | Tier 3 | 2017-08-02 | 2010-01-19 | Weather | 404 | 518 | Circ. Flashover/storm/high winds/undet. | #2 5/2 AWAC AL | CUTOUT | 2017 | 2010
100119E7502 | Before | 7.1562 | 14.8548 | 1 | Tier 3 | 2015-11-06 | 2010-01-19 | Weather | 404 | 518 | Circ. Flashover/storm/high winds/undet. | #2 5/2 AWAC AL | CUTOUT | 2015 | 2010
100119E9901 | Before | 1.0082 | 21.0027 | 1 | Tier 3 | 2021-12-28 | 2010-01-19 | Equipment | 518 |  | Cutout failure | #2 5/2 AWAC AL | CUTOUT | 2021 | 2010
100121E5283 | Before | 5.4164 | 16.5945 | 1 | Tier 3 | 2017-08-02 | 2010-01-21 | Weather | 408 | 518 | Ice or snow/Equipment failure | #2 5/2 AWAC AL | CUTOUT | 2017 | 2010
100121E5283 | Before | 7.1562 | 14.8548 | 1 | Tier 3 | 2015-11-06 | 2010-01-21 | Weather | 408 | 518 | Ice or snow/Equipment failure | #2 5/2 AWAC AL | CUTOUT | 2015 | 2010
100121E7505 | Before | 4 | 18.011 | 1 | Tier 2 | 2019-01-01 | 2010-01-21 | Equipment | 520 |  | Fuse holder/fuse cabinet failed | #2 ACSR AL | FUSE | 2019 | 2010
100121E7805 | Before | 2.2822 | 19.7288 | 1 | Tier 3 | 2020-09-19 | 2010-01-21 | Weather | 404 | 513 | Circ. Flashover/storm/high winds/undet. | #2 5/2 AWAC AL | OH CONDUCTOR | 2020 | 2010
100121E7808 | Before | 6.2219 | 15.789 | 1 | Tier 3 | 2016-10-12 | 2010-01-21 | Weather | 408 | 532 | Ice or snow/Equipment failure | #2 5/2 AWAC AL | POLE | 2016 | 2010
100121E7808 | Before | 7.3397 | 14.6712 | 1 | Tier 3 | 2015-08-31 | 2010-01-21 | Weather | 408 | 532 | Ice or snow/Equipment failure | #2 5/2 AWAC AL | POLE | 2015 | 2010
100227E5065 | Before | 2.3014 | 19.7096 | 1 | Tier 3 | 2020-09-12 | 2010-02-27 | Foreign Object | 308 | 513 | Bird contact | 336 ACSR AL | OH CONDUCTOR | 2020 | 2010
100227E5065 | Before | 2.3014 | 19.7096 | 1 | Tier 3 | 2020-09-12 | 2010-02-27 | Foreign Object | 308 | 513 | Bird contact | 336 ACSR AL | OH CONDUCTOR | 2020 | 2010
100307E5034 | Before | 7.0493 | 14.9616 | 1 | Tier 2 | 2015-12-15 | 2010-03-07 | Customer Contact | 710 | 532 | Vehicle contact | #2 AWAC AL | POLE | 2015 | 2010
100312E5005 | Before | 1.074 | 20.937 | 1 | Tier 3 | 2021-12-04 | 2010-03-12 | Equipment | 515 |  | OH connector failure (jumper/splice/squeeze-on) | #2 5/2 AWAC AL | JUMPER | 2021 | 2010
100314E5034 | Before | 4.8767 | 17.1342 | 1 | Tier 2 | 2018-02-15 | 2010-03-14 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2018 | 2010
100320E7601 | Before | 7.7836 | 14.2274 | 1 | Tier 2 | 2015-03-22 | 2010-03-20 | Equipment | 513 |  | Conductor failure/wire down | #2 5/2 AWAC AL | OH CONDUCTOR | 2015 | 2010
100404E5016 | Before | 4.5671 | 17.4438 | 1 | Tier 2 | 2018-06-08 | 2010-04-04 | Equipment | 520 |  | Fuse holder/fuse cabinet failed | #2 5/2 AWAC AL | FUSE | 2018 | 2010
100404E5016 | Before | 5 | 17.011 | 1 | Tier 2 | 2018-01-01 | 2010-04-04 | Equipment | 520 |  | Fuse holder/fuse cabinet failed | #2 ACSR AL | FUSE | 2018 | 2010
100602E7602 | Before | 3.0548 | 18.9562 | 1 | Tier 3 | 2019-12-12 | 2010-06-02 | Equipment | 550 |  | Transformer faulted/mechanical | #2 5/2 AWAC AL | TRANSFORMER | 2019 | 2010
100718E5051 | Before | 5.6027 | 16.4082 | 1 | Tier 2 | 2017-05-26 | 2010-07-18 | Equipment | 520 |  | Fuse holder/fuse cabinet failed | #2 5/2 AWAC AL | FUSE | 2017 | 2010
100907E5081 | Before | 8.8356 | 13.1753 | 1 | Tier 3 | 2014-03-03 | 2010-09-07 | Equipment | 502 |  | Arrester (lightning) failure | #2 5/2 AWAC AL | LIGHTNING ARRESTER | 2014 | 2010
100923E9901 | Before | 6.5288 | 15.4822 | 1 | Tier 2 | 2016-06-22 | 2010-09-23 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2016 | 2010
100923E9901 | Before | 6.5288 | 15.4822 | 1 | Tier 3 | 2016-06-22 | 2010-09-23 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2016 | 2010
101008E5006 | Before | 7.2603 | 14.7507 | 1 | Tier 2 | 2015-09-29 | 2010-10-08 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2015 | 2010
101018E7601 | Before | 4 | 18.011 | 1 | Tier 3 | 2019-01-01 | 2010-10-18 | Customer Contact | 710 | 532 | Vehicle contact | #2 ACSR AL | POLE | 2019 | 2010
101019E9907 | Before | 4.4384 | 17.5726 | 1 | Tier 2 | 2018-07-25 | 2010-10-19 | Weather | 410 | 208 | Lightning Arrester/Transformer failure | 336 ACSR AL | SERVICE RESTORER | 2018 | 2010
101020E5143 | Before | 7.4877 | 14.5233 | 1 | Tier 3 | 2015-07-08 | 2010-10-20 | Equipment | 515 | 532 | OH connector failure (jumper/splice/squeeze-on) | #2 5/2 AWAC AL | JUMPER | 2015 | 2010
101021E7811 | Before | 7.1479 | 14.863 | 1 | Tier 3 | 2015-11-09 | 2010-10-21 | Customer Contact | 710 | 532 | Vehicle contact | #4 SSC AL | POLE | 2015 | 2010
101022E7801 | Before | 7.1479 | 14.863 | 1 | Tier 3 | 2015-11-09 | 2010-10-22 | Equipment | 222 |  | Tie switch closed into fault | #4 SSC AL | POLE | 2015 | 2010
101022E7802 | Before | 7.1479 | 14.863 | 1 | Tier 3 | 2015-11-09 | 2010-10-22 | Customer Contact | 710 | 532 | Vehicle contact | #4 SSC AL | POLE | 2015 | 2010
101025E7201 | Before | 6.4521 | 15.5589 | 1 | Tier 3 | 2016-07-20 | 2010-10-25 | Equipment | 554 | 214 | Crossarm failure | #2 5/2 AWAC AL | CROSSARM | 2016 | 2010
101108E5008 | Before | 7.589 | 14.4219 | 1 | Tier 3 | 2015-06-01 | 2010-11-08 | Equipment | 516 | 554 | Connector/jumper/splice/elbow/rack | #2 5/2 AWAC AL | BUSHING | 2015 | 2010
101112E5133 | Before | 3.0247 | 18.9863 | 1 | Tier 3 | 2019-12-23 | 2010-11-12 | Equipment | 518 |  | Cutout failure | #2 5/2 AWAC AL | CUTOUT | 2019 | 2010
101220E5162 | Before | 3.2329 | 18.7781 | 1 | Tier 2 | 2019-10-08 | 2010-12-20 | Weather | 408 | 554 | Ice or snow/Equipment failure | #2 5/2 AWAC AL | CROSSARM | 2019 | 2010
101220E5162 | Before | 4 | 18.011 | 1 | Tier 2 | 2019-01-01 | 2010-12-20 | Weather | 408 | 554 | Ice or snow/Equipment failure | #2 ACSR AL | CROSSARM | 2019 | 2010
101222E5032 | Before | 3.5534 | 18.4575 | 1 | Tier 2 | 2019-06-13 | 2010-12-22 | Weather | 408 | 520 | Ice or snow/Equipment failure | 636 ACSR AL | FUSE | 2019 | 2010
101222E5032 | Before | 4 | 18.011 | 1 | Tier 2 | 2019-01-01 | 2010-12-22 | Weather | 408 | 520 | Ice or snow/Equipment failure | #2 ACSR AL | FUSE | 2019 | 2010
101222E5065 | Before | 1.9973 | 20.0137 | 1 | Tier 3 | 2021-01-01 | 2010-12-22 | Weather | 426 | 314 | Tree fell on line due to storm/wind | #2 ACSR AL | OH CONDUCTOR | 2021 | 2010
101222E7704 | Before | 6.1836 | 15.8274 | 1 | Tier 3 | 2016-10-26 | 2010-12-22 | Weather | 412 | 513 | Wind - wires slap/pole down | #2 5/2 AWAC AL | OH CONDUCTOR | 2016 | 2010
101222E7704 | Before | 6.1836 | 15.8274 | 1 | Tier 3 | 2016-10-26 | 2010-12-22 | Weather | 412 | 513 | Wind - wires slap/pole down | #2 5/2 AWAC AL | OH CONDUCTOR | 2016 | 2010
101229E5114 | Before | 1.9973 | 20.0137 | 1 | Tier 3 | 2021-01-01 | 2010-12-29 | Weather | 426 | 510 | Tree fell on line due to storm/wind | #2 ACSR AL | OH CONDUCTOR | 2021 | 2010
110115E7802 | Before | 5.1123 | 16.8986 | 1 | Tier 3 | 2017-11-21 | 2011-01-15 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2017 | 2011
110125E9901 | Before | 5.7096 | 16.3014 | 1 | Tier 3 | 2017-04-17 | 2011-01-25 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2017 | 2011
110205E5044 | Before | 2.8384 | 19.1726 | 1 | Tier 3 | 2020-02-29 | 2011-02-05 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2020 | 2011
110208E7501 | Before | 2.0904 | 19.9205 | 1 | Tier 3 | 2020-11-28 | 2011-02-08 | Foreign Object | 308 | 513 | Bird contact | 336 ACSR AL | OH CONDUCTOR | 2020 | 2011
110208E7501 | Before | 2.0904 | 19.9205 | 1 | Tier 3 | 2020-11-28 | 2011-02-08 | Foreign Object | 308 | 513 | Bird contact | 336 ACSR AL | OH CONDUCTOR | 2020 | 2011
110219E7802 | Before | 4.8384 | 17.1726 | 1 | Tier 3 | 2018-03-01 | 2011-02-19 | Weather | 410 | 532 | Lightning Arrester/Transformer failure | 336 ACSR AL | POLE | 2018 | 2011
110220E7601 | Before | 9.8603 | 12.1507 | 1 | Tier 2 | 2013-02-22 | 2011-02-20 | Weather | 408 | 513 | Ice or snow/Equipment failure | 336.4 ACSR AL | OH CONDUCTOR | 2013 | 2011
110220E7603 | Before | 8.8356 | 13.1753 | 1 | Tier 3 | 2014-03-03 | 2011-02-20 | Weather | 412 | 513 | Wind - wires slap/pole down | #2 5/2 AWAC AL | OH CONDUCTOR | 2014 | 2011
110220E7603 | Before | 8.8356 | 13.1753 | 1 | Tier 3 | 2014-03-03 | 2011-02-20 | Weather | 412 | 513 | Wind - wires slap/pole down | #2 5/2 AWAC AL | OH CONDUCTOR | 2014 | 2011
110220E9901 | Before | 3 | 19.011 | 1 | Tier 3 | 2020-01-01 | 2011-02-20 | Weather | 408 | 520 | Ice or snow/Equipment failure | #2 ACSR AL | FUSE | 2020 | 2011
110305E5073 | Before | 6.5836 | 15.4274 | 1 | Tier 2 | 2016-06-02 | 2011-03-05 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2016 | 2011
110308E7606 | Before | 7.7836 | 14.2274 | 1 | Tier 2 | 2015-03-22 | 2011-03-08 | Weather | 412 | 513 | Wind - wires slap/pole down | #2 5/2 AWAC AL | OH CONDUCTOR | 2015 | 2011
110308E7606 | Before | 7.7836 | 14.2274 | 1 | Tier 2 | 2015-03-22 | 2011-03-08 | Weather | 412 | 513 | Wind - wires slap/pole down | #2 5/2 AWAC AL | OH CONDUCTOR | 2015 | 2011
110322E7801 | Before | 4.5918 | 17.4192 | 1 | Tier 3 | 2018-05-30 | 2011-03-22 | Equipment | 554 | 214 | Crossarm failure | #2 5/2 AWAC AL | CROSSARM | 2018 | 2011
110517E5092 | Before | 1.0822 | 20.9288 | 1 | Tier 2 | 2021-12-01 | 2011-05-17 | Foreign Object | 308 | 510 | Bird contact | #2 5/2 AWAC AL | OH CONDUCTOR | 2021 | 2011
110517E5092 | Before | 1.0822 | 20.9288 | 1 | Tier 2 | 2021-12-01 | 2011-05-17 | Foreign Object | 308 | 510 | Bird contact | #2 5/2 AWAC AL | OH CONDUCTOR | 2021 | 2011
110519E9901 | Before | 4.5479 | 17.463 | 1 | Tier 2 | 2018-06-15 | 2011-05-19 | Equipment | 502 | 554 | Arrester (lightning) failure | #2 5/2 AWAC AL | LIGHTNING ARRESTER | 2018 | 2011
110526E7603 | Before | 4.5808 | 17.4301 | 1 | Tier 2 | 2018-06-03 | 2011-05-26 | Equipment | 515 | 214 | OH connector failure (jumper/splice/squeeze-on) | #2 5/2 AWAC AL | JUMPER | 2018 | 2011
110530E7801 | Before | 4.2658 | 17.7452 | 1 | Tier 2 | 2018-09-26 | 2011-05-30 | Tree Contact | 318 | 513 | Tree contact | #2 5/2 AWAC AL | OH CONDUCTOR | 2018 | 2011
110530E7801 | Before | 4.2658 | 17.7452 | 1 | Tier 2 | 2018-09-26 | 2011-05-30 | Tree Contact | 318 | 513 | Tree contact | #2 5/2 AWAC AL | OH CONDUCTOR | 2018 | 2011
110531E5030 | Before | 5.1233 | 16.8877 | 1 | Tier 2 | 2017-11-17 | 2011-05-31 | Equipment | 520 |  | Fuse holder/fuse cabinet failed | #2 5/2 AWAC AL | FUSE | 2017 | 2011
110531E9902 | Before | 6.0055 | 16.0055 | 1 | Tier 3 | 2016-12-30 | 2011-05-31 | Equipment | 530 | 214 | Insulator/pin failure/wire floating | #2 5/2 AWAC AL | CONNECTOR | 2016 | 2011
110701E7101 | Before | 2.7041 | 19.3068 | 1 | Tier 3 | 2020-04-18 | 2011-07-01 | Equipment | 550 |  | Transformer faulted/mechanical | #2 5/2 AWAC AL | TRANSFORMER | 2020 | 2011
110706E7602 | Before | 7.4658 | 14.5452 | 1 | Tier 3 | 2015-07-16 | 2011-07-06 | Equipment | 554 | 532 | Crossarm failure | #2 5/2 AWAC AL | CROSSARM | 2015 | 2011
110711E5101 | Before | 7.4438 | 14.5671 | 1 | Tier 3 | 2015-07-24 | 2011-07-11 | Equipment | 554 |  | Crossarm failure | #2 5/2 AWAC AL | CROSSARM | 2015 | 2011
110711E5101 | Before | 9.0027 | 13.0082 | 1 | Tier 3 | 2014-01-01 | 2011-07-11 | Equipment | 554 |  | Crossarm failure | #2 5/2 AWAC AL | CROSSARM | 2014 | 2011
110801E5006 | Before | 6.6192 | 15.3918 | 1 | Tier 3 | 2016-05-20 | 2011-08-01 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2016 | 2011
110807E7601 | Before | 7.7781 | 14.2329 | 1 | Tier 3 | 2015-03-24 | 2011-08-07 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2015 | 2011
110828E9902 | Before | 5.6247 | 16.3863 | 1 | Tier 3 | 2017-05-18 | 2011-08-28 | Equipment | 540 | 214 | Regulator faulted/mechanical | 336 ACSR AL | REGULATOR | 2017 | 2011
110829E7801 | Before | 5 | 17.011 | 1 | Tier 3 | 2018-01-01 | 2011-08-29 | Customer Contact | 710 | 532 | Vehicle contact | #2 ACSR AL | POLE | 2018 | 2011
110907E5075 | Before | 1.6521 | 20.3589 | 1 | Tier 2 | 2021-05-07 | 2011-09-07 | Equipment | 515 |  | OH connector failure (jumper/splice/squeeze-on) | #2 5/2 AWAC AL | JUMPER | 2021 | 2011
110915E5086 | Before | 2.6877 | 19.3233 | 1 | Tier 2 | 2020-04-24 | 2011-09-15 | Weather | 410 | 532 | Lightning Arrester/Transformer failure | #2 5/2 AWAC AL | POLE | 2020 | 2011
110915E5086 | Before | 1.5151 | 20.4959 | 1 | Tier 2 | 2021-06-26 | 2011-09-15 | Weather | 410 | 532 | Lightning Arrester/Transformer failure | #2 5/2 AWAC AL | POLE | 2021 | 2011
111112E7801 | Before | 1.0795 | 20.9315 | 1 | Tier 2 | 2021-12-02 | 2011-11-12 | Equipment | 518 |  | Cutout failure | 336 ACSR AL | CUTOUT | 2021 | 2011
111120E7804 | Before | 5 | 17.011 | 1 | Tier 2 | 2018-01-01 | 2011-11-20 | Equipment | 550 | 214 | Transformer faulted/mechanical | #2 ACSR AL | TRANSFORMER | 2018 | 2011
111130E5046 | Before | 3.0247 | 18.9863 | 1 | Tier 3 | 2019-12-23 | 2011-11-30 | Crew Contact | 632 | 522 | SDG&E Contr. Crew error | #2 5/2 AWAC AL | FUSE | 2019 | 2011
111130E5046 | Before | 3.2712 | 18.7397 | 1 | Tier 3 | 2019-09-24 | 2011-11-30 | Crew Contact | 632 | 522 | SDG&E Contr. Crew error | #2 5/2 AWAC AL | FUSE | 2019 | 2011
111212E9901 | Before | 2.8384 | 19.1726 | 1 | Tier 3 | 2020-02-29 | 2011-12-12 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2020 | 2011
111213E7801 | Before | 4.5918 | 17.4192 | 1 | Tier 2 | 2018-05-30 | 2011-12-12 | Foreign Object | 308 | 510 | Bird contact | #2 5/2 AWAC AL | OH CONDUCTOR | 2018 | 2011
111213E7801 | Before | 4.5918 | 17.4192 | 1 | Tier 2 | 2018-05-30 | 2011-12-12 | Foreign Object | 308 | 510 | Bird contact | #2 5/2 AWAC AL | OH CONDUCTOR | 2018 | 2011
111227E5105 | Before | 3.2685 | 18.7425 | 1 | Tier 2 | 2019-09-25 | 2011-12-27 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2019 | 2011
120125E7601 | Before | 7.6712 | 14.3397 | 1 | Tier 3 | 2015-05-02 | 2012-01-25 | Equipment | 532 | 214 | Pole broke/rotted/on fire | #2 5/2 AWAC AL | POLE | 2015 | 2012
120212E7601 | Before | 4.2493 | 17.7616 | 1 | Tier 3 | 2018-10-02 | 2012-02-12 | Tree Contact | 322 | 510 | Tree fell on line | #2 5/2 AWAC AL | OH CONDUCTOR | 2018 | 2012
120212E7601 | Before | 4.2493 | 17.7616 | 1 | Tier 3 | 2018-10-02 | 2012-02-12 | Tree Contact | 322 | 510 | Tree fell on line | #2 5/2 AWAC AL | OH CONDUCTOR | 2018 | 2012
120214E9901 | Before | 7.0329 | 14.9781 | 1 | Tier 2 | 2015-12-21 | 2012-02-14 | Weather | 412 | 513 | Wind - wires slap/pole down | #2 5/2 AWAC AL | OH CONDUCTOR | 2015 | 2012
120214E9901 | Before | 7.0329 | 14.9781 | 1 | Tier 2 | 2015-12-21 | 2012-02-14 | Weather | 412 | 513 | Wind - wires slap/pole down | #2 5/2 AWAC AL | OH CONDUCTOR | 2015 | 2012
120216E7601 | Before | 0.69863 | 21.3123 | 1 | Tier 3 | 2022-04-20 | 2012-02-15 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2022 | 2012
120227E5143 | Before | 7.0027 | 15.0082 | 1 | Tier 3 | 2016-01-01 | 2012-02-27 | Weather | 410 | 550 | Lightning Arrester/Transformer failure | #2 5/2 AWAC AL | TRANSFORMER | 2016 | 2012
120307E9901 | Before | 4.5918 | 17.4192 | 1 | Tier 2 | 2018-05-30 | 2012-03-07 | Equipment | 518 |  | Cutout failure | 336 ACSR AL | CUTOUT | 2018 | 2012
120314E7801 | Before | 5.8164 | 16.1945 | 1 | Tier 3 | 2017-03-09 | 2012-03-13 | Equipment | 515 |  | OH connector failure (jumper/splice/squeeze-on) | #2 5/2 AWAC AL | JUMPER | 2017 | 2012
120318E7603 | Before | 9.9068 | 12.1041 | 1 | Tier 3 | 2013-02-05 | 2012-03-18 | Weather | 412 | 513 | Wind - wires slap/pole down | #2 5/2 AWAC AL | OH CONDUCTOR | 2013 | 2012
120318E7603 | Before | 9.9068 | 12.1041 | 1 | Tier 3 | 2013-02-05 | 2012-03-18 | Weather | 412 | 513 | Wind - wires slap/pole down | #2 5/2 AWAC AL | OH CONDUCTOR | 2013 | 2012
120318E9911 | Before | 8.8356 | 13.1753 | 1 | Tier 3 | 2014-03-03 | 2012-03-18 | Weather | 408 | 513 | Ice or snow/Equipment failure | #2 5/2 AWAC AL | OH CONDUCTOR | 2014 | 2012
120318E9914 | Before | 8.8356 | 13.1753 | 1 | Tier 3 | 2014-03-03 | 2012-03-18 | Weather | 412 | 513 | Wind - wires slap/pole down | #2 5/2 AWAC AL | OH CONDUCTOR | 2014 | 2012
120318E9914 | Before | 8.8356 | 13.1753 | 1 | Tier 3 | 2014-03-03 | 2012-03-18 | Weather | 412 | 513 | Wind - wires slap/pole down | #2 5/2 AWAC AL | OH CONDUCTOR | 2014 | 2012
120319E7605 | Before | 0.56164 | 21.4493 | 1 | Tier 3 | 2022-06-09 | 2012-03-19 | Weather | 408 | 520 | Ice or snow/Equipment failure | #2 5/2 AWAC AL | FUSE | 2022 | 2012
120414E9902 | Before | 8.8356 | 13.1753 | 1 | Tier 3 | 2014-03-03 | 2012-04-14 | Weather | 412 | 513 | Wind - wires slap/pole down | #2 5/2 AWAC AL | OH CONDUCTOR | 2014 | 2012
120414E9902 | Before | 8.8356 | 13.1753 | 1 | Tier 3 | 2014-03-03 | 2012-04-14 | Weather | 412 | 513 | Wind - wires slap/pole down | #2 5/2 AWAC AL | OH CONDUCTOR | 2014 | 2012
120513E9904 | Before | 3.1753 | 18.8356 | 1 | Tier 2 | 2019-10-29 | 2012-05-13 | Equipment | 518 |  | Cutout failure | #2 5/2 AWAC AL | CUTOUT | 2019 | 2012
120528E8106 | Before | 3.6274 | 18.3836 | 1 | Tier 2 | 2019-05-17 | 2012-05-28 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2019 | 2012
120603E8104 | Before | 8.4137 | 13.5973 | 1 | Tier 3 | 2014-08-04 | 2012-06-03 | Foreign Object | 308 | 513 | Bird contact | #2 5/2 AWAC AL | OH CONDUCTOR | 2014 | 2012
120603E8104 | Before | 8.4137 | 13.5973 | 1 | Tier 3 | 2014-08-04 | 2012-06-03 | Foreign Object | 308 | 513 | Bird contact | #2 5/2 AWAC AL | OH CONDUCTOR | 2014 | 2012
120604E8102 | Before | 6.0877 | 15.9233 | 1 | Tier 3 | 2016-11-30 | 2012-06-04 | Equipment | 528 |  | Hardware failure | #2 5/2 AWAC AL | MISC EQUIPMENT | 2016 | 2012
120613E5067 | Before | 8.0055 | 14.0055 | 1 | Tier 3 | 2014-12-31 | 2012-06-13 | Equipment | 522 |  | Fuse overloaded/inadequate fuse size | #2 5/2 AWAC AL | FUSE | 2014 | 2012
120627E8101 | Before | 2.3397 | 19.6712 | 1 | Tier 2 | 2020-08-29 | 2012-06-27 | Equipment | 532 | 214 | Pole broke/rotted/on fire | #2 5/2 AWAC AL | POLE | 2020 | 2012
120717E8105 | Before | 6.7753 | 15.2356 | 1 | Tier 3 | 2016-03-24 | 2012-07-17 | Equipment | 550 | 214 | Transformer faulted/mechanical | 1/0 15kV Spacer Cable AL | TRANSFORMER | 2016 | 2012
120810E8101 | Before | 5.1233 | 16.8877 | 1 | Tier 2 | 2017-11-17 | 2012-08-10 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2017 | 2012
120811E5074 | Before | 7.7781 | 14.2329 | 1 | Tier 3 | 2015-03-24 | 2012-08-11 | Weather | 410 | 550 | Lightning Arrester/Transformer failure | #2 5/2 AWAC AL | TRANSFORMER | 2015 | 2012
120813E8123 | Before | 7.0493 | 14.9616 | 1 | Tier 2 | 2015-12-15 | 2012-08-13 | Equipment | 552 |  | Transformer overloaded/electrical | #2 AWAC AL | BOOSTER STA | 2015 | 2012
120816E5042 | Before | 2.9726 | 19.0384 | 1 | Tier 3 | 2020-01-11 | 2012-08-16 | Weather | 410 | 518 | Lightning Arrester/Transformer failure | 336 ACSR AL | CUTOUT | 2020 | 2012
120830E5044 | Before | 2.8384 | 19.1726 | 1 | Tier 3 | 2020-02-29 | 2012-08-30 | Customer Contact | 710 | 526 | Vehicle contact | #2 5/2 AWAC AL | GUY WIRE | 2020 | 2012
120909E5042 | Before | 7.0027 | 15.0082 | 1 | Tier 2 | 2016-01-01 | 2012-09-09 | Weather | 410 | 550 | Lightning Arrester/Transformer failure | #2 ACSR AL | TRANSFORMER | 2016 | 2012
121011E3026 | Before | 6.6082 | 15.4027 | 1 | Tier 3 | 2016-05-24 | 2012-10-11 | Equipment | 522 |  | Fuse overloaded/inadequate fuse size | #2 5/2 AWAC AL | FUSE | 2016 | 2012
121107E5250 | Before | 3.9342 | 18.0767 | 1 | Tier 2 | 2019-01-25 | 2012-11-07 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2019 | 2012
121116E5723 | Before | 7.6986 | 14.3123 | 1 | Tier 2 | 2015-04-22 | 2012-11-16 | Foreign Object | 308 | 510 | Bird contact | #2 5/2 AWAC AL | OH CONDUCTOR | 2015 | 2012
121116E5723 | Before | 7.6986 | 14.3123 | 1 | Tier 2 | 2015-04-22 | 2012-11-16 | Foreign Object | 308 | 510 | Bird contact | #2 5/2 AWAC AL | OH CONDUCTOR | 2015 | 2012
121210E6939 | Before | 1.8356 | 20.1753 | 1 | Tier 3 | 2021-03-01 | 2012-12-10 | Equipment | 550 |  | Transformer faulted/mechanical | #2 5/2 AWAC AL | TRANSFORMER | 2021 | 2012
121213E7239 | Before | 5.6521 | 16.3589 | 1 | Tier 3 | 2017-05-08 | 2012-12-13 | Equipment | 550 |  | Transformer faulted/mechanical | #2 5/2 AWAC AL | TRANSFORMER | 2017 | 2012
121213E7285 | Before | 4 | 18.011 | 1 | Tier 3 | 2019-01-01 | 2012-12-13 | Customer Contact | 710 | 532 | Vehicle contact | #2 ACSR AL | POLE | 2019 | 2012
121218E7497 | Before | 7.3589 | 14.6521 | 1 | Tier 2 | 2015-08-24 | 2012-12-18 | Foreign Object | 308 | 513 | Bird contact | #2 5/2 AWAC AL | OH CONDUCTOR | 2015 | 2012
121218E7497 | Before | 7.3589 | 14.6521 | 1 | Tier 2 | 2015-08-24 | 2012-12-18 | Foreign Object | 308 | 513 | Bird contact | #2 5/2 AWAC AL | OH CONDUCTOR | 2015 | 2012
130106E8388 | Before | 3.9753 | 18.0356 | 1 | Tier 2 | 2019-01-10 | 2013-01-06 | Equipment | 513 |  | Conductor failure/wire down | #2 5/2 AWAC AL | OH CONDUCTOR | 2019 | 2013
130113E8876 | Before | 3.0356 | 18.9753 | 1 | Tier 3 | 2019-12-19 | 2013-01-13 | Equipment | 513 |  | Conductor failure/wire down | #2 5/2 AWAC AL | OH CONDUCTOR | 2019 | 2013
130126E9767 | Before | 6.8548 | 15.1562 | 1 | Tier 3 | 2016-02-24 | 2013-01-26 | Equipment | 502 |  | Arrester (lightning) failure | #2 5/2 AWAC AL | LIGHTNING ARRESTER | 2016 | 2013
130203E10326 | After | 10.0027 | 12.0082 | 1 | Tier 2 | 2013-01-01 | 2013-02-03 | Equipment | 532 | 554 | Pole broke/rotted/on fire | 394.5 5005 AL | POLE | 2013 | 2013
130203E10330 | After | 10.0027 | 12.0082 | 1 | Tier 2 | 2013-01-01 | 2013-02-03 | Equipment | 532 | 214 | Pole broke/rotted/on fire | 394.5 5005 AL | POLE | 2013 | 2013
130216E11251 | Before | 1.9973 | 20.0137 | 1 | Tier 2 | 2021-01-01 | 2013-02-16 | Equipment | 554 |  | Crossarm failure | 4/0 B.STRD CU | CROSSARM | 2021 | 2013
130220E11367 | Before | 7.9041 | 14.1068 | 1 | Tier 2 | 2015-02-06 | 2013-02-20 | Weather | 404 | 412 | Circ. Flashover/storm/high winds/undet. | #2 5/2 AWAC AL | OH CONDUCTOR | 2015 | 2013
130220E11376 | Before | 2.2822 | 19.7288 | 1 | Tier 3 | 2020-09-19 | 2013-02-20 | Weather | 408 | 513 | Ice or snow/Equipment failure | #2 5/2 AWAC AL | OH CONDUCTOR | 2020 | 2013
130310E12520 | Before | 4 | 18.011 | 1 | Tier 3 | 2019-01-01 | 2013-03-10 | Customer Contact | 710 | 532 | Vehicle contact | #2 ACSR AL | POLE | 2019 | 2013
130502E16735 | Before | 4.4384 | 17.5726 | 1 | Tier 2 | 2018-07-25 | 2013-05-02 | Equipment | 532 |  | Pole broke/rotted/on fire | 336 ACSR AL | POLE | 2018 | 2013
130506E16791 | Before | 5.3836 | 16.6274 | 1 | Tier 3 | 2017-08-14 | 2013-05-06 | Equipment | 515 | 513 | OH connector failure (jumper/splice/squeeze-on) | #2 5/2 AWAC AL | CONNECTOR | 2017 | 2013
130506E16797 | Before | 3.0137 | 18.9973 | 1 | Tier 2 | 2019-12-27 | 2013-05-06 | Equipment | 554 |  | Crossarm failure | 636 ACSR AL | CROSSARM | 2019 | 2013
130506E17006 | Before | 3.0137 | 18.9973 | 1 | Tier 2 | 2019-12-27 | 2013-05-06 | Equipment | 554 | 214 | Crossarm failure | 636 ACSR AL | CROSSARM | 2019 | 2013
130512E17359 | Before | 7.2411 | 14.7699 | 1 | Tier 2 | 2015-10-06 | 2013-05-12 | Equipment | 515 | 214 | OH connector failure (jumper/splice/squeeze-on) | 636 ACSR AL | JUMPER | 2015 | 2013
130516E17710 | Before | 2.4548 | 19.5562 | 1 | Tier 2 | 2020-07-18 | 2013-05-16 | Equipment | 554 | 214 | Crossarm failure | #2 5/2 AWAC AL | CROSSARM | 2020 | 2013
130523E18204 | Before | 6.5836 | 15.4274 | 1 | Tier 3 | 2016-06-02 | 2013-05-23 | Equipment | 502 | 550 | Arrester (lightning) failure | #2 5/2 AWAC AL | LIGHTNING ARRESTER | 2016 | 2013
130627E20500 | Before | 1.5534 | 20.4575 | 1 | Tier 2 | 2021-06-12 | 2013-06-27 | Equipment | 522 |  | Fuse overloaded/inadequate fuse size | #2 5/2 AWAC AL | FUSE | 2021 | 2013
130628E20504 | Before | 2.6849 | 19.326 | 1 | Tier 2 | 2020-04-25 | 2013-06-28 | Equipment | 504 |  | Capacitor failure | #2 5/2 AWAC AL | CAP BANK | 2020 | 2013
130721E21949 | After | 9.5014 | 12.5096 | 1 | Tier 2 | 2013-07-03 | 2013-07-21 | Equipment | 520 |  | Fuse holder/fuse cabinet failed | 336.4 ACSR AL | FUSE | 2013 | 2013
130721E21950 | Before | 5 | 17.011 | 1 | Tier 2 | 2018-01-01 | 2013-07-21 | Equipment | 550 |  | Transformer faulted/mechanical | #2 5/2 AWAC AL | TRANSFORMER | 2018 | 2013
130806E23022 | Before | 3.9753 | 18.0356 | 1 | Tier 3 | 2019-01-10 | 2013-08-06 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2019 | 2013
130809E23257 | Before | 5.8055 | 16.2055 | 1 | Tier 3 | 2017-03-13 | 2013-08-09 | Equipment | 515 | 530 | OH connector failure (jumper/splice/squeeze-on) | #2 5/2 AWAC AL | CONNECTOR | 2017 | 2013
130829E24511 | Before | 1.463 | 20.5479 | 1 | Tier 3 | 2021-07-15 | 2013-08-29 | Weather | 410 | 518 | Lightning Arrester/Transformer failure | #2 3/4 AWAC AL | CUTOUT | 2021 | 2013
130907E25347 | Before | 8.6219 | 13.389 | 1 | Tier 3 | 2014-05-20 | 2013-09-07 | Weather | 410 | 532 | Lightning Arrester/Transformer failure | 1/0 4/3 AWAC AL | POLE | 2014 | 2013
130913E25788 | Before | 7.7836 | 14.2274 | 1 | Tier 2 | 2015-03-22 | 2013-09-13 | Equipment | 528 | 513 | Hardware failure | #2 5/2 AWAC AL | MISC EQUIPMENT | 2015 | 2013
131006E27276 | Before | 5.8055 | 16.2055 | 1 | Tier 3 | 2017-03-13 | 2013-10-06 | Equipment | 518 | 504 | Cutout failure | #2 5/2 AWAC AL | CUTOUT | 2017 | 2013
131008E27441 | Before | 7.8877 | 14.1233 | 1 | Tier 3 | 2015-02-12 | 2013-10-08 | Equipment | 515 | 513 | OH connector failure (jumper/splice/squeeze-on) | 336 ACSR AL | CONNECTOR | 2015 | 2013
131026E28780 | Before | 7.6055 | 14.4055 | 1 | Tier 2 | 2015-05-26 | 2013-10-26 | Equipment | 502 | 550 | Arrester (lightning) failure | #2 5/2 AWAC AL | LIGHTNING ARRESTER | 2015 | 2013
131026E28780 | Before | 7.6219 | 14.389 | 1 | Tier 2 | 2015-05-20 | 2013-10-26 | Equipment | 502 | 550 | Arrester (lightning) failure | #2 5/2 AWAC AL | LIGHTNING ARRESTER | 2015 | 2013
131028E28835 | Before | 4.7425 | 17.2685 | 1 | Tier 3 | 2018-04-05 | 2013-10-28 | Equipment | 502 |  | Arrester (lightning) failure | #2 5/2 AWAC AL | LIGHTNING ARRESTER | 2018 | 2013
131103E29248 | Before | 1.5534 | 20.4575 | 1 | Tier 2 | 2021-06-12 | 2013-11-03 | Equipment | 520 |  | Fuse holder/fuse cabinet failed | #2 5/2 AWAC AL | FUSE | 2021 | 2013
131111E29747 | Before | 6.4658 | 15.5452 | 1 | Tier 3 | 2016-07-15 | 2013-11-11 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2016 | 2013
131111E29755 | Before | 6.4384 | 15.5726 | 1 | Tier 3 | 2016-07-25 | 2013-11-11 | Foreign Object | 308 | 510 | Bird contact | #2 5/2 AWAC AL | OH CONDUCTOR | 2016 | 2013
131111E29755 | Before | 6.4384 | 15.5726 | 1 | Tier 3 | 2016-07-25 | 2013-11-11 | Foreign Object | 308 | 510 | Bird contact | #2 5/2 AWAC AL | OH CONDUCTOR | 2016 | 2013
131201E30934 | Before | 4.6466 | 17.3644 | 1 | Tier 3 | 2018-05-10 | 2013-12-01 | Equipment | 532 | 513 | Pole broke/rotted/on fire | #2 5/2 AWAC AL | POLE | 2018 | 2013
131207E31310 | Before | 8.8356 | 13.1753 | 1 | Tier 3 | 2014-03-03 | 2013-12-07 | Weather | 412 | 513 | Wind - wires slap/pole down | #2 5/2 AWAC AL | OH CONDUCTOR | 2014 | 2013
131207E31310 | Before | 8.8356 | 13.1753 | 1 | Tier 3 | 2014-03-03 | 2013-12-07 | Weather | 412 | 513 | Wind - wires slap/pole down | #2 5/2 AWAC AL | OH CONDUCTOR | 2014 | 2013
131207E31333 | Before | 1.6247 | 20.3863 | 1 | Tier 3 | 2021-05-17 | 2013-12-07 | Weather | 408 | 536 | Ice or snow/Equipment failure | #2 3/4 AWAC AL | SERVICE RESTORER | 2021 | 2013
131227E32428 | Before | 3.5507 | 18.4603 | 1 | Tier 2 | 2019-06-14 | 2013-12-27 | Equipment | 532 | 214 | Pole broke/rotted/on fire | #2 5/2 AWAC AL | POLE | 2019 | 2013
140125E34233 | Before | 0.69863 | 21.3123 | 1 | Tier 3 | 2022-04-20 | 2014-01-25 | Equipment | 502 |  | Arrester (lightning) failure | #2 5/2 AWAC AL | LIGHTNING ARRESTER | 2022 | 2014
140206E35229 | Before | 6.6192 | 15.3918 | 1 | Tier 3 | 2016-05-20 | 2014-02-06 | Equipment | 518 |  | Cutout failure | #2 5/2 AWAC AL | CUTOUT | 2016 | 2014
140208E35334 | Before | 3.9342 | 18.0767 | 1 | Tier 2 | 2019-01-25 | 2014-02-08 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2019 | 2014
140224E36398 | After | 9.0027 | 13.0082 | 1 | Tier 2 | 2014-01-01 | 2014-02-24 | Customer Contact | 710 | 532 | Vehicle contact | #2 ACSR AL | POLE | 2014 | 2014
140228E36876 | Before | 6.811 | 15.2 | 1 | Tier 3 | 2016-03-11 | 2014-02-28 | Weather | 404 | 208 | Circ. Flashover/storm/high winds/undet. | 336 ACSR AL | SERVICE RESTORER | 2016 | 2014
140228E36965 | Before | 3.9753 | 18.0356 | 1 | Tier 3 | 2019-01-10 | 2014-02-28 | Weather | 410 | 550 | Lightning Arrester/Transformer failure | #2 5/2 AWAC AL | TRANSFORMER | 2019 | 2014
140228E36996 | Before | 4.5671 | 17.4438 | 1 | Tier 2 | 2018-06-08 | 2014-02-28 | Equipment | 515 |  | OH connector failure (jumper/splice/squeeze-on) | #2 5/2 AWAC AL | JUMPER | 2018 | 2014
140301E37038 | Before | 1.0356 | 20.9753 | 1 | Tier 2 | 2021-12-18 | 2014-03-01 | Weather | 412 | 513 | Wind - wires slap/pole down | #2 3/4 AWAC AL | OH CONDUCTOR | 2021 | 2014
140301E37051 | Before | 3.9397 | 18.0712 | 1 | Tier 2 | 2019-01-23 | 2014-03-01 | Weather | 410 | 550 | Lightning Arrester/Transformer failure | #2 5/2 AWAC AL | TRANSFORMER | 2019 | 2014
140318E38334 | After | 9.3507 | 12.6603 | 1 | Tier 3 | 2013-08-27 | 2014-03-18 | Equipment | 530 | 214 | Insulator/pin failure/wire floating | #2 ACSR AL | OH CONDUCTOR | 2013 | 2014
140324E38861 | Before | 8.2082 | 13.8027 | 1 | Tier 3 | 2014-10-18 | 2014-03-24 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2014 | 2014
140331E39501 | Before | 4.8767 | 17.1342 | 1 | Tier 2 | 2018-02-15 | 2014-03-31 | Tree Contact | 322 | 513 | Tree fell on line | 336 ACSR AL | OH CONDUCTOR | 2018 | 2014
140331E39501 | Before | 4.8767 | 17.1342 | 1 | Tier 2 | 2018-02-15 | 2014-03-31 | Tree Contact | 322 | 513 | Tree fell on line | 336 ACSR AL | OH CONDUCTOR | 2018 | 2014
140429E41740 | Before | 3.5507 | 18.4603 | 1 | Tier 2 | 2019-06-14 | 2014-04-29 | Equipment | 515 |  | OH connector failure (jumper/splice/squeeze-on) | #2 5/2 AWAC AL | JUMPER | 2019 | 2014
140430E41755 | Before | 7.1151 | 14.8959 | 1 | Tier 3 | 2015-11-21 | 2014-04-30 | Weather | 426 | 532 | Tree fell on line due to storm/wind | #2 5/2 AWAC AL |  | 2015 | 2014
140430E41817 | Before | 3.9068 | 18.1041 | 1 | Tier 2 | 2019-02-04 | 2014-04-30 | Weather | 426 | 526 | Tree fell on line due to storm/wind | #2 5/2 AWAC AL | GUY WIRE | 2019 | 2014
140501E41885 | Before | 6 | 16.011 | 1 | Tier 2 | 2017-01-01 | 2014-05-01 | Equipment | 554 |  | Crossarm failure | 336.4 ACSR AL | CROSSARM | 2017 | 2014
140501E41885 | Before | 6 | 16.011 | 1 | Tier 2 | 2017-01-01 | 2014-05-01 | Equipment | 554 |  | Crossarm failure | 636 ACSR AL | CROSSARM | 2017 | 2014
140513E42675 | Before | 7.5096 | 14.5014 | 1 | Tier 3 | 2015-06-30 | 2014-05-13 | Equipment | 515 |  | OH connector failure (jumper/splice/squeeze-on) | #2 5/2 AWAC AL | JUMPER | 2015 | 2014
140527E43728 | Before | 7.6603 | 14.3507 | 1 | Tier 2 | 2015-05-06 | 2014-05-27 | Equipment | 522 |  | Fuse overloaded/inadequate fuse size | 336.4 ACSR AL | FUSE | 2015 | 2014
140527E43729 | Before | 7.6603 | 14.3507 | 1 | Tier 2 | 2015-05-06 | 2014-05-27 | Equipment | 522 |  | Fuse overloaded/inadequate fuse size | 336.4 ACSR AL | FUSE | 2015 | 2014
140615E45061 | Before | 1.5726 | 20.4384 | 1 | Tier 3 | 2021-06-05 | 2014-06-15 | Customer Contact | 702 | 510 | Heavy equp contact/digin | 336 ACSR AL | OH CONDUCTOR | 2021 | 2014
140627E45946 | Before | 4.8767 | 17.1342 | 1 | Tier 2 | 2018-02-15 | 2014-06-27 | Equipment | 515 | 513 | OH connector failure (jumper/splice/squeeze-on) | 336 ACSR AL | CONNECTOR | 2018 | 2014
140714E47175 | Before | 1.1123 | 20.8986 | 1 | Tier 3 | 2021-11-20 | 2014-07-14 | Weather | 410 | 538 | Lightning Arrester/Transformer failure | #2 5/2 AWAC AL | SERVICE RESTORER | 2021 | 2014
140714E47175 | Before | 1.1123 | 20.8986 | 1 | Tier 3 | 2021-11-20 | 2014-07-14 | Weather | 410 | 538 | Lightning Arrester/Transformer failure | 336 ACSR AL | SERVICE RESTORER | 2021 | 2014
140717E47386 | After | 9.0027 | 13.0082 | 1 | Tier 2 | 2014-01-01 | 2014-07-17 | Customer Contact | 710 | 532 | Vehicle contact | 3/0 ACSR AL | POLE | 2014 | 2014
140717E47386 | Before | 4 | 18.011 | 1 | Tier 2 | 2019-01-01 | 2014-07-17 | Customer Contact | 710 | 532 | Vehicle contact | 3/0 ACSR AL | POLE | 2019 | 2014
140724E48008 | Before | 8.0027 | 14.0082 | 1 | Tier 2 | 2015-01-01 | 2014-07-24 | Weather | 404 | 536 | Circ. Flashover/storm/high winds/undet. | 636 ACSR AL | SERVICE RESTORER | 2015 | 2014
140803E48739 | Before | 8.0274 | 13.9836 | 1 | Tier 3 | 2014-12-23 | 2014-08-03 | Weather | 410 | 550 | Lightning Arrester/Transformer failure | #2 5/2 AWAC AL | TRANSFORMER | 2014 | 2014
140804E48838 | Before | 6 | 16.011 | 1 | Tier 2 | 2017-01-01 | 2014-08-04 | Customer Contact | 710 | 532 | Vehicle contact | #2 ACSR AL | POLE | 2017 | 2014
140820E49991 | Before | 4.5699 | 17.4411 | 1 | Tier 2 | 2018-06-07 | 2014-08-20 | Weather | 410 | 502 | Lightning Arrester/Transformer failure | #2 5/2 AWAC AL | LIGHTNING ARRESTER | 2018 | 2014
140823E50305 | Before | 5.0767 | 16.9342 | 1 | Tier 3 | 2017-12-04 | 2014-08-23 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2017 | 2014
140905E51051 | Before | 6 | 16.011 | 1 | Tier 2 | 2017-01-01 | 2014-09-05 | Customer Contact | 710 | 532 | Vehicle contact | #2 ACSR AL | POLE | 2017 | 2014
140914E51711 | Before | 3.3233 | 18.6877 | 1 | Tier 2 | 2019-09-05 | 2014-09-14 | Weather | 408 | 518 | Ice or snow/Equipment failure | #2 5/2 AWAC AL | CUTOUT | 2019 | 2014
140924E52581 | Before | 5.3397 | 16.6712 | 1 | Tier 3 | 2017-08-30 | 2014-09-24 | Equipment | 550 |  | Transformer faulted/mechanical | 336 ACSR AL | TRANSFORMER | 2017 | 2014
141014E54117 | Before | 7.589 | 14.4219 | 1 | Tier 3 | 2015-06-01 | 2014-10-14 | Equipment | 518 |  | Cutout failure | #2 5/2 AWAC AL | CUTOUT | 2015 | 2014
141028E55164 | Before | 2.6466 | 19.3644 | 1 | Tier 3 | 2020-05-09 | 2014-10-28 | Equipment | 554 | 214 | Crossarm failure | #2 5/2 AWAC AL | CROSSARM | 2020 | 2014
141028E55164 | Before | 8.0055 | 14.0055 | 1 | Tier 3 | 2014-12-31 | 2014-10-28 | Equipment | 554 | 214 | Crossarm failure | #2 5/2 AWAC AL | CROSSARM | 2014 | 2014
141114E56427 | Before | 8.0055 | 14.0055 | 1 | Tier 3 | 2014-12-31 | 2014-11-14 | Equipment | 513 |  | Conductor failure/wire down | #2 5/2 AWAC AL | OH CONDUCTOR | 2014 | 2014
141119E56836 | Before | 7.0493 | 14.9616 | 1 | Tier 2 | 2015-12-15 | 2014-11-19 | Weather | 408 | 506 | Ice or snow/Equipment failure | #2 AWAC AL | CONNECTOR | 2015 | 2014
141119E56836 | Before | 7.7836 | 14.2274 | 1 | Tier 2 | 2015-03-22 | 2014-11-19 | Weather | 408 | 506 | Ice or snow/Equipment failure | #2 5/2 AWAC AL | CONNECTOR | 2015 | 2014
141220E58903 | Before | 3.5507 | 18.4603 | 1 | Tier 2 | 2019-06-14 | 2014-12-20 | Equipment | 515 |  | OH connector failure (jumper/splice/squeeze-on) | #2 5/2 AWAC AL | JUMPER | 2019 | 2014
150107E59579 | Before | 3.9342 | 18.0767 | 1 | Tier 2 | 2019-01-25 | 2015-01-07 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2019 | 2015
150109E59744 | Before | 2.4356 | 19.5753 | 1 | Tier 3 | 2020-07-25 | 2015-01-09 | Equipment | 522 |  | Fuse overloaded/inadequate fuse size | 336.4 ACSR AL | FUSE | 2020 | 2015
150115E60127 | Before | 7.6767 | 14.3342 | 1 | Tier 3 | 2015-04-30 | 2015-01-15 | Equipment | 515 |  | OH connector failure (jumper/splice/squeeze-on) | #2 5/2 AWAC AL | JUMPER | 2015 | 2015
150124E60653 | Before | 3.3014 | 18.7096 | 1 | Tier 2 | 2019-09-13 | 2015-01-24 | Equipment | 515 |  | OH connector failure (jumper/splice/squeeze-on) | #2 5/2 AWAC AL | JUMPER | 2019 | 2015
150126E60773 | Before | 1.5151 | 20.4959 | 1 | Tier 2 | 2021-06-26 | 2015-01-26 | Weather | 412 | 513 | Wind - wires slap/pole down | #2 5/2 AWAC AL | OH CONDUCTOR | 2021 | 2015
150126E60773 | Before | 1.5151 | 20.4959 | 1 | Tier 2 | 2021-06-26 | 2015-01-26 | Weather | 412 | 513 | Wind - wires slap/pole down | #2 5/2 AWAC AL | OH CONDUCTOR | 2021 | 2015
150215E62471 | Before | 5.1836 | 16.8274 | 1 | Tier 3 | 2017-10-26 | 2015-02-15 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2017 | 2015
150217E62559 | Before | 7.2603 | 14.7507 | 1 | Tier 2 | 2015-09-29 | 2015-02-17 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2015 | 2015
150218E62627 | Before | 2.8384 | 19.1726 | 1 | Tier 3 | 2020-02-29 | 2015-02-18 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2020 | 2015
150302E63481 | Before | 5.9507 | 16.0603 | 1 | Tier 3 | 2017-01-19 | 2015-03-02 | Weather | 410 | 515 | Lightning Arrester/Transformer failure | #2 5/2 AWAC AL | JUMPER | 2017 | 2015
150309E63983 | Before | 6.7753 | 15.2356 | 1 | Tier 3 | 2016-03-24 | 2015-03-09 | Customer Contact | 710 | 532 | Vehicle contact | 3/0 15kV Spacer Cable AL | POLE | 2016 | 2015
150319E64881 | Before | 7.789 | 14.2219 | 1 | Tier 2 | 2015-03-20 | 2015-03-19 | Customer Contact | 710 | 532 | Vehicle contact | #2 ACSR AL | POLE | 2015 | 2015
150413E66721 | Before | 2.8575 | 19.1534 | 1 | Tier 2 | 2020-02-22 | 2015-04-13 | Customer Contact | 710 | 532 | Vehicle contact | 636 ACSR AL | POLE | 2020 | 2015
150413E66770 | Before | 2.8575 | 19.1534 | 1 | Tier 2 | 2020-02-22 | 2015-04-13 | Customer Contact | 710 | 532 | Vehicle contact | 636 ACSR AL | POLE | 2020 | 2015
150424E67666 | Before | 6.8685 | 15.1425 | 1 | Tier 2 | 2016-02-19 | 2015-04-24 | Customer Contact | 710 | 532 | Vehicle contact | 636 ACSR AL | POLE | 2016 | 2015
150424E67686 | Before | 5.0767 | 16.9342 | 1 | Tier 3 | 2017-12-04 | 2015-04-24 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2017 | 2015
150424E67690 | Before | 6.8685 | 15.1425 | 1 | Tier 2 | 2016-02-19 | 2015-04-24 | Customer Contact | 710 | 532 | Vehicle contact | 636 ACSR AL | POLE | 2016 | 2015
150508E68794 | Before | 3.8301 | 18.1808 | 1 | Tier 2 | 2019-03-04 | 2015-05-08 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2019 | 2015
150508E68908 | Before | 5.3397 | 16.6712 | 1 | Tier 3 | 2017-08-30 | 2015-05-08 | Equipment | 550 |  | Transformer faulted/mechanical | 336 ACSR AL | TRANSFORMER | 2017 | 2015
150513E69137 | Before | 5.6521 | 16.3589 | 1 | Tier 3 | 2017-05-08 | 2015-05-13 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2017 | 2015
150605E70841 | Before | 3.9753 | 18.0356 | 1 | Tier 2 | 2019-01-10 | 2015-06-05 | Equipment | 522 |  | Fuse overloaded/inadequate fuse size | #2 5/2 AWAC AL | TRANSFORMER | 2019 | 2015
150702E72836 | Before | 3.074 | 18.937 | 1 | Tier 2 | 2019-12-05 | 2015-07-02 | Weather | 404 | 516 | Circ. Flashover/storm/high winds/undet. | #2 5/2 AWAC AL | DEADEND | 2019 | 2015
150707E72990 | Before | 2.3452 | 19.6658 | 1 | Tier 2 | 2020-08-27 | 2015-07-07 | Equipment | 515 |  | OH connector failure (jumper/splice/squeeze-on) | #2 5/2 AWAC AL | JUMPER | 2020 | 2015
150718E73979 | Before | 5.2384 | 16.7726 | 1 | Tier 3 | 2017-10-06 | 2015-07-18 | Weather | 410 | 550 | Lightning Arrester/Transformer failure | #2 5/2 AWAC AL | TRANSFORMER | 2017 | 2015
150718E74018 | Before | 5.6274 | 16.3836 | 1 | Tier 3 | 2017-05-17 | 2015-07-18 | Weather | 410 | 550 | Lightning Arrester/Transformer failure | #2 5/2 AWAC AL | TRANSFORMER | 2017 | 2015
150813E76133 | Before | 3.0137 | 18.9973 | 1 | Tier 2 | 2019-12-27 | 2015-08-13 | Equipment | 515 |  | OH connector failure (jumper/splice/squeeze-on) | 336 ACSR AL | JUMPER | 2019 | 2015
150813E76133 | Before | 3.0137 | 18.9973 | 1 | Tier 2 | 2019-12-27 | 2015-08-13 | Equipment | 515 |  | OH connector failure (jumper/splice/squeeze-on) | 336.4 ACSR AL | JUMPER | 2019 | 2015
150813E76133 | Before | 3.0137 | 18.9973 | 1 | Tier 2 | 2019-12-27 | 2015-08-13 | Equipment | 515 |  | OH connector failure (jumper/splice/squeeze-on) | 636 ACSR AL | JUMPER | 2019 | 2015
150818E76523 | After | 8.0027 | 14.0082 | 1 | Tier 2 | 2015-01-01 | 2015-08-18 | Customer Contact | 710 | 532 | Vehicle contact | 336.4 ACSR AL | POLE | 2015 | 2015
150908E77978 | After | 7.389 | 14.6219 | 1 | Tier 3 | 2015-08-13 | 2015-09-08 | Equipment | 515 |  | OH connector failure (jumper/splice/squeeze-on) | #2 5/2 AWAC AL | JUMPER | 2015 | 2015
150930E79754 | Before | 6 | 16.011 | 1 | Tier 3 | 2017-01-01 | 2015-09-30 | Customer Contact | 710 | 532 | Vehicle contact | #2 ACSR AL | POLE | 2017 | 2015
151004E80026 | After | 8.0027 | 14.0082 | 1 | Tier 2 | 2015-01-01 | 2015-10-04 | Customer Contact | 710 | 532 | Vehicle contact | 4/0 B.STRD CU | POLE | 2015 | 2015
151004E80028 | Before | 5.7397 | 16.2712 | 1 | Tier 3 | 2017-04-06 | 2015-10-04 | Equipment | 518 |  | Cutout failure | #2 5/2 AWAC AL | CUTOUT | 2017 | 2015
151102E81991 | Before | 3.2685 | 18.7425 | 1 | Tier 2 | 2019-09-25 | 2015-11-02 | Equipment | 554 |  | Crossarm failure | #2 5/2 AWAC AL | CROSSARM | 2019 | 2015
151118E83153 | Before | 3.3041 | 18.7068 | 1 | Tier 2 | 2019-09-12 | 2015-11-18 | Customer Contact | 702 | 513 | Heavy equp contact/digin | #2 3/4 AWAC AL | OH CONDUCTOR | 2019 | 2015
160101E85337 | Before | 5.5315 | 16.4795 | 1 | Tier 2 | 2017-06-21 | 2016-01-01 | Equipment | 522 |  | Fuse overloaded/inadequate fuse size | #2 5/2 AWAC AL | FUSE | 2017 | 2016
160101E85337 | After | 9.8438 | 12.1671 | 1 | Tier 2 | 2013-02-28 | 2016-01-01 | Equipment | 522 |  | Fuse overloaded/inadequate fuse size | 336.4 ACSR AL | FUSE | 2013 | 2016
160105E85494 | Before | 5.6027 | 16.4082 | 1 | Tier 3 | 2017-05-26 | 2016-01-05 | Weather | 412 | 513 | Wind - wires slap/pole down | #2 5/2 AWAC AL | OH CONDUCTOR | 2017 | 2016
160105E85494 | Before | 5.6027 | 16.4082 | 1 | Tier 3 | 2017-05-26 | 2016-01-05 | Weather | 412 | 513 | Wind - wires slap/pole down | #2 5/2 AWAC AL | OH CONDUCTOR | 2017 | 2016
160108E85723 | Before | 5.8932 | 16.1178 | 1 | Tier 3 | 2017-02-09 | 2016-01-08 | Equipment | 522 |  | Fuse overloaded/inadequate fuse size | #2 5/2 AWAC AL | FUSE | 2017 | 2016
160131E87248 | After | 7.4329 | 14.5781 | 1 | Tier 3 | 2015-07-28 | 2016-01-31 | Weather | 412 | 513 | Wind - wires slap/pole down | #2 5/2 AWAC AL | OH CONDUCTOR | 2015 | 2016
160131E87248 | After | 7.4329 | 14.5781 | 1 | Tier 3 | 2015-07-28 | 2016-01-31 | Weather | 412 | 513 | Wind - wires slap/pole down | #2 5/2 AWAC AL | OH CONDUCTOR | 2015 | 2016
160227E89496 | Before | 3.0356 | 18.9753 | 1 | Tier 3 | 2019-12-19 | 2016-02-27 | Equipment | 522 |  | Fuse overloaded/inadequate fuse size | #2 5/2 AWAC AL | FUSE | 2019 | 2016
160308E90255 | Before | 4 | 18.011 | 1 | Tier 3 | 2019-01-01 | 2016-03-08 | Equipment | 518 |  | Cutout failure | #2 ACSR AL | CUTOUT | 2019 | 2016
160324E91711 | Before | 4.7425 | 17.2685 | 1 | Tier 3 | 2018-04-05 | 2016-03-24 | Equipment | 518 | 214 | Cutout failure | #2 5/2 AWAC AL | CUTOUT | 2018 | 2016
160328E91923 | Before | 0.74521 | 21.2658 | 1 | Tier 3 | 2022-04-03 | 2016-03-28 | Equipment | 554 |  | Crossarm failure | #2 3/4 AWAC AL | CROSSARM | 2022 | 2016
160328E91923 | Before | 0.74521 | 21.2658 | 1 | Tier 3 | 2022-04-03 | 2016-03-28 | Equipment | 554 |  | Crossarm failure | #2 5/2 AWAC AL | CROSSARM | 2022 | 2016
160328E91923 | Before | 0.7863 | 21.2247 | 1 | Tier 3 | 2022-03-19 | 2016-03-28 | Equipment | 554 |  | Crossarm failure | #2 5/2 AWAC AL | CROSSARM | 2022 | 2016
160329E91928 | Before | 4.5918 | 17.4192 | 1 | Tier 2 | 2018-05-30 | 2016-03-28 | Equipment | 515 |  | OH connector failure (jumper/splice/squeeze-on) | 336 ACSR AL | JUMPER | 2018 | 2016
160407E92648 | Before | 5.2274 | 16.7836 | 1 | Tier 3 | 2017-10-10 | 2016-04-07 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2017 | 2016
160410E92844 | Before | 6.5288 | 15.4822 | 1 | Tier 3 | 2016-06-22 | 2016-04-10 | Weather | 404 | 532 | Circ. Flashover/storm/high winds/undet. | #2 5/2 AWAC AL | POLE | 2016 | 2016
160416E93383 | Before | 5.2274 | 16.7836 | 1 | Tier 3 | 2017-10-10 | 2016-04-16 | Equipment | 550 |  | Transformer faulted/mechanical | #2 5/2 AWAC AL | TRANSFORMER | 2017 | 2016
160430E94487 | After | 8.8356 | 13.1753 | 1 | Tier 3 | 2014-03-03 | 2016-04-30 | Equipment | 502 |  | Arrester (lightning) failure | #2 5/2 AWAC AL | LIGHTNING ARRESTER | 2014 | 2016
160528E96923 | Before | 6 | 16.011 | 1 | Tier 2 | 2017-01-01 | 2016-05-28 | Customer Contact | 710 | 532 | Vehicle contact | 636 ACSR AL | POLE | 2017 | 2016
160618E98585 | Before | 1.074 | 20.937 | 1 | Tier 3 | 2021-12-04 | 2016-06-19 | Equipment | 550 |  | Transformer faulted/mechanical | #2 5/2 AWAC AL | TRANSFORMER | 2021 | 2016
160630E99408 | After | 7.0027 | 15.0082 | 1 | Tier 3 | 2016-01-01 | 2016-06-30 | Equipment | 532 | 214 | Pole broke/rotted/on fire | #2 ACSR AL | POLE | 2016 | 2016
160711E100085 | Before | 4.7425 | 17.2685 | 1 | Tier 3 | 2018-04-05 | 2016-07-11 | Equipment | 502 | 214 | Arrester (lightning) failure | #2 5/2 AWAC AL | LIGHTNING ARRESTER | 2018 | 2016
160809E102395 | Before | 3.5507 | 18.4603 | 1 | Tier 2 | 2019-06-14 | 2016-08-09 | Equipment | 515 |  | OH connector failure (jumper/splice/squeeze-on) | #2 5/2 AWAC AL | JUMPER | 2019 | 2016
160812E102647 | After | 7.0712 | 14.9397 | 1 | Tier 3 | 2015-12-07 | 2016-08-12 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2015 | 2016
160821E103302 | Before | 3.8301 | 18.1808 | 1 | Tier 2 | 2019-03-04 | 2016-08-21 | Equipment | 550 |  | Transformer faulted/mechanical | #2 5/2 AWAC AL | TRANSFORMER | 2019 | 2016
160920E105462 | Before | 4.5945 | 17.4164 | 1 | Tier 3 | 2018-05-29 | 2016-09-20 | Equipment | 550 |  | Transformer faulted/mechanical | #2 5/2 AWAC AL | TRANSFORMER | 2018 | 2016
161009E106862 | Before | 3.2685 | 18.7425 | 1 | Tier 2 | 2019-09-25 | 2016-10-09 | Equipment | 532 | 214 | Pole broke/rotted/on fire | #2 5/2 AWAC AL | POLE | 2019 | 2016
161024E107928 | After | 6.937 | 15.074 | 1 | Tier 3 | 2016-01-25 | 2016-10-24 | Weather | 410 | 550 | Lightning Arrester/Transformer failure | #2 5/2 AWAC AL | TRANSFORMER | 2016 | 2016
161024E108033 | Before | 4.4384 | 17.5726 | 1 | Tier 2 | 2018-07-25 | 2016-10-24 | Equipment | 550 |  | Transformer faulted/mechanical | 336 ACSR AL | LIGHTNING ARRESTER | 2018 | 2016
161124E110161 | Before | 3.0137 | 18.9973 | 1 | Tier 2 | 2019-12-27 | 2016-11-24 | Equipment | 515 | 412 | OH connector failure (jumper/splice/squeeze-on) | 336 ACSR AL | JUMPER | 2019 | 2016
161124E110161 | Before | 3.0137 | 18.9973 | 1 | Tier 2 | 2019-12-27 | 2016-11-24 | Equipment | 515 | 412 | OH connector failure (jumper/splice/squeeze-on) | 336.4 ACSR AL | JUMPER | 2019 | 2016
161124E110161 | Before | 3.0137 | 18.9973 | 1 | Tier 2 | 2019-12-27 | 2016-11-24 | Equipment | 515 | 412 | OH connector failure (jumper/splice/squeeze-on) | 636 ACSR AL | JUMPER | 2019 | 2016
161203E110710 | Before | 3.0548 | 18.9562 | 1 | Tier 3 | 2019-12-12 | 2016-12-03 | Equipment | 522 |  | Fuse overloaded/inadequate fuse size | #2 5/2 AWAC AL | FUSE | 2019 | 2016
161216E111711 | Before | 3.0137 | 18.9973 | 1 | Tier 3 | 2019-12-27 | 2016-12-16 | Equipment | 510 |  | Conductor contact/wire slap | 336 ACSR AL | OH CONDUCTOR | 2019 | 2016
161216E111717 | Before | 4 | 18.011 | 1 | Tier 2 | 2019-01-01 | 2016-12-16 | Equipment | 532 | 550 | Pole broke/rotted/on fire | #2 ACSR AL | POLE | 2019 | 2016
161220E111926 | Before | 3.0137 | 18.9973 | 1 | Tier 3 | 2019-12-27 | 2016-12-20 | Foreign Object | 308 | 513 | Bird contact | 336 ACSR AL | OH CONDUCTOR | 2019 | 2016
161220E111926 | Before | 3.0137 | 18.9973 | 1 | Tier 3 | 2019-12-27 | 2016-12-20 | Foreign Object | 308 | 513 | Bird contact | 336 ACSR AL | OH CONDUCTOR | 2019 | 2016
161228E112311 | Before | 5.6027 | 16.4082 | 1 | Tier 2 | 2017-05-26 | 2016-12-28 | Equipment | 522 |  | Fuse overloaded/inadequate fuse size | #2 5/2 AWAC AL | FUSE | 2017 | 2016
161231E112536 | Before | 3 | 19.011 | 1 | Tier 2 | 2020-01-01 | 2016-12-31 | Equipment | 532 |  | Pole broke/rotted/on fire | 3/0 ACSR AL | POLE | 2020 | 2016
170108E113004 | Before | 5.7589 | 16.2521 | 1 | Tier 3 | 2017-03-30 | 2017-01-08 | Equipment | 522 |  | Fuse overloaded/inadequate fuse size | #2 5/2 AWAC AL | FUSE | 2017 | 2017
170121E113928 | Before | 4.9205 | 17.0904 | 1 | Tier 3 | 2018-01-30 | 2017-01-21 | Weather | 404 | 515 | Circ. Flashover/storm/high winds/undet. | #2 5/2 AWAC AL | JUMPER | 2018 | 2017
170122E114565 | Before | 4.9205 | 17.0904 | 1 | Tier 3 | 2018-01-30 | 2017-01-22 | Equipment | 515 |  | OH connector failure (jumper/splice/squeeze-on) | #2 5/2 AWAC AL | JUMPER | 2018 | 2017
170123E114041 | Before | 5.5068 | 16.5041 | 1 | Tier 3 | 2017-06-30 | 2017-01-23 | Equipment | 532 | 214 | Pole broke/rotted/on fire | #2 5/2 AWAC AL | POLE | 2017 | 2017
170123E114065 | Before | 1.2 | 20.811 | 1 | Tier 3 | 2021-10-19 | 2017-01-23 | Equipment | 532 | 214 | Pole broke/rotted/on fire | #2 5/2 AWAC AL | POLE | 2021 | 2017
170125E114226 | Before | 4.5918 | 17.4192 | 1 | Tier 2 | 2018-05-30 | 2017-01-25 | Equipment | 532 |  | Pole broke/rotted/on fire | #2 5/2 AWAC AL | POLE | 2018 | 2017
170127E114472 | Before | 1.274 | 20.737 | 1 | Tier 3 | 2021-09-22 | 2017-01-27 | Equipment | 528 |  | Hardware failure | #2 5/2 AWAC AL | MISC EQUIPMENT | 2021 | 2017
170128E114540 | Before | 1.2 | 20.811 | 1 | Tier 3 | 2021-10-19 | 2017-01-28 | Equipment | 502 |  | Arrester (lightning) failure | #2 5/2 AWAC AL | LIGHTNING ARRESTER | 2021 | 2017
170203E114945 | Before | 4 | 18.011 | 1 | Tier 2 | 2019-01-01 | 2017-02-03 | Customer Contact | 710 | 532 | Vehicle contact | 1/0 B.STRD CU | POLE | 2019 | 2017
170217E116075 | After | 9.1699 | 12.8411 | 1 | Tier 2 | 2013-11-01 | 2017-02-17 | Equipment | 510 |  | Conductor contact/wire slap | 4/0 B.STRD CU | OH CONDUCTOR | 2013 | 2017
170217E116080 | After | 9.1699 | 12.8411 | 1 | Tier 2 | 2013-11-01 | 2017-02-17 | Weather | 402 | 510 | Circuit Flashover/fog/foreign object | 4/0 B.STRD CU | OH CONDUCTOR | 2013 | 2017
170304E117218 | Before | 3.3014 | 18.7096 | 1 | Tier 2 | 2019-09-13 | 2017-03-04 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2019 | 2017
170311E117743 | Before | 5 | 17.011 | 1 | Tier 2 | 2018-01-01 | 2017-03-11 | Equipment | 528 |  | Hardware failure | #2 ACSR AL | MISC EQUIPMENT | 2018 | 2017
170316E118230 | Before | 2.0712 | 19.9397 | 1 | Tier 3 | 2020-12-05 | 2017-03-16 | Equipment | 550 |  | Transformer faulted/mechanical | #2 5/2 AWAC AL | TRANSFORMER | 2020 | 2017
170329E119156 | Before | 3.0247 | 18.9863 | 1 | Tier 3 | 2019-12-23 | 2017-03-29 | Equipment | 518 |  | Cutout failure | #2 5/2 AWAC AL | CUTOUT | 2019 | 2017
170401E119385 | Before | 3.2329 | 18.7781 | 1 | Tier 2 | 2019-10-08 | 2017-04-01 | Equipment | 522 |  | Fuse overloaded/inadequate fuse size | #2 5/2 AWAC AL | FUSE | 2019 | 2017
170404E119606 | Before | 4.5671 | 17.4438 | 1 | Tier 2 | 2018-06-08 | 2017-04-04 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2018 | 2017
170415E120278 | After | 6 | 16.011 | 1 | Tier 2 | 2017-01-01 | 2017-04-15 | Customer Contact | 710 | 532 | Vehicle contact | #2 ACSR AL | POLE | 2017 | 2017
170416E120281 | Before | 2.4466 | 19.5644 | 1 | Tier 2 | 2020-07-21 | 2017-04-16 | Customer Contact | 710 | 526 | Vehicle contact | #2 5/2 AWAC AL | GUY WIRE | 2020 | 2017
170502E121455 | After | 5.6685 | 16.3425 | 1 | Tier 2 | 2017-05-02 | 2017-05-02 | Customer Contact | 710 | 532 | Vehicle contact | #2 ACSR AL | POLE | 2017 | 2017
170506E121812 | After | 6.3699 | 15.6411 | 1 | Tier 3 | 2016-08-19 | 2017-05-06 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2016 | 2017
170510E122046 | After | 6.7753 | 15.2356 | 1 | Tier 3 | 2016-03-24 | 2017-05-10 | Customer Contact | 710 | 532 | Vehicle contact | 3/0 15kV Spacer Cable AL | POLE | 2016 | 2017
170524E122956 | Before | 5.0767 | 16.9342 | 1 | Tier 3 | 2017-12-04 | 2017-05-24 | Equipment | 554 |  | Crossarm failure | #2 5/2 AWAC AL | CROSSARM | 2017 | 2017
170530E123330 | Before | 2.4356 | 19.5753 | 1 | Tier 3 | 2020-07-25 | 2017-05-30 | Equipment | 518 |  | Cutout failure | #2 5/2 AWAC AL | CUTOUT | 2020 | 2017
170626E125242 | Before | 1.5726 | 20.4384 | 1 | Tier 3 | 2021-06-05 | 2017-06-26 | Equipment | 515 |  | OH connector failure (jumper/splice/squeeze-on) | 336 ACSR AL | JUMPER | 2021 | 2017
170707E126155 | After | 6.6082 | 15.4027 | 1 | Tier 3 | 2016-05-24 | 2017-07-07 | Equipment | 554 | 518 | Crossarm failure | #2 5/2 AWAC AL | CROSSARM | 2016 | 2017
170713E126544 | After | 9.1945 | 12.8164 | 1 | Tier 3 | 2013-10-23 | 2017-07-13 | Equipment | 554 | 214 | Crossarm failure | 3/0 15kV Spacer Cable AL | CROSSARM | 2013 | 2017
170721E127174 | Before | 5.3534 | 16.6575 | 1 | Tier 2 | 2017-08-25 | 2017-07-21 | Crew Contact | 632 | 510 | SDG&E Contr. Crew error | #2 5/2 AWAC AL | OH CONDUCTOR | 2017 | 2017
170805E128336 | Before | 2.0712 | 19.9397 | 1 | Tier 3 | 2020-12-05 | 2017-08-05 | Equipment | 502 |  | Arrester (lightning) failure | #2 5/2 AWAC AL | LIGHTNING ARRESTER | 2020 | 2017
170817E129123 | Before | 1.6521 | 20.3589 | 1 | Tier 2 | 2021-05-07 | 2017-08-17 | Equipment | 532 |  | Pole broke/rotted/on fire | #2 5/2 AWAC AL | POLE | 2021 | 2017
170825E129796 | Before | 4 | 18.011 | 1 | Tier 2 | 2019-01-01 | 2017-08-25 | Customer Contact | 710 | 532 | Vehicle contact | #2 ACSR AL | POLE | 2019 | 2017
170829E130080 | Before | 2.9589 | 19.0521 | 1 | Tier 2 | 2020-01-16 | 2017-08-29 | Equipment | 544 |  | Switch faulted/mechanical | 336.4 ACSR AL | SWITCH | 2020 | 2017
171008E133411 | Before | 1.0082 | 21.0027 | 1 | Tier 3 | 2021-12-28 | 2017-10-08 | Equipment | 522 |  | Fuse overloaded/inadequate fuse size | #2 5/2 AWAC AL | FUSE | 2021 | 2017
171013E133856 | After | 6 | 16.011 | 1 | Tier 3 | 2017-01-01 | 2017-10-13 | Equipment | 532 |  | Pole broke/rotted/on fire | #2 ACSR AL | POLE | 2017 | 2017
171014E133931 | Before | 2.0904 | 19.9205 | 1 | Tier 3 | 2020-11-28 | 2017-10-14 | Customer Contact | 710 | 518 | Vehicle contact | 336 ACSR AL | CUTOUT | 2020 | 2017
171014E133931 | Before | 2.0904 | 19.9205 | 1 | Tier 3 | 2020-11-28 | 2017-10-14 | Customer Contact | 710 | 518 | Vehicle contact | 336 ACSR AL | CUTOUT | 2020 | 2017
171019E134309 | Before | 3.4192 | 18.5918 | 1 | Tier 2 | 2019-08-01 | 2017-10-19 | Equipment | 515 |  | OH connector failure (jumper/splice/squeeze-on) | 636 ACSR AL | CONNECTOR | 2019 | 2017
171019E134309 | Before | 4 | 18.011 | 1 | Tier 2 | 2019-01-01 | 2017-10-19 | Equipment | 515 |  | OH connector failure (jumper/splice/squeeze-on) | 636 ACSR AL | CONNECTOR | 2019 | 2017
171110E135863 | Before | 5.0767 | 16.9342 | 1 | Tier 3 | 2017-12-04 | 2017-11-10 | Equipment | 515 |  | OH connector failure (jumper/splice/squeeze-on) | #2 5/2 AWAC AL | CONNECTOR | 2017 | 2017
171203E137181 | Before | 2.474 | 19.537 | 1 | Tier 2 | 2020-07-11 | 2017-12-03 | Equipment | 542 | 214 | Regulator overloaded/electrical | 336 ACSR AL | REGULATOR | 2020 | 2017
171203E137181 | Before | 1.3863 | 20.6247 | 1 | Tier 2 | 2021-08-12 | 2017-12-03 | Equipment | 542 | 214 | Regulator overloaded/electrical | 336.4 ACSR AL | REGULATOR | 2021 | 2017
171206E137424 | Before | 4.337 | 17.674 | 1 | Tier 2 | 2018-08-31 | 2017-12-06 | Equipment | 532 |  | Pole broke/rotted/on fire | #2 5/2 AWAC AL | POLE | 2018 | 2017
171210E137741 | After | 6 | 16.011 | 1 | Tier 2 | 2017-01-01 | 2017-12-10 | Equipment | 532 |  | Pole broke/rotted/on fire | #2 ACSR AL | POLE | 2017 | 2017
180104E139161 | Before | 4 | 18.011 | 1 | Tier 3 | 2019-01-01 | 2018-01-04 | Equipment | 554 |  | Crossarm failure | #2 ACSR AL | CROSSARM | 2019 | 2018
180109E139437 | Before | 3.1014 | 18.9096 | 1 | Tier 3 | 2019-11-25 | 2018-01-09 | Weather | 404 | 530 | Circ. Flashover/storm/high winds/undet. | 336.4 ACSR AL | INSULATOR | 2019 | 2018
180109E139564 | After | 6.4658 | 15.5452 | 1 | Tier 3 | 2016-07-15 | 2018-01-09 | Weather | 404 | 532 | Circ. Flashover/storm/high winds/undet. | #2 5/2 AWAC AL | POLE | 2016 | 2018
180126E141026 | Before | 4.5178 | 17.4932 | 1 | Tier 2 | 2018-06-26 | 2018-01-26 | Customer Contact | 710 | 513 | Vehicle contact | #2 5/2 AWAC AL | OH CONDUCTOR | 2018 | 2018
180127E141039 | Before | 3.3041 | 18.7068 | 1 | Tier 2 | 2019-09-12 | 2018-01-27 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2019 | 2018
180127E141039 | Before | 3.3041 | 18.7068 | 1 | Tier 2 | 2019-09-12 | 2018-01-27 | Customer Contact | 710 | 532 | Vehicle contact | 336 ACSR AL | POLE | 2019 | 2018
180219E142807 | After | 6.789 | 15.2219 | 1 | Tier 3 | 2016-03-19 | 2018-02-19 | Equipment | 515 |  | OH connector failure (jumper/splice/squeeze-on) | #2 5/2 AWAC AL | JUMPER | 2016 | 2018
180221E143029 | After | 5 | 17.011 | 1 | Tier 3 | 2018-01-01 | 2018-02-21 | Customer Contact | 710 | 532 | Vehicle contact | #2 ACSR AL | POLE | 2018 | 2018
180402E146357 | Before | 3 | 19.011 | 1 | Tier 2 | 2020-01-01 | 2018-04-02 | Equipment | 534 |  | Pothead failure | 636 ACSR AL | POTHEAD | 2020 | 2018
180402E146380 | Before | 3.9753 | 18.0356 | 1 | Tier 2 | 2019-01-10 | 2018-04-02 | Equipment | 516 | 513 | Connector/jumper/splice/elbow/rack | #2 5/2 AWAC AL | DEADEND | 2019 | 2018
180413E147307 | Before | 1.5589 | 20.4521 | 1 | Tier 2 | 2021-06-10 | 2018-04-13 | Equipment | 515 |  | OH connector failure (jumper/splice/squeeze-on) | 336 ACSR AL | JUMPER | 2021 | 2018
180413E147307 | After | 5 | 17.011 | 1 | Tier 2 | 2018-01-01 | 2018-04-13 | Equipment | 515 |  | OH connector failure (jumper/splice/squeeze-on) | #2 ACSR AL | JUMPER | 2018 | 2018
180425E148889 | After | 4.7425 | 17.2685 | 1 | Tier 3 | 2018-04-05 | 2018-04-25 | Equipment | 554 |  | Crossarm failure | #2 5/2 AWAC AL | CROSSARM | 2018 | 2018
180521E150253 | After | 5 | 17.011 | 1 | Tier 3 | 2018-01-01 | 2018-05-21 | Customer Contact | 710 | 532 | Vehicle contact | #2 ACSR AL | POLE | 2018 | 2018
180522E150424 | After | 4.8384 | 17.1726 | 1 | Tier 3 | 2018-03-01 | 2018-05-22 | Foreign Object | 315 | 510 | Balloon contact | 336 ACSR AL | OH CONDUCTOR | 2018 | 2018
180522E150424 | After | 4.8384 | 17.1726 | 1 | Tier 3 | 2018-03-01 | 2018-05-22 | Foreign Object | 315 | 510 | Balloon contact | 336 ACSR AL | OH CONDUCTOR | 2018 | 2018
180601E151051 | After | 4.5945 | 17.4164 | 1 | Tier 3 | 2018-05-29 | 2018-06-01 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2018 | 2018
180607E151560 | After | 6.0877 | 15.9233 | 1 | Tier 3 | 2016-11-30 | 2018-06-07 | Crew Contact | 612 | 510 | SDG&E Crew error | #2 5/2 AWAC AL | OH CONDUCTOR | 2016 | 2018
180614E151981 | After | 5.6521 | 16.3589 | 1 | Tier 3 | 2017-05-08 | 2018-06-14 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2017 | 2018
180627E153108 | After | 8.6603 | 13.3507 | 1 | Tier 2 | 2014-05-06 | 2018-06-27 | Customer Contact | 710 | 532 | Vehicle contact | #2 ACSR AL | POLE | 2014 | 2018
180629E153296 | After | 6.937 | 15.074 | 1 | Tier 3 | 2016-01-25 | 2018-06-29 | Equipment | 520 |  | Fuse holder/fuse cabinet failed | #2 5/2 AWAC AL | FUSE | 2016 | 2018
180629E153296 | After | 5 | 17.011 | 1 | Tier 3 | 2018-01-01 | 2018-06-29 | Equipment | 520 |  | Fuse holder/fuse cabinet failed | #2 ACSR AL | FUSE | 2018 | 2018
180718E154622 | Before | 4 | 18.011 | 1 | Tier 3 | 2019-01-01 | 2018-07-18 | Customer Contact | 710 | 532 | Vehicle contact | #2 ACSR AL | POLE | 2019 | 2018
180720E154896 | Before | 3.9753 | 18.0356 | 1 | Tier 2 | 2019-01-10 | 2018-07-20 | Crew Contact | 612 |  | SDG&E Crew error | #2 5/2 AWAC AL | OH CONDUCTOR | 2019 | 2018
180808E156452 | After | 5 | 17.011 | 1 | Tier 2 | 2018-01-01 | 2018-08-08 | Equipment | 532 |  | Pole broke/rotted/on fire | 3/0 ACSR AL | POLE | 2018 | 2018
180901E158245 | Before | 4 | 18.011 | 1 | Tier 3 | 2019-01-01 | 2018-09-01 | Equipment | 504 |  | Capacitor failure | 1/0 B.STRD CU | CAP BANK | 2019 | 2018
180913E159143 | After | 6.0438 | 15.9671 | 1 | Tier 3 | 2016-12-16 | 2018-09-13 | Equipment | 520 |  | Fuse holder/fuse cabinet failed | #2 5/2 AWAC AL | FUSE | 2016 | 2018
180918E159433 | After | 4.4384 | 17.5726 | 1 | Tier 3 | 2018-07-25 | 2018-09-18 | Equipment | 502 |  | Arrester (lightning) failure | #2 5/2 AWAC AL | LIGHTNING ARRESTER | 2018 | 2018
180930E160277 | After | 5 | 17.011 | 1 | Tier 2 | 2018-01-01 | 2018-09-30 | Customer Contact | 710 | 532 | Vehicle contact | 394.5 5005 AL | POLE | 2018 | 2018
181004E160561 | After | 5.8932 | 16.1178 | 1 | Tier 3 | 2017-02-09 | 2018-10-04 | Equipment | 550 |  | Transformer faulted/mechanical | #2 5/2 AWAC AL | TRANSFORMER | 2017 | 2018
181012E161307 | After | 5.7397 | 16.2712 | 1 | Tier 3 | 2017-04-06 | 2018-10-12 | Weather | 410 |  | Lightning Arrester/Transformer failure | #2 5/2 AWAC AL |  | 2017 | 2018
181015E161463 | After | 7.0329 | 14.9781 | 1 | Tier 2 | 2015-12-21 | 2018-10-15 | Equipment | 518 |  | Cutout failure | #2 5/2 AWAC AL | CUTOUT | 2015 | 2018
181126E164103 | Before | 3.0137 | 18.9973 | 1 | Tier 3 | 2019-12-27 | 2018-11-26 | Foreign Object | 304 | 510 | Animal contact | 336 ACSR AL | OH CONDUCTOR | 2019 | 2018
181126E164103 | Before | 3.0137 | 18.9973 | 1 | Tier 3 | 2019-12-27 | 2018-11-26 | Foreign Object | 304 | 510 | Animal contact | 336 ACSR AL | OH CONDUCTOR | 2019 | 2018
181206E164866 | After | 6.6082 | 15.4027 | 1 | Tier 3 | 2016-05-24 | 2018-12-06 | Weather | 404 | 554 | Circ. Flashover/storm/high winds/undet. | #2 5/2 AWAC AL | CROSSARM | 2016 | 2018
181209E165022 | After | 7.2192 | 14.7918 | 1 | Tier 3 | 2015-10-14 | 2018-12-09 | Equipment | 520 |  | Fuse holder/fuse cabinet failed | #2 5/2 AWAC AL | FUSE | 2015 | 2018
190106E166576 | After | 7.2411 | 14.7699 | 1 | Tier 2 | 2015-10-06 | 2019-01-06 | Equipment | 516 |  | Connector/jumper/splice/elbow/rack | 636 ACSR AL | DEADEND | 2015 | 2019
190126E168081 | After | 4 | 18.011 | 1 | Tier 3 | 2019-01-01 | 2019-01-26 | Equipment | 532 |  | Pole broke/rotted/on fire | #2 ACSR AL | POLE | 2019 | 2019
190126E168083 | Before | 2.2822 | 19.7288 | 1 | Tier 3 | 2020-09-19 | 2019-01-26 | Equipment | 518 |  | Cutout failure | 336 ACSR AL | CUTOUT | 2020 | 2019
190210E169221 | Before | 3 | 19.011 | 1 | Tier 2 | 2020-01-01 | 2019-02-10 | Equipment | 532 |  | Pole broke/rotted/on fire | #2 ACSR AL | POLE | 2020 | 2019
190306E171047 | After | 5.7397 | 16.2712 | 1 | Tier 3 | 2017-04-06 | 2019-03-06 | Weather | 410 |  | Lightning Arrester/Transformer failure | #2 5/2 AWAC AL |  | 2017 | 2019
190306E171048 | After | 5.8055 | 16.2055 | 1 | Tier 3 | 2017-03-13 | 2019-03-06 | Weather | 410 |  | Lightning Arrester/Transformer failure | #2 5/2 AWAC AL |  | 2017 | 2019
190314E171590 | After | 9.1945 | 12.8164 | 1 | Tier 3 | 2013-10-23 | 2019-03-14 | Equipment | 528 |  | Hardware failure | 3/0 15kV Spacer Cable AL | MISC EQUIPMENT | 2013 | 2019
190314E171666 | After | 4.3562 | 17.6548 | 1 | Tier 3 | 2018-08-24 | 2019-03-14 | Foreign Object | 315 | 510 | Balloon contact | #2 5/2 AWAC AL | OH CONDUCTOR | 2018 | 2019
190314E171666 | After | 4.3562 | 17.6548 | 1 | Tier 3 | 2018-08-24 | 2019-03-14 | Foreign Object | 315 | 510 | Balloon contact | #2 5/2 AWAC AL | OH CONDUCTOR | 2018 | 2019
190422E174540 | After | 5.3726 | 16.6384 | 1 | Tier 3 | 2017-08-18 | 2019-04-22 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2017 | 2019
190430E175503 | After | 10.0027 | 12.0082 | 1 | Tier 3 | 2013-01-01 | 2019-04-30 | Equipment | 532 | 214 | Pole broke/rotted/on fire | 636 ACSR AL | POLE | 2013 | 2019
190501E175209 | Before | 1.2411 | 20.7699 | 1 | Tier 3 | 2021-10-04 | 2019-05-01 | Equipment | 532 | 214 | Pole broke/rotted/on fire | #2 5/2 AWAC AL | POLE | 2021 | 2019
190507E175374 | Before | 1.2466 | 20.7644 | 1 | Tier 3 | 2021-10-02 | 2019-05-07 | Equipment | 532 |  | Pole broke/rotted/on fire | 336 ACSR AL | POLE | 2021 | 2019
190518E176609 | After | 4 | 18.011 | 1 | Tier 2 | 2019-01-01 | 2019-05-18 | Equipment | 532 |  | Pole broke/rotted/on fire | #2 ACSR AL | POLE | 2019 | 2019
190530E177367 | After | 4.7425 | 17.2685 | 1 | Tier 3 | 2018-04-05 | 2019-05-30 | Equipment | 515 |  | OH connector failure (jumper/splice/squeeze-on) | #2 5/2 AWAC AL | JUMPER | 2018 | 2019
190601E177485 | After | 6.6137 | 15.3973 | 1 | Tier 3 | 2016-05-22 | 2019-06-01 | Equipment | 550 |  | Transformer faulted/mechanical | #2 5/2 AWAC AL | TRANSFORMER | 2016 | 2019
190602E177510 | After | 6.4384 | 15.5726 | 1 | Tier 3 | 2016-07-25 | 2019-06-02 | Foreign Object | 308 | 510 | Bird contact | #2 5/2 AWAC AL | OH CONDUCTOR | 2016 | 2019
190602E177510 | After | 6.4384 | 15.5726 | 1 | Tier 3 | 2016-07-25 | 2019-06-02 | Foreign Object | 308 | 510 | Bird contact | #2 5/2 AWAC AL | OH CONDUCTOR | 2016 | 2019
190611E178155 | After | 6.2027 | 15.8082 | 1 | Tier 3 | 2016-10-19 | 2019-06-11 | Customer Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2016 | 2019
190624E179238 | Before | 2.6849 | 19.326 | 1 | Tier 3 | 2020-04-25 | 2019-06-24 | Equipment | 532 |  | Pole broke/rotted/on fire | #2 5/2 AWAC AL | POLE | 2020 | 2019
190624E179238 | Before | 3.0356 | 18.9753 | 1 | Tier 3 | 2019-12-19 | 2019-06-24 | Equipment | 532 |  | Pole broke/rotted/on fire | #2 5/2 AWAC AL | POLE | 2019 | 2019
190705E179942 | Before | 1.1315 | 20.8795 | 1 | Tier 2 | 2021-11-13 | 2019-07-05 | Equipment | 515 |  | OH connector failure (jumper/splice/squeeze-on) | 336 ACSR AL | JUMPER | 2021 | 2019
190724E181355 | After | 7.9014 | 14.1096 | 1 | Tier 3 | 2015-02-07 | 2019-07-24 | Equipment | 530 |  | Insulator/pin failure/wire floating | #2 5/2 AWAC AL | INSULATOR | 2015 | 2019
190724E181355 | After | 7.9014 | 14.1096 | 1 | Tier 3 | 2015-02-07 | 2019-07-24 | Equipment | 530 |  | Insulator/pin failure/wire floating | 336 ACSR AL | INSULATOR | 2015 | 2019
190821E183342 | Before | 3 | 19.011 | 1 | Tier 2 | 2020-01-01 | 2019-08-21 | Equipment | 532 |  | Pole broke/rotted/on fire | 3/0 ACSR AL | POLE | 2020 | 2019
190825E183659 | After | 6.6192 | 15.3918 | 1 | Tier 3 | 2016-05-20 | 2019-08-25 | Equipment | 550 |  | Transformer faulted/mechanical | #2 5/2 AWAC AL | TRANSFORMER | 2016 | 2019
190904E184396 | After | 5.6027 | 16.4082 | 1 | Tier 3 | 2017-05-26 | 2019-09-04 | Equipment | 515 |  | OH connector failure (jumper/splice/squeeze-on) | #2 5/2 AWAC AL | JUMPER | 2017 | 2019
190906E184668 | Before | 3.3041 | 18.7068 | 1 | Tier 2 | 2019-09-12 | 2019-09-06 | Customer Contact | 710 | 532 | Vehicle contact | 336 ACSR AL | POLE | 2019 | 2019
190922E185771 | After | 4 | 18.011 | 1 | Tier 2 | 2019-01-01 | 2019-09-22 | Customer Contact | 710 | 532 | Vehicle contact | 3/0 ACSR AL | POLE | 2019 | 2019
190926E186095 | After | 4 | 18.011 | 1 | Tier 3 | 2019-01-01 | 2019-09-26 | Equipment | 515 |  | OH connector failure (jumper/splice/squeeze-on) | #2 ACSR AL | OH CONDUCTOR | 2019 | 2019
191112E190179 | After | 4.8384 | 17.1726 | 1 | Tier 3 | 2018-03-01 | 2019-11-12 | Customer Contact | 704 | 510 | Line fault/tree trimming | #2 5/2 AWAC AL | OH CONDUCTOR | 2018 | 2019
191114E190358 | After | 4 | 18.011 | 1 | Tier 3 | 2019-01-01 | 2019-11-14 | Customer Contact | 710 | 532 | Vehicle contact | #2 ACSR AL | POLE | 2019 | 2019
191126E191432 | Before | 0.7863 | 21.2247 | 1 | Tier 3 | 2022-03-19 | 2019-11-26 | Equipment | 554 |  | Crossarm failure | #2 5/2 AWAC AL | CROSSARM | 2022 | 2019
191126E191432 | After | 4 | 18.011 | 1 | Tier 3 | 2019-01-01 | 2019-11-26 | Equipment | 554 |  | Crossarm failure | #2 3/4 AWAC AL | CROSSARM | 2019 | 2019
191128E191563 | Before | 3.0137 | 18.9973 | 1 | Tier 2 | 2019-12-27 | 2019-11-28 | Equipment | 515 |  | OH connector failure (jumper/splice/squeeze-on) | 336 ACSR AL | LINE DISC | 2019 | 2019
191128E191563 | Before | 3.0137 | 18.9973 | 1 | Tier 2 | 2019-12-27 | 2019-11-28 | Equipment | 515 |  | OH connector failure (jumper/splice/squeeze-on) | 336.4 ACSR AL | LINE DISC | 2019 | 2019
191217E192684 | After | 6.4521 | 15.5589 | 1 | Tier 3 | 2016-07-20 | 2019-12-17 | Equipment | 534 |  | Pothead failure | #2 5/2 AWAC AL | POTHEAD | 2016 | 2019
191218E192724 | After | 6 | 16.011 | 1 | Tier 3 | 2017-01-01 | 2019-12-18 | Equipment | 532 |  | Pole broke/rotted/on fire | #2 ACSR AL | POLE | 2017 | 2019
200109E193979 | After | 3 | 19.011 | 1 | Tier 2 | 2020-01-01 | 2020-01-09 | Third Party Contact | 702 | 532 | Heavy equipment contact/dig-in | #2 5/2 AWAC AL | POLE | 2020 | 2020
200209E198469 | After | 3.6274 | 18.3836 | 1 | Tier 2 | 2019-05-17 | 2020-02-09 | Third Party Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2019 | 2020
200210E196515 | Before | 2.7233 | 19.2877 | 1 | Tier 2 | 2020-04-11 | 2020-02-10 | Equipment | 528 |  | Hardware failure | #2 5/2 AWAC AL | MISC EQUIPMENT | 2020 | 2020
200210E196559 | Before | 2.7233 | 19.2877 | 1 | Tier 2 | 2020-04-11 | 2020-02-10 | Equipment | 528 |  | Hardware failure | #2 5/2 AWAC AL | MISC EQUIPMENT | 2020 | 2020
200226E197846 | Before | 1.8356 | 20.1753 | 1 | Tier 3 | 2021-03-01 | 2020-02-26 | Equipment | 515 |  | OH connector failure (jumper/splice/squeeze-on) | 636 ACSR AL | JUMPER | 2021 | 2020
200226E197846 | Before | 2.2849 | 19.726 | 1 | Tier 3 | 2020-09-18 | 2020-02-26 | Equipment | 515 |  | OH connector failure (jumper/splice/squeeze-on) | 636 ACSR AL | JUMPER | 2020 | 2020
200307E198704 | After | 3 | 19.011 | 1 | Tier 3 | 2020-01-01 | 2020-03-07 | Equipment | 532 |  | Pole - contact/damage/broke/rotted/on fire | #2 ACSR AL | POLE | 2020 | 2020
200323E199904 | After | 3.2329 | 18.7781 | 1 | Tier 2 | 2019-10-08 | 2020-03-23 | Equipment | 502 |  | Arrester failure | #2 5/2 AWAC AL | LIGHTNING ARRESTER | 2019 | 2020
200324E199920 | After | 5.6438 | 16.3671 | 1 | Tier 3 | 2017-05-11 | 2020-03-24 | Equipment | 518 |  | Cutout failure | 336 ACSR AL | CUTOUT | 2017 | 2020
200327E200351 | After | 6.5068 | 15.5041 | 1 | Tier 3 | 2016-06-30 | 2020-03-27 | Equipment | 554 |  | Crossarm failure/contact | #2 5/2 AWAC AL | CROSSARM | 2016 | 2020
200328E200376 | After | 7.789 | 14.2219 | 1 | Tier 2 | 2015-03-20 | 2020-03-28 | Third Party Contact | 710 | 532 | Vehicle contact | #2 ACSR AL | POLE | 2015 | 2020
200401E200765 | After | 6.4658 | 15.5452 | 1 | Tier 3 | 2016-07-15 | 2020-04-01 | Third Party Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2016 | 2020
200428E203022 | Before | 2.2438 | 19.7671 | 1 | Tier 3 | 2020-10-03 | 2020-04-28 | Equipment | 532 |  | Pole - contact/damage/broke/rotted/on fire | #2 5/2 AWAC AL | POLE | 2020 | 2020
200428E203051 | Before | 1.2 | 20.811 | 1 | Tier 3 | 2021-10-19 | 2020-04-28 | Equipment | 550 |  | Transformer (station) failure/contact | #2 5/2 AWAC AL | TRANSFORMER | 2021 | 2020
200520E205214 | Before | 1.7836 | 20.2274 | 1 | Tier 3 | 2021-03-20 | 2020-05-20 | Equipment | 532 |  | Pole - contact/damage/broke/rotted/on fire | #2 5/2 AWAC AL | POLE | 2021 | 2020
200615E207298 | After | 3 | 19.011 | 1 | Tier 3 | 2020-01-01 | 2020-06-15 | Third Party Contact | 710 | 532 | Vehicle contact | #2 ACSR AL | POLE | 2020 | 2020
200615E207816 | After | 3 | 19.011 | 1 | Tier 3 | 2020-01-01 | 2020-06-15 | Third Party Contact | 710 | 532 | Vehicle contact | #2 ACSR AL | POLE | 2020 | 2020
200619E207750 | After | 3 | 19.011 | 1 | Tier 3 | 2020-01-01 | 2020-06-19 | Third Party Contact | 710 | 532 | Vehicle contact | #2 ACSR AL | POLE | 2020 | 2020
200701E208687 | Before | 1.5151 | 20.4959 | 1 | Tier 3 | 2021-06-26 | 2020-07-01 | Equipment | 515 | 214 | OH connector failure (jumper/splice/squeeze-on) | #2 5/2 AWAC AL | CONNECTOR | 2021 | 2020
200712E209371 | Before | 0.74521 | 21.2658 | 1 | Tier 3 | 2022-04-03 | 2020-07-12 | Equipment | 532 |  | Pole - contact/damage/broke/rotted/on fire | #2 5/2 AWAC AL | POLE | 2022 | 2020
200723E210343 | Before | 2.2822 | 19.7288 | 1 | Tier 3 | 2020-09-19 | 2020-07-23 | Foreign Object | 314 | 510 | Foreign object | 336 ACSR AL | OH CONDUCTOR | 2020 | 2020
200723E210343 | Before | 2.2822 | 19.7288 | 1 | Tier 3 | 2020-09-19 | 2020-07-23 | Foreign Object | 314 | 510 | Foreign object | 336 ACSR AL | OH CONDUCTOR | 2020 | 2020
200724E210540 | Before | 2.3205 | 19.6904 | 1 | Tier 3 | 2020-09-05 | 2020-07-24 | SDGE/Contractor Contact | 632 | 314 | SDG&E contractor crew error | #2 3/4 AWAC AL | OH CONDUCTOR | 2020 | 2020
200724E210572 | After | 2.6466 | 19.3644 | 1 | Tier 2 | 2020-05-09 | 2020-07-24 | Miscellaneous | 226 |  | Protection misoperation (UFO, settings, fuse miscoordination) | #2 5/2 AWAC AL |  | 2020 | 2020
200730E211164 | After | 6.5836 | 15.4274 | 1 | Tier 3 | 2016-06-02 | 2020-07-30 | Weather | 404 | 522 | Undetermined (severe weather) | #2 5/2 AWAC AL | FUSE | 2016 | 2020
200731E211253 | Before | 2.3397 | 19.6712 | 1 | Tier 2 | 2020-08-29 | 2020-07-31 | SDGE/Contractor Contact | 632 | 515 | SDG&E contractor crew error | #2 5/2 AWAC AL | CONNECTOR | 2020 | 2020
200814E212426 | After | 4 | 18.011 | 1 | Tier 2 | 2019-01-01 | 2020-08-14 | Weather | 404 | 536 | Undetermined (severe weather) | 336.4 ACSR AL | SERVICE RESTORER | 2019 | 2020
200826E213445 | After | 7.1151 | 14.8959 | 1 | Tier 3 | 2015-11-21 | 2020-08-26 | Equipment | 522 |  | Fuse - overload/inadequate size/fatigue | #2 5/2 AWAC AL | FUSE | 2015 | 2020
200901E213927 | After | 7.6603 | 14.3507 | 1 | Tier 2 | 2015-05-06 | 2020-09-01 | Equipment | 554 | 214 | Crossarm failure/contact | 336.4 ACSR AL | CROSSARM | 2015 | 2020
200905E214319 | Before | 1.9479 | 20.063 | 1 | Tier 3 | 2021-01-19 | 2020-09-05 | Miscellaneous | 206 | 214 | Fire/smoke | #2 3/4 AWAC AL |  | 2021 | 2020
200906E214500 | After | 9.6685 | 12.3425 | 1 | Tier 2 | 2013-05-03 | 2020-09-06 | Equipment | 536 |  | Recloser/service restorer failure/contact | #2 ACSR AL | SERVICE RESTORER | 2013 | 2020
200906E214500 | After | 8.0301 | 13.9808 | 1 | Tier 2 | 2014-12-22 | 2020-09-06 | Equipment | 536 |  | Recloser/service restorer failure/contact | #2 5/2 AWAC AL | SERVICE RESTORER | 2014 | 2020
200915E215145 | After | 3 | 19.011 | 1 | Tier 3 | 2020-01-01 | 2020-09-15 | Equipment | 532 |  | Pole - contact/damage/broke/rotted/on fire | #2 5/2 AWAC AL | POLE | 2020 | 2020
201015E217715 | After | 9.1589 | 12.8521 | 1 | Tier 2 | 2013-11-05 | 2020-10-15 | Equipment | 540 | 214 | Regulator failure/contact | 636 ACSR AL | REGULATOR | 2013 | 2020
201019E218117 | Before | 1.7836 | 20.2274 | 1 | Tier 3 | 2021-03-20 | 2020-10-19 | SDGE/Contractor Contact | 628 | 528 | SDG&E contractor personnel contact | #2 5/2 AWAC AL | MISC EQUIPMENT | 2021 | 2020
201019E218129 | After | 8.0027 | 14.0082 | 1 | Tier 2 | 2015-01-01 | 2020-10-19 | Equipment | 502 |  | Arrester failure | #2 ACSR AL | LIGHTNING ARRESTER | 2015 | 2020
201026E218739 | Before | 1.1123 | 20.8986 | 1 | Tier 3 | 2021-11-20 | 2020-10-26 | SDGE/Contractor Contact | 612 | 536 | SDG&E Crew error | #2 5/2 AWAC AL | SERVICE RESTORER | 2021 | 2020
201026E218739 | Before | 1.1123 | 20.8986 | 1 | Tier 3 | 2021-11-20 | 2020-10-26 | SDGE/Contractor Contact | 612 | 536 | SDG&E Crew error | 336 ACSR AL | SERVICE RESTORER | 2021 | 2020
201106E219939 | After | 7.2027 | 14.8082 | 1 | Tier 3 | 2015-10-20 | 2020-11-06 | Equipment | 518 |  | Cutout failure | #2 5/2 AWAC AL | CUTOUT | 2015 | 2020
201106E219939 | Before | 1.2411 | 20.7699 | 1 | Tier 3 | 2021-10-04 | 2020-11-06 | Equipment | 518 |  | Cutout failure | #2 5/2 AWAC AL | CUTOUT | 2021 | 2020
201120E221015 | After | 2.7041 | 19.3068 | 1 | Tier 3 | 2020-04-18 | 2020-11-20 | Equipment | 550 |  | Transformer (station) failure/contact | #2 5/2 AWAC AL | TRANSFORMER | 2020 | 2020
201120E221064 | Before | 2.0904 | 19.9205 | 1 | Tier 3 | 2020-11-28 | 2020-11-20 | SDGE/Contractor Contact | 632 | 513 | SDG&E contractor crew error | 336 ACSR AL | OH CONDUCTOR | 2020 | 2020
201126E221302 | After | 3.0247 | 18.9863 | 1 | Tier 3 | 2019-12-23 | 2020-11-26 | Equipment | 522 |  | Fuse - overload/inadequate size/fatigue | #2 5/2 AWAC AL | FUSE | 2019 | 2020
201205E222501 | After | 6.7671 | 15.2438 | 1 | Tier 3 | 2016-03-27 | 2020-12-05 | Equipment | 522 |  | Fuse - overload/inadequate size/fatigue | #2 5/2 AWAC AL | FUSE | 2016 | 2020
201205E222501 | Before | 1.9233 | 20.0877 | 1 | Tier 3 | 2021-01-28 | 2020-12-05 | Equipment | 522 |  | Fuse - overload/inadequate size/fatigue | #2 5/2 AWAC AL | FUSE | 2021 | 2020
201205E222502 | After | 6.7671 | 15.2438 | 1 | Tier 3 | 2016-03-27 | 2020-12-05 | Equipment | 522 |  | Fuse - overload/inadequate size/fatigue | #2 5/2 AWAC AL | FUSE | 2016 | 2020
201205E222502 | Before | 1.9233 | 20.0877 | 1 | Tier 3 | 2021-01-28 | 2020-12-05 | Equipment | 522 |  | Fuse - overload/inadequate size/fatigue | #2 5/2 AWAC AL | FUSE | 2021 | 2020
210114E224077 | After | 1.9973 | 20.0137 | 1 | Tier 2 | 2021-01-01 | 2021-01-14 | Third Party Contact | 710 | 532 | Vehicle contact | 336.4 ACSR AL | POLE | 2021 | 2021
210115E224155 | After | 7.7342 | 14.2767 | 1 | Tier 3 | 2015-04-09 | 2021-01-15 | Equipment | 518 |  | Cutout failure | #2 5/2 AWAC AL | CUTOUT | 2015 | 2021
210125E224920 | After | 1.9973 | 20.0137 | 1 | Tier 3 | 2021-01-01 | 2021-01-25 | Third Party Contact | 710 | 532 | Vehicle contact | #2 ACSR AL | POLE | 2021 | 2021
210125E224964 | Before | 1.6247 | 20.3863 | 1 | Tier 3 | 2021-05-17 | 2021-01-25 | Weather | 408 | 528 | Ice/snow/equipment failure (severe weather) | #2 3/4 AWAC AL | MISC EQUIPMENT | 2021 | 2021
210125E224971 | After | 8.0027 | 14.0082 | 1 | Tier 3 | 2015-01-01 | 2021-01-25 | Weather | 412 | 513 | Wire slap/pole down/wire down (severe weather) | #2 5/2 AWAC AL | OH CONDUCTOR | 2015 | 2021
210125E224971 | After | 8.0027 | 14.0082 | 1 | Tier 3 | 2015-01-01 | 2021-01-25 | Weather | 412 | 513 | Wire slap/pole down/wire down (severe weather) | #2 5/2 AWAC AL | OH CONDUCTOR | 2015 | 2021
210127E225156 | After | 4.7425 | 17.2685 | 1 | Tier 3 | 2018-04-05 | 2021-01-27 | Weather | 408 | 534 | Ice/snow/equipment failure (severe weather) | #2 5/2 AWAC AL | POTHEAD | 2018 | 2021
210208E226035 | After | 6.6137 | 15.3973 | 1 | Tier 3 | 2016-05-22 | 2021-02-08 | Equipment | 502 |  | Arrester failure | #2 5/2 AWAC AL | LIGHTNING ARRESTER | 2016 | 2021
210309E228262 | After | 7.6411 | 14.3699 | 1 | Tier 2 | 2015-05-13 | 2021-03-09 | Equipment | 515 |  | OH connector failure (jumper/splice/squeeze-on) | #2 ACSR AL | JUMPER | 2015 | 2021
210318E228965 | After | 5.3836 | 16.6274 | 1 | Tier 3 | 2017-08-14 | 2021-03-18 | Third Party Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2017 | 2021
210319E229140 | Before | 1.6247 | 20.3863 | 1 | Tier 3 | 2021-05-17 | 2021-03-19 | Equipment | 534 |  | Pothead failure | #2 3/4 AWAC AL | POTHEAD | 2021 | 2021
210323E229340 | After | 5.0767 | 16.9342 | 1 | Tier 3 | 2017-12-04 | 2021-03-23 | Third Party Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2017 | 2021
210401E230180 | After | 4.6082 | 17.4027 | 1 | Tier 3 | 2018-05-24 | 2021-04-01 | Equipment | 554 |  | Crossarm failure/contact | 636 ACSR AL | CROSSARM | 2018 | 2021
210423E231957 | After | 10.0027 | 12.0082 | 1 | Tier 2 | 2013-01-01 | 2021-04-23 | Third Party Contact | 710 | 532 | Vehicle contact | 394.5 5005 AL | POLE | 2013 | 2021
210519E233865 | Before | 1.611 | 20.4 | 1 | Tier 2 | 2021-05-22 | 2021-05-19 | SDGE/Contractor Contact | 622 | 512 | SDG&E contractor heavy equipment contact/dig-in | #2 5/2 AWAC AL | UG CABLE | 2021 | 2021
210603E234826 | After | 6.4521 | 15.5589 | 1 | Tier 3 | 2016-07-20 | 2021-06-03 | SDGE/Contractor Contact | 632 |  | SDG&E contractor crew error | #2 5/2 AWAC AL |  | 2016 | 2021
210608E235079 | After | 7.7918 | 14.2192 | 1 | Tier 3 | 2015-03-19 | 2021-06-08 | Third Party Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2015 | 2021
210608E235143 | After | 6.811 | 15.2 | 1 | Tier 3 | 2016-03-11 | 2021-06-08 | Equipment | 544 |  | Switch failure/contact | #2 5/2 AWAC AL | SWITCH | 2016 | 2021
210608E235143 | After | 6.811 | 15.2 | 1 | Tier 3 | 2016-03-11 | 2021-06-08 | Equipment | 544 |  | Switch failure/contact | 336 ACSR AL | SWITCH | 2016 | 2021
210610E235279 | After | 1.9973 | 20.0137 | 1 | Tier 2 | 2021-01-01 | 2021-06-10 | Third Party Contact | 710 | 532 | Vehicle contact | 4/0 B.STRD CU | POLE | 2021 | 2021
210621E236094 | After | 7.1479 | 14.863 | 1 | Tier 3 | 2015-11-09 | 2021-06-21 | Third Party Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2015 | 2021
210622E236214 | After | 5.6685 | 16.3425 | 1 | Tier 2 | 2017-05-02 | 2021-06-22 | Third Party Contact | 710 | 532 | Vehicle contact | #2 ACSR AL | POLE | 2017 | 2021
210625E236536 | After | 4.5178 | 17.4932 | 1 | Tier 2 | 2018-06-26 | 2021-06-25 | Equipment | 518 |  | Cutout failure | #2 5/2 AWAC AL | CUTOUT | 2018 | 2021
210715E237971 | Before | 1.0795 | 20.9315 | 1 | Tier 2 | 2021-12-02 | 2021-07-15 | Third Party Contact | 710 | 550 | Vehicle contact | 336 ACSR AL | TRANSFORMER | 2021 | 2021
210722E238579 | After | 7.1534 | 14.8575 | 1 | Tier 3 | 2015-11-07 | 2021-07-22 | Third Party Contact | 702 | 526 | Heavy equipment contact/dig-in | #2 5/2 AWAC AL | GUY WIRE | 2015 | 2021
210731E239266 | After | 7.0712 | 14.9397 | 1 | Tier 3 | 2015-12-07 | 2021-07-31 | Weather | 410 | 550 | Lightning/arrester/xfmr failure (severe weather) | #2 5/2 AWAC AL | TRANSFORMER | 2015 | 2021
210815E240343 | After | 5.0767 | 16.9342 | 1 | Tier 3 | 2017-12-04 | 2021-08-15 | Third Party Contact | 710 | 532 | Vehicle contact | #2 5/2 AWAC AL | POLE | 2017 | 2021
210816E240448 | After | 9.8438 | 12.1671 | 1 | Tier 2 | 2013-02-28 | 2021-08-16 | Third Party Contact | 710 | 532 | Vehicle contact | #2 ACSR AL | POLE | 2013 | 2021
210825E241106 | After | 6.063 | 15.9479 | 1 | Tier 2 | 2016-12-09 | 2021-08-25 | Equipment | 515 |  | OH connector failure (jumper/splice/squeeze-on) | 636 ACSR AL | JUMPER | 2016 | 2021
210829E241340 | Before | 1.2082 | 20.8027 | 1 | Tier 3 | 2021-10-16 | 2021-08-29 | Equipment | 532 |  | Pole - contact/damage/broke/rotted/on fire | #2 5/2 AWAC AL | POLE | 2021 | 2021
210829E241340 | Before | 1.2082 | 20.8027 | 1 | Tier 3 | 2021-10-16 | 2021-08-29 | Equipment | 532 |  | Pole - contact/damage/broke/rotted/on fire | #2 ACSR AL | POLE | 2021 | 2021
210829E241355 | After | 3 | 19.011 | 1 | Tier 2 | 2020-01-01 | 2021-08-29 | Weather | 410 | 550 | Lightning/arrester/xfmr failure (severe weather) | #2 ACSR AL | TRANSFORMER | 2020 | 2021
210829E241363 | After | 5.7836 | 16.2274 | 1 | Tier 2 | 2017-03-21 | 2021-08-29 | Weather | 410 |  | Lightning/arrester/xfmr failure (severe weather) | #2 5/2 AWAC AL |  | 2017 | 2021
210829E241370 | After | 5.6027 | 16.4082 | 1 | Tier 3 | 2017-05-26 | 2021-08-29 | Weather | 410 |  | Lightning/arrester/xfmr failure (severe weather) | #2 5/2 AWAC AL |  | 2017 | 2021
210829E241370 | After | 5.5068 | 16.5041 | 1 | Tier 3 | 2017-06-30 | 2021-08-29 | Weather | 410 |  | Lightning/arrester/xfmr failure (severe weather) | #2 5/2 AWAC AL |  | 2017 | 2021
210911E242274 | After | 8.0027 | 14.0082 | 1 | Tier 3 | 2015-01-01 | 2021-09-11 | Third Party Contact | 710 | 532 | Vehicle contact | #2 ACSR AL | POLE | 2015 | 2021
210913E242342 | After | 3 | 19.011 | 1 | Tier 2 | 2020-01-01 | 2021-09-13 | Third Party Contact | 710 | 532 | Vehicle contact | #2 ACSR AL | POLE | 2020 | 2021
210924E243248 | After | 8.0493 | 13.9616 | 1 | Tier 3 | 2014-12-15 | 2021-09-24 | Weather | 410 | 502 | Lightning/arrester/xfmr failure (severe weather) | #2 5/2 AWAC AL | LIGHTNING ARRESTER | 2014 | 2021
211009E244508 | After | 4 | 18.011 | 1 | Tier 3 | 2019-01-01 | 2021-10-09 | Third Party Contact | 710 | 526 | Vehicle contact | #2 ACSR AL | GUY WIRE | 2019 | 2021
211129E247841 | After | 9.2959 | 12.7151 | 1 | Tier 2 | 2013-09-16 | 2021-11-29 | Third Party Contact | 710 | 532 | Vehicle contact | #2 ACSR AL | POLE | 2013 | 2021
211214E248894 | After | 4 | 18.011 | 1 | Tier 3 | 2019-01-01 | 2021-12-14 | Weather | 404 |  | Undetermined (severe weather) | #2 ACSR AL |  | 2019 | 2021
220211E252701 | After | 6.4 | 15.611 | 1 | Tier 2 | 2016-08-08 | 2022-02-11 | Equipment | 566 | 214 | Disconnect Failure | 636 ACSR AL | LINE DISC | 2016 | 2022
220221E253353 | After | 7.4329 | 14.5781 | 1 | Tier 3 | 2015-07-28 | 2022-02-21 | Equipment | 515 |  | OH connector failure (jumper/splice/squeeze-on) | #2 5/2 AWAC AL | JUMPER | 2015 | 2022
220307E254439 | After | 6.5288 | 15.4822 | 1 | Tier 2 | 2016-06-22 | 2022-03-07 | Equipment | 550 |  | Transformer (station) failure/contact | #2 5/2 AWAC AL | TRANSFORMER | 2016 | 2022
220407E256919 | After | 1.2411 | 20.7699 | 1 | Tier 3 | 2021-10-04 | 2022-04-07 | Equipment | 515 | 214 | OH connector failure (jumper/splice/squeeze-on) | #2 5/2 AWAC AL | JUMPER | 2021 | 2022
220414E257452 | After | 4.7425 | 17.2685 | 1 | Tier 3 | 2018-04-05 | 2022-04-14 | Equipment | 515 | 214 | OH connector failure (jumper/splice/squeeze-on) | #2 5/2 AWAC AL | JUMPER | 2018 | 2022
220523E260150 | After | 4 | 18.011 | 1 | Tier 3 | 2019-01-01 | 2022-05-23 | Third Party Contact | 710 | 532 | Vehicle contact | #2 ACSR AL | POLE | 2019 | 2022
220609E261405 | After | 6.7753 | 15.2356 | 1 | Tier 3 | 2016-03-24 | 2022-06-09 | Third Party Contact | 710 | 532 | Vehicle contact | 3/0 15kV Spacer Cable AL | POLE | 2016 | 2022
220629E262819 | After | 5 | 17.011 | 1 | Tier 3 | 2018-01-01 | 2022-06-29 | Miscellaneous | 226 | 308 | Protection misoperation (UFO, settings, fuse miscoordination) | #2 ACSR AL | TRANSFORMER | 2018 | 2022
220804E265294 | After | 7.0027 | 15.0082 | 1 | Tier 2 | 2016-01-01 | 2022-08-04 | Equipment | 534 |  | Pothead failure | 3/0 ACSR AL | POTHEAD | 2016 | 2022
220813E265991 | After | 9.9068 | 12.1041 | 1 | Tier 3 | 2013-02-05 | 2022-08-13 | Weather | 410 | 550 | Lightning/arrester/xfmr failure (severe weather) | #2 5/2 AWAC AL | TRANSFORMER | 2013 | 2022
220826E266975 | After | 2.2301 | 19.7808 | 1 | Tier 2 | 2020-10-08 | 2022-08-26 | Equipment | 504 | 214 | Capacitor/cap bank failure | 336.4 ACSR AL | Capacitor | 2020 | 2022
220831E267275 | After | 2.3014 | 19.7096 | 1 | Tier 3 | 2020-09-12 | 2022-08-31 | Miscellaneous | 206 | 532 | Fire/smoke | 336 ACSR AL | POLE | 2020 | 2022
220831E267275 | After | 2.4548 | 19.5562 | 1 | Tier 3 | 2020-07-18 | 2022-08-31 | Miscellaneous | 206 | 532 | Fire/smoke | #2 5/2 AWAC AL | POLE | 2020 | 2022
220909E268116 | After | 7.1205 | 14.8904 | 1 | Tier 3 | 2015-11-19 | 2022-09-09 | Weather | 426 | 550 | Tree/branch or palm trunk fell on line or equipment (severe weather) | #2 ACSR AL | TRANSFORMER | 2015 | 2022
220909E268116 | After | 7.0685 | 14.9425 | 1 | Tier 3 | 2015-12-08 | 2022-09-09 | Weather | 426 | 550 | Tree/branch or palm trunk fell on line or equipment (severe weather) | #2 5/2 AWAC AL | TRANSFORMER | 2015 | 2022
221011E270413 | After | 6.6137 | 15.3973 | 1 | Tier 3 | 2016-05-22 | 2022-10-11 | Weather | 410 | 502 | Lightning/arrester/xfmr failure (severe weather) | #2 5/2 AWAC AL | Arrestor | 2016 | 2022
221029E271770 | After | 8.0027 | 14.0082 | 1 | Tier 2 | 2015-01-01 | 2022-10-29 | Equipment | 510 | 513 | Conductor contact/failure/overload/wire slap | 2/0 B.STRD CU | Conductor, OH | 2015 | 2022
221124E273544 | After | 6.6575 | 15.3534 | 1 | Tier 3 | 2016-05-06 | 2022-11-24 | Weather | 420 | 510 | Tree sway contact due to high wind (severe weather) | #2 5/2 AWAC AL | Conductor, OH | 2016 | 2022
221208E274398 | After | 7.5945 | 14.4164 | 1 | Tier 3 | 2015-05-30 | 2022-12-08 | Equipment | 502 |  | Arrester failure | #2 5/2 AWAC AL | Arrestor | 2015 | 2022

## Summary
Project Id | Unhardened Faults | Unhardened years | Unhardned faults per operating year Average | Hardened Faults | Hardened years | Hardned faults per operating year Average | Poles
0078-D | 4 | 16.6712 | 0.23993 | 0 | 5.3397 | 0 | 26
0078-E | 1 | 15.2329 | 0.065647 | 0 | 6.7781 | 0 | 8
0078-G | 1 | 16.674 | 0.059974 | 0 | 5.337 | 0 | 28
0079-A | 2 | 15.2219 | 0.13139 | 1 | 6.789 | 0.1473 | 34
0079-M | 2 | 15.2356 | 0.13127 | 2 | 6.7753 | 0.29519 | 18
0079-P | 1 | 14.9315 | 0.066972 | 0 | 7.0795 | 0 | 45
0157-CC | 2 | 19.9397 | 0.1003 | 0 | 2.0712 | 0 | 8
0157-D | 1 | 20.7644 | 0.048159 | 0 | 1.2466 | 0 | 39
0157-G | 3 | 20.4384 | 0.14678 | 0 | 1.5726 | 0 | 42
0157-H | 1 | 19.7096 | 0.050737 | 0 | 2.3014 | 0 | 37
0157-I | 0 | 19.5562 | 0 | 0 | 2.4548 | 0 | 23
0157-K | 2 | 19.5753 | 0.10217 | 0 | 2.4356 | 0 | 45
0157-L | 1 | 20.1205 | 0.0497 | 0 | 1.8904 | 0 | 39
0157-M | 1 | 19.0384 | 0.052526 | 0 | 2.9726 | 0 | 37
0157-T | 2 | 18.9562 | 0.10551 | 0 | 3.0548 | 0 | 8
0157-U | 1 | 19.3068 | 0.051795 | 1 | 2.7041 | 0.36981 | 30
0157-V | 1 | 20.2082 | 0.049485 | 0 | 1.8027 | 0 | 48
0157-W | 7 | 19.1726 | 0.3651 | 0 | 2.8384 | 0 | 35
0157-X | 2 | 21.3123 | 0.093842 | 0 | 0.69863 | 0 | 32
0175-A | 1 | 16.0603 | 0.062265 | 0 | 5.9507 | 0 | 40
0175-B | 2 | 16.3068 | 0.12265 | 0 | 5.7041 | 0 | 30
0175-C | 1 | 16.2521 | 0.061531 | 0 | 5.7589 | 0 | 39
0175-D | 0 | 16.1178 | 0 | 1 | 5.8932 | 0.16969 | 17
0175-E | 1 | 15.8274 | 0.063182 | 0 | 6.1836 | 0 | 9
0176-A | 1 | 16.2712 | 0.061458 | 2 | 5.7397 | 0.34845 | 32
0176-C | 2 | 16.1178 | 0.12409 | 0 | 5.8932 | 0 | 24
0176-D | 1 | 18.0356 | 0.055446 | 0 | 3.9753 | 0 | 24
0176-F | 0 | 17.6548 | 0 | 1 | 4.3562 | 0.22956 | 31
0176-H | 2 | 18.0356 | 0.11089 | 0 | 3.9753 | 0 | 17
0176-J | 2 | 16.3836 | 0.12207 | 0 | 5.6274 | 0 | 23
0176-L | 1 | 20.4959 | 0.04879 | 0 | 1.5151 | 0 | 14
0185-CAMINITO_A_CASA | 1 | 19.5644 | 0.051113 | 0 | 2.4466 | 0 | 4
0212-A | 6 | 18.9973 | 0.31584 | 0 | 3.0137 | 0 | 70
0212-B | 6 | 18.9973 | 0.31584 | 0 | 3.0137 | 0 | 46
0212-C-PH-02 | 3 | 19.9205 | 0.1506 | 0 | 2.0904 | 0 | 46
0212-C-PH-03 | 1 | 19.9205 | 0.050199 | 0 | 2.0904 | 0 | 12
0212-D | 3 | 19.7288 | 0.15206 | 0 | 2.2822 | 0 | 35
0212-E | 3 | 19.537 | 0.15355 | 0 | 2.474 | 0 | 69
0212-F | 1 | 19.5562 | 0.051135 | 0 | 2.4548 | 0 | 38
0212-J | 1 | 20.8795 | 0.047894 | 0 | 1.1315 | 0 | 54
0212-P | 1 | 19.9014 | 0.050248 | 0 | 2.1096 | 0 | 61
0212-U | 3 | 20.4575 | 0.14665 | 0 | 1.5534 | 0 | 75
0212-V | 1 | 19.326 | 0.051744 | 0 | 2.6849 | 0 | 56
0212-W | 2 | 19.326 | 0.10349 | 0 | 2.6849 | 0 | 40
0212-W-FT-02 | 1 | 19.3233 | 0.051751 | 0 | 2.6877 | 0 | 10
0212-X | 2 | 20.4959 | 0.097581 | 0 | 1.5151 | 0 | 30
0215-A | 3 | 17.4932 | 0.1715 | 1 | 4.5178 | 0.22135 | 27
0215-B | 3 | 17.4438 | 0.17198 | 0 | 4.5671 | 0 | 30
0215-C | 2 | 18.6877 | 0.10702 | 0 | 3.3233 | 0 | 30
0215-E (ASD) | 1 | 17.463 | 0.057264 | 0 | 4.5479 | 0 | 2
0217-A | 4 | 18.9863 | 0.21068 | 0 | 3.0247 | 0 | 43
0217-AD | 1 | 19.326 | 0.051744 | 0 | 2.6849 | 0 | 5
0217-B | 1 | 17.6466 | 0.056668 | 0 | 4.3644 | 0 | 23
0217-C | 2 | 17.1726 | 0.11646 | 1 | 4.8384 | 0.20668 | 37
0217-D | 4 | 18.9753 | 0.2108 | 0 | 3.0356 | 0 | 33
0217-E | 2 | 18.9753 | 0.1054 | 0 | 3.0356 | 0 | 37
0217-G | 1 | 17.674 | 0.05658 | 0 | 4.337 | 0 | 18
0217-H | 2 | 18.2685 | 0.10948 | 0 | 3.7425 | 0 | 28
0217-J | 3 | 18.4603 | 0.16251 | 0 | 3.5507 | 0 | 26
0217-M | 2 | 18.1808 | 0.11001 | 0 | 3.8301 | 0 | 31
0217-N | 1 | 18.1041 | 0.055236 | 0 | 3.9068 | 0 | 29
0217-P | 1 | 18.2685 | 0.054739 | 0 | 3.7425 | 0 | 27
0217-Q | 1 | 18.4603 | 0.05417 | 0 | 3.5507 | 0 | 32
0217-R | 5 | 18.7096 | 0.26724 | 0 | 3.3014 | 0 | 26
0217-W (ASD) | 1 | 18.7397 | 0.053363 | 0 | 3.2712 | 0 | 1
0217-X (ASD) | 1 | 18.937 | 0.052807 | 0 | 3.074 | 0 | 5
0220-C | 1 | 15.2767 | 0.065459 | 0 | 6.7342 | 0 | 18
0220-K | 2 | 15.789 | 0.12667 | 0 | 6.2219 | 0 | 28
0220-N | 3 | 15.8274 | 0.18954 | 0 | 6.1836 | 0 | 28
0220-Q | 2 | 16.3425 | 0.12238 | 0 | 5.6685 | 0 | 11
0221-A | 4 | 17.2685 | 0.23164 | 4 | 4.7425 | 0.84344 | 32
0221-D-VOLCAN MTN | 1 | 19.6904 | 0.050786 | 0 | 2.3205 | 0 | 20
0221-F | 2 | 17.4164 | 0.11483 | 1 | 4.5945 | 0.21765 | 36
0221-G | 2 | 17.0904 | 0.11702 | 0 | 4.9205 | 0 | 22
0221-I | 1 | 16.3863 | 0.061027 | 0 | 5.6247 | 0 | 32
0221-J | 1 | 16.0055 | 0.062479 | 0 | 6.0055 | 0 | 36
0221-L | 0 | 15.9671 | 0 | 1 | 6.0438 | 0.16546 | 30
0221-N | 1 | 15.9671 | 0.062629 | 0 | 6.0438 | 0 | 38
0221-O | 1 | 17.3644 | 0.057589 | 0 | 4.6466 | 0 | 14
0221-S | 1 | 17.6767 | 0.056572 | 0 | 4.3342 | 0 | 30
0221-T | 1 | 17.5753 | 0.056898 | 0 | 4.4356 | 0 | 24
0221-V | 1 | 15.9233 | 0.062801 | 1 | 6.0877 | 0.16427 | 27
0221-Y-PH1-SLAUGHTER | 0 | 17.5726 | 0 | 1 | 4.4384 | 0.22531 | 2
0222-AA | 3 | 16.5945 | 0.18078 | 0 | 5.4164 | 0 | 30
0222-BB | 0 | 15.2438 | 0 | 2 | 6.7671 | 0.29555 | 10
0222-DD | 1 | 20.0356 | 0.049911 | 0 | 1.9753 | 0 | 5
0222-EE | 1 | 19.8247 | 0.050442 | 0 | 2.1863 | 0 | 27
0222-FF | 7 | 21.2658 | 0.32917 | 0 | 0.74521 | 0 | 35
0222-FF-PH-02 | 4 | 21.2247 | 0.18846 | 0 | 0.7863 | 0 | 15
0222-HH | 1 | 19.3644 | 0.051641 | 0 | 2.6466 | 0 | 6
0222-II | 1 | 19.7671 | 0.050589 | 0 | 2.2438 | 0 | 38
0222-JJ | 1 | 19.7863 | 0.05054 | 0 | 2.2247 | 0 | 23
0222-K | 2 | 15.5452 | 0.12866 | 2 | 6.4658 | 0.30932 | 32
0222-LL | 2 | 20.2274 | 0.098876 | 0 | 1.7836 | 0 | 46
0222-MM | 2 | 19.7288 | 0.10137 | 0 | 2.2822 | 0 | 43
0222-PP | 2 | 20.8986 | 0.0957 | 0 | 1.1123 | 0 | 46
0222-R | 3 | 15.2795 | 0.19634 | 0 | 6.7315 | 0 | 45
0222-S | 1 | 15.1753 | 0.065896 | 0 | 6.8356 | 0 | 19
0222-U | 1 | 15.5726 | 0.064215 | 1 | 6.4384 | 0.15532 | 36
0222-UU | 1 | 20.8027 | 0.048071 | 0 | 1.2082 | 0 | 8
0222-Z | 1 | 16.3671 | 0.061098 | 1 | 5.6438 | 0.17718 | 26
0230-B | 3 | 18.0356 | 0.16634 | 0 | 3.9753 | 0 | 50
0230-C | 5 | 18.0356 | 0.27723 | 0 | 3.9753 | 0 | 39
0230-D | 4 | 18.0767 | 0.22128 | 0 | 3.9342 | 0 | 43
0230-E | 2 | 17.4411 | 0.11467 | 0 | 4.5699 | 0 | 22
0230-I | 1 | 20.4 | 0.04902 | 0 | 1.611 | 0 | 10
0236-B | 0 | 15.8082 | 0 | 1 | 6.2027 | 0.16122 | 37
0237-C | 3 | 15.5452 | 0.19299 | 0 | 6.4658 | 0 | 27
0237-F | 0 | 15.074 | 0 | 2 | 6.937 | 0.28831 | 26
0237-G | 1 | 17.1726 | 0.058232 | 0 | 4.8384 | 0 | 26
0237-I | 1 | 18.9863 | 0.05267 | 1 | 3.0247 | 0.33062 | 28
0237-O | 1 | 15.4274 | 0.06482 | 1 | 6.5836 | 0.15189 | 40
0237-Q | 1 | 15.4274 | 0.06482 | 0 | 6.5836 | 0 | 28
0240-B | 2 | 15.3918 | 0.12994 | 1 | 6.6192 | 0.15108 | 32
0240-C | 1 | 15.1562 | 0.06598 | 0 | 6.8548 | 0 | 24
0240-D | 2 | 15.5589 | 0.12854 | 0 | 6.4521 | 0 | 23
0240-G | 1 | 17.7616 | 0.056301 | 0 | 4.2493 | 0 | 33
0350-A | 1 | 17.3781 | 0.057544 | 0 | 4.6329 | 0 | 30
0350-E | 1 | 18.5918 | 0.053787 | 0 | 3.4192 | 0 | 32
0350-F | 2 | 18.7781 | 0.10651 | 1 | 3.2329 | 0.30932 | 42
0350-G | 2 | 17.7452 | 0.11271 | 0 | 4.2658 | 0 | 26
0350-K | 1 | 18.0712 | 0.055337 | 0 | 3.9397 | 0 | 32
0350-L | 3 | 18.7425 | 0.16006 | 0 | 3.2685 | 0 | 11
0350-M | 1 | 18.7425 | 0.053355 | 0 | 3.2685 | 0 | 5
0358-C | 1 | 15.4027 | 0.064924 | 2 | 6.6082 | 0.30265 | 31
0358-D | 1 | 14.8575 | 0.067306 | 1 | 7.1534 | 0.13979 | 27
0441-CFSP | 1 | 15.8055 | 0.063269 | 0 | 6.2055 | 0 | 26
0442-D | 3 | 14.8959 | 0.2014 | 1 | 7.1151 | 0.14055 | 12
0444-A | 2 | 20.4521 | 0.09779 | 0 | 1.5589 | 0 | 38
0444-B | 1 | 20.4575 | 0.048882 | 0 | 1.5534 | 0 | 20
0445-C | 1 | 17.5671 | 0.056925 | 0 | 4.4438 | 0 | 42
0445-E | 2 | 19.3644 | 0.10328 | 0 | 2.6466 | 0 | 56
0445-G | 1 | 17.4301 | 0.057372 | 0 | 4.5808 | 0 | 3
0445-N | 4 | 18.3836 | 0.21759 | 1 | 3.6274 | 0.27568 | 36
0445-O | 5 | 19.6712 | 0.25418 | 0 | 2.3397 | 0 | 27
0445-Q | 2 | 20.9753 | 0.09535 | 0 | 1.0356 | 0 | 63
0445-R | 2 | 20.9945 | 0.095263 | 0 | 1.0164 | 0 | 38
0445-U | 2 | 18.7068 | 0.10691 | 0 | 3.3041 | 0 | 26
0448-A | 1 | 20.7644 | 0.048159 | 0 | 1.2466 | 0 | 15
0520-B | 1 | 16.6575 | 0.060033 | 0 | 5.3534 | 0 | 49
0520-C | 1 | 16.6356 | 0.060112 | 0 | 5.3753 | 0 | 28
0520-D | 1 | 16.4795 | 0.060682 | 0 | 5.5315 | 0 | 31
0520-F | 5 | 17.5726 | 0.28453 | 0 | 4.4384 | 0 | 60
0520-H | 1 | 17.1342 | 0.058363 | 0 | 4.8767 | 0 | 33
0520-I | 2 | 17.1342 | 0.11673 | 0 | 4.8767 | 0 | 54
0520-L | 3 | 17.4438 | 0.17198 | 0 | 4.5671 | 0 | 50
0520-N | 1 | 17.5726 | 0.056907 | 0 | 4.4384 | 0 | 45
0908-D | 3 | 18.8356 | 0.15927 | 0 | 3.1753 | 0 | 38
0908-E | 3 | 18.7068 | 0.16037 | 0 | 3.3041 | 0 | 33
0908-F | 1 | 19.6658 | 0.05085 | 0 | 2.3452 | 0 | 37
0908-H | 2 | 19.2877 | 0.10369 | 0 | 2.7233 | 0 | 8
0971-A | 4 | 16.4082 | 0.24378 | 0 | 5.6027 | 0 | 35
0971-B | 2 | 17.3808 | 0.11507 | 0 | 4.6301 | 0 | 44
0971-C | 1 | 16.7726 | 0.059621 | 0 | 5.2384 | 0 | 31
0971-D | 1 | 16.7726 | 0.059621 | 0 | 5.2384 | 0 | 43
0971-E | 1 | 16.1945 | 0.061749 | 0 | 5.8164 | 0 | 20
0971-G | 2 | 16.3014 | 0.12269 | 0 | 5.7096 | 0 | 34
0971-I | 1 | 16.5041 | 0.060591 | 0 | 5.5068 | 0 | 27
0971-J | 1 | 16.4082 | 0.060945 | 2 | 5.6027 | 0.35697 | 33
0971-K | 0 | 16.5041 | 0 | 1 | 5.5068 | 0.18159 | 21
0971-M | 2 | 17.1726 | 0.11646 | 1 | 4.8384 | 0.20668 | 32
0971-Q | 3 | 20.937 | 0.14329 | 0 | 1.074 | 0 | 51
0972-A | 1 | 16.5014 | 0.060601 | 0 | 5.5096 | 0 | 33
0972-C | 2 | 16.2055 | 0.12342 | 1 | 5.8055 | 0.17225 | 26
0972-D | 0 | 16.2274 | 0 | 1 | 5.7836 | 0.1729 | 24
0974-B | 6 | 16.9342 | 0.35431 | 2 | 5.0767 | 0.39396 | 29
0974-C | 6 | 16.7836 | 0.35749 | 0 | 5.2274 | 0 | 27
0974-D | 1 | 16.8274 | 0.059427 | 0 | 5.1836 | 0 | 38
1030-B | 1 | 15.5589 | 0.064272 | 2 | 6.4521 | 0.30998 | 17
1030-C | 3 | 16.3589 | 0.18339 | 1 | 5.6521 | 0.17693 | 42
1030-F | 2 | 16.6384 | 0.1202 | 1 | 5.3726 | 0.18613 | 44
1030-J | 4 | 16.8986 | 0.23671 | 0 | 5.1123 | 0 | 42
1030-N | 1 | 16.6274 | 0.060142 | 1 | 5.3836 | 0.18575 | 44
1030-O | 2 | 16.3589 | 0.12226 | 0 | 5.6521 | 0 | 58
1030-T | 0 | 15.6411 | 0 | 1 | 6.3699 | 0.15699 | 7
1030-U | 2 | 16.8877 | 0.11843 | 0 | 5.1233 | 0 | 41
1458-B | 2 | 16.389 | 0.12203 | 0 | 5.6219 | 0 | 33
2052284 | 3 | 20.3863 | 0.14716 | 0 | 1.6247 | 0 | 127
2308440 | 1 | 13.6986 | 0.073 | 0 | 8.3123 | 0 | 8
2317030 | 1 | 13.389 | 0.074688 | 0 | 8.6219 | 0 | 20
2351870 | 2 | 15.1425 | 0.13208 | 0 | 6.8685 | 0 | 27
2352101 | 0 | 14.3699 | 0 | 1 | 7.6411 | 0.13087 | 9
2367811 | 0 | 13.3507 | 0 | 1 | 8.6603 | 0.11547 | 2
2376476 | 1 | 14.5671 | 0.068648 | 0 | 7.4438 | 0 | 3
2378982 | 1 | 14.3342 | 0.069763 | 0 | 7.6767 | 0 | 17
2378983 | 1 | 14.0055 | 0.071401 | 0 | 8.0055 | 0 | 11
2379320 | 2 | 14.4082 | 0.13881 | 0 | 7.6027 | 0 | 28
2402507 | 1 | 14.6247 | 0.068378 | 0 | 7.3863 | 0 | 3
2414910 | 0 | 15.611 | 0 | 1 | 6.4 | 0.15625 | 8
2430984 | 2 | 14.2219 | 0.14063 | 1 | 7.789 | 0.12839 | 2
2434453 | 1 | 18.4575 | 0.054178 | 0 | 3.5534 | 0 | 25
2574755 | 3 | 19.0521 | 0.15746 | 0 | 2.9589 | 0 | 9
2587010 | 2 | 20.1753 | 0.099131 | 0 | 1.8356 | 0 | 46
2920310 | 0 | 12.3425 | 0 | 1 | 9.6685 | 0.10343 | 12
2929264 | 2 | 12.1507 | 0.1646 | 0 | 9.8603 | 0 | 32
2931350 | 1 | 12.1671 | 0.082189 | 1 | 9.8438 | 0.10159 | 47
2936510 | 1 | 12.1041 | 0.082617 | 1 | 9.9068 | 0.10094 | 30
2936972 | 0 | 15.9479 | 0 | 1 | 6.063 | 0.16493 | 20
2937450 | 1 | 18.9096 | 0.052883 | 0 | 3.1014 | 0 | 47
2940070 | 1 | 12.8521 | 0.077809 | 1 | 9.1589 | 0.10918 | 24
2940100 | 4 | 14.3507 | 0.27873 | 1 | 7.6603 | 0.13054 | 31
2947900 | 0 | 12.5096 | 0 | 1 | 9.5014 | 0.10525 | 11
2952820 | 2 | 18.5918 | 0.10757 | 0 | 3.4192 | 0 | 35
2959260 | 2 | 13.0493 | 0.15326 | 0 | 8.9616 | 0 | 2
2959830 | 2 | 12.9342 | 0.15463 | 0 | 9.0767 | 0 | 20
2961130 | 1 | 15.1397 | 0.066051 | 0 | 6.8712 | 0 | 12
2961750 | 0 | 12.1671 | 0 | 1 | 9.8438 | 0.10159 | 4
2963330 | 0 | 12.7151 | 0 | 1 | 9.2959 | 0.10757 | 2
2966980 | 0 | 17.4027 | 0 | 1 | 4.6082 | 0.217 | 7
2967170 | 8 | 13.1753 | 0.60719 | 1 | 8.8356 | 0.11318 | 39
2968050 | 0 | 12.8411 | 0 | 2 | 9.1699 | 0.21811 | 3
2969070 | 0 | 12.6603 | 0 | 1 | 9.3507 | 0.10694 | 6
2982181 | 1 | 14.7699 | 0.067705 | 1 | 7.2411 | 0.1381 | 12
300000428477 | 2 | 21.0027 | 0.095226 | 0 | 1.0082 | 0 | 39
300000433006 | 4 | 20.3589 | 0.19647 | 0 | 1.6521 | 0 | 25
300000433322 | 1 | 20.6247 | 0.048486 | 0 | 1.3863 | 0 | 2
448O CC-FIRE-01 | 1 | 17.4192 | 0.057408 | 0 | 4.5918 | 0 | 25
448T | 1 | 20.737 | 0.048223 | 0 | 1.274 | 0 | 10
448YY | 3 | 20.811 | 0.14415 | 0 | 1.2 | 0 | 8
456168-510 | 1 | 13.3863 | 0.074703 | 0 | 8.6247 | 0 | 2
530000025615 | 0 | 14.8904 | 0 | 1 | 7.1205 | 0.14044 | 2
530000053574 | 1 | 15.5041 | 0.064499 | 1 | 6.5068 | 0.15368 | 19
530000073064 | 0 | 16.3425 | 0 | 2 | 5.6685 | 0.35283 | 2
530000149264 | 1 | 18.9315 | 0.052822 | 0 | 3.0795 | 0 | 3
530000162846 | 2 | 19.1534 | 0.10442 | 0 | 2.8575 | 0 | 5
530000186859 | 0 | 19.7808 | 0 | 1 | 2.2301 | 0.4484 | 8
530000203440 | 0 | 20.063 | 0 | 0 | 1.9479 | 0 | 8
530000298293 | 1 | 21.8329 | 0.045802 | 0 | 0.17808 | 0 | 2
79N | 1 | 21.4493 | 0.046622 | 0 | 0.56164 | 0 | 4
C1001-SF_ADDL_WRK | 1 | 20.9288 | 0.047781 | 0 | 1.0822 | 0 | 7
C1023/C354_NEW_12KV_RECON | 2 | 20.9315 | 0.09555 | 0 | 1.0795 | 0 | 81
C1215 MAINLINE CFSP W/S R1 | 1 | 14.3397 | 0.069736 | 0 | 7.6712 | 0 | 16
C157:2013 CFSP CNF RIDGEPI | 2 | 13.5973 | 0.14709 | 0 | 8.4137 | 0 | 3
C212: 2013 FIRE HARDENING | 1 | 14.6521 | 0.06825 | 0 | 7.3589 | 0 | 6
C220 PH 2 I RECONDUCT R8 | 2 | 14.6712 | 0.13632 | 0 | 7.3397 | 0 | 50
C220 PH 2 L RECONDUCT R1 | 1 | 14.5589 | 0.068686 | 0 | 7.4521 | 0 | 29
C220 PH 2 O RECONDUCTOR | 1 | 14.8822 | 0.067194 | 0 | 7.1288 | 0 | 15
C220 PH 4 D POLE CHGOUT | 0 | 13.9616 | 0 | 1 | 8.0493 | 0.12423 | 14
C221 PH4 #B POLE REPLA R1 | 0 | 14.4164 | 0 | 1 | 7.5945 | 0.13167 | 19
C221 PH4 D POLE REPLA R2 | 1 | 15.3973 | 0.064947 | 3 | 6.6137 | 0.4536 | 4
C221:ERI 2012 REBUILD IM R9 | 0 | 12.8164 | 0 | 2 | 9.1945 | 0.21752 | 11
C222 FIRE RISK MITIG PRJPH | 1 | 14.1233 | 0.070805 | 0 | 7.8877 | 0 | 75
C222 FIRE RISK MITIG PRO R1 | 0 | 14.1096 | 0 | 1 | 7.9014 | 0.12656 | 15
C222 PH 1 F RECONDUCTOR | 1 | 15.2 | 0.065789 | 1 | 6.811 | 0.14682 | 25
C222 PH 1 H RECONDUC R1 | 0 | 14.863 | 0 | 1 | 7.1479 | 0.1399 | 12
C222 PH 1 I RECONDUC R7 | 0 | 14.6219 | 0 | 1 | 7.389 | 0.13534 | 23
C222 PH 1 P RECONDUC R7 | 1 | 14.4219 | 0.069339 | 0 | 7.589 | 0 | 22
C222 PH 2 #T RECONDU R11 | 2 | 14.8548 | 0.13464 | 0 | 7.1562 | 0 | 23
C222 PH4 SEC2 CPOLE CHGOU | 4 | 14.3342 | 0.27905 | 0 | 7.6767 | 0 | 29
C222 PH4 SEC2 DPOLE CH R1 | 2 | 14.0055 | 0.1428 | 0 | 8.0055 | 0 | 22
C230: 2013 FIRE HARDNG 4 R2 | 1 | 14.3123 | 0.06987 | 0 | 7.6986 | 0 | 2
C233 LONG SPAN EVAL P61 R18 | 1 | 13.9808 | 0.071527 | 1 | 8.0301 | 0.12453 | 3
C236 PH 2 D RECONDUCTOR | 2 | 15.4822 | 0.12918 | 1 | 6.5288 | 0.15317 | 33
C237 PH 2 D RECONDUCT R1 | 2 | 14.5781 | 0.13719 | 1 | 7.4329 | 0.13454 | 37
C237 PH 2 E RECONDUCTOR | 1 | 14.4795 | 0.069063 | 0 | 7.5315 | 0 | 23
C237 PH 2 H RECONDUCT R8 | 1 | 14.6247 | 0.068378 | 0 | 7.3863 | 0 | 24
C237 PH 2 J RECONDUCTOR | 1 | 14.5781 | 0.068596 | 1 | 7.4329 | 0.13454 | 24
C237 PH 2 M RECONDUCTOR | 2 | 14.663 | 0.1364 | 0 | 7.3479 | 0 | 41
C239:2013 RIRAT RELIABILITY | 1 | 14.5753 | 0.068609 | 0 | 7.4356 | 0 | 12
C240 PH 2 E RECONDUCT R1 | 0 | 14.9425 | 0 | 1 | 7.0685 | 0.14147 | 28
C358 PH 2 A RECONDUCTOR | 0 | 14.7918 | 0 | 1 | 7.2192 | 0.13852 | 9
C358 PH 2 B RECONDUCTOR | 1 | 14.6192 | 0.068403 | 0 | 7.3918 | 0 | 14
C442 PH 4 BPOLE CHGOUT R1 | 0 | 14.2767 | 0 | 1 | 7.7342 | 0.1293 | 25
C442 PH 4 EPOLE CHGOUT R7 | 1 | 13.8027 | 0.072449 | 0 | 8.2082 | 0 | 4
C442 PH 4 FPOLE CHGOUT R1 | 0 | 15.3534 | 0 | 1 | 6.6575 | 0.15021 | 42
C442 PH 4 GPOLE CHGOUT R1 | 0 | 14.9397 | 0 | 2 | 7.0712 | 0.28284 | 8
C444 BRANCHLN CFSP P4 R1 | 3 | 14.9616 | 0.20051 | 0 | 7.0493 | 0 | 17
C444 BRANCHLN CFSP W/S R1 | 1 | 14.4055 | 0.069418 | 0 | 7.6055 | 0 | 5
C444 BRANCHLN PH1 P41936 | 1 | 14.389 | 0.069497 | 0 | 7.6219 | 0 | 13
C444 BRANCHLN PH2 P4196 R1 | 5 | 14.2274 | 0.35143 | 0 | 7.7836 | 0 | 23
C445 2012 CFSP WS BRANCH R1 | 2 | 14.9781 | 0.13353 | 1 | 7.0329 | 0.14219 | 34
C445,BU:LG SPAN/DESIMI R16 | 2 | 14.1068 | 0.14178 | 0 | 7.9041 | 0 | 5
C67,BAR:LG SPAN/DESIMIL R3 | 1 | 13.6411 | 0.073308 | 0 | 8.3699 | 0 | 12
C73 PH 4 APOLE CHGOUT/ R9 | 1 | 14.2192 | 0.070328 | 1 | 7.7918 | 0.12834 | 17
C73 PH 4 BPOLE CHGOUT/ R5 | 1 | 13.9836 | 0.071513 | 0 | 8.0274 | 0 | 31
C78 PH4 BPOLE CHGOUT/R R8 | 1 | 14.2329 | 0.07026 | 0 | 7.7781 | 0 | 9
C78 PH4 CPOLE CHGOUT/RECO | 1 | 14.2329 | 0.07026 | 0 | 7.7781 | 0 | 20
C79 FIRE RISK MITIGATION R2 | 2 | 14.5452 | 0.1375 | 0 | 7.4658 | 0 | 72
C79 PH 2 R RECONDUCTOR | 0 | 14.8082 | 0 | 1 | 7.2027 | 0.13884 | 22
C79 PH4 SEC 2 E POLE R1 | 2 | 14.4219 | 0.13868 | 0 | 7.589 | 0 | 18
C973 PH 2 #A RECOND | 1 | 14.5233 | 0.068855 | 0 | 7.4877 | 0 | 17
CNF-C440 II | 1 | 20.5479 | 0.048667 | 0 | 1.463 | 0 | 25
CNF-C442 I | 1 | 17.3014 | 0.057799 | 0 | 4.7096 | 0 | 88
CNF-C79B | 2 | 20.7699 | 0.096293 | 1 | 1.2411 | 0.80574 | 172
CNF-TL629A | 1 | 19.726 | 0.050694 | 0 | 2.2849 | 0 | 57
CRA1 PH 2 A RECONDUCTOR | 2 | 14.7507 | 0.13559 | 0 | 7.2603 | 0 | 23
FiRM C0237 R RECON | 2 | 17.4192 | 0.11482 | 0 | 4.5918 | 0 | 20
FiRM C0444 CFSP RECON | 2 | 17.4192 | 0.11482 | 0 | 4.5918 | 0 | 21
FiRM C0971 H RECON | 3 | 17.4192 | 0.17222 | 0 | 4.5918 | 0 | 26
FiRM C221 PINE HILLS R1 FTZ | 3 | 14.863 | 0.20184 | 0 | 7.1479 | 0 | 5
HANA2013 | 2 | 12.0082 | 0.16655 | 2 | 10.0027 | 0.19995 | 82
HANA2014 | 4 | 13.0082 | 0.3075 | 0 | 9.0027 | 0 | 93
HANA2015 | 3 | 14.0082 | 0.21416 | 4 | 8.0027 | 0.49983 | 127
HANA2016 | 2 | 15.0082 | 0.13326 | 1 | 7.0027 | 0.1428 | 134
HANA2017 | 9 | 16.011 | 0.56211 | 1 | 6 | 0.16667 | 148
HANA2018 | 8 | 17.011 | 0.47029 | 0 | 5 | 0 | 199
HANA2019 | 22 | 18.011 | 1.2215 | 4 | 4 | 1 | 412
HANA2020 | 7 | 19.011 | 0.36821 | 2 | 3 | 0.66667 | 329
HANA2021 | 5 | 20.0137 | 0.24983 | 0 | 1.9973 | 0 | 69
PE1 PH 4 A POLE CHGO R11 | 2 | 14.5014 | 0.13792 | 0 | 7.5096 | 0 | 51
PE1 PH 4#C POLE CHGOUT/RE | 1 | 14.2795 | 0.070031 | 0 | 7.7315 | 0 | 11
Track 2 530000154309 | 2 | 20.0877 | 0.099564 | 0 | 1.9233 | 0 | 16
0073-H | 0 | 16.2521 | 0 | 0 | 5.7589 | 0 | 23
0075-A | 0 | 17.1014 | 0 | 0 | 4.9096 | 0 | 21
0079-I | 0 | 14.3288 | 0 | 0 | 7.6822 | 0 | 24
0157-B | 0 | 20.7644 | 0 | 0 | 1.2466 | 0 | 48
0157-FF | 0 | 20.7452 | 0 | 0 | 1.2658 | 0 | 10
0157-J | 0 | 20.3288 | 0 | 0 | 1.6822 | 0 | 29
0157-N | 0 | 20.5726 | 0 | 0 | 1.4384 | 0 | 36
0157-Q | 0 | 19.1151 | 0 | 0 | 2.8959 | 0 | 21
0176-B | 0 | 16.3507 | 0 | 0 | 5.6603 | 0 | 23
0176-E | 0 | 16.3123 | 0 | 0 | 5.6986 | 0 | 27
0176-G | 0 | 16.0411 | 0 | 0 | 5.9699 | 0 | 18
0176-I-FT-02 | 0 | 20.7041 | 0 | 0 | 1.3068 | 0 | 2
0176-M | 0 | 20.6877 | 0 | 0 | 1.3233 | 0 | 10
0182-COUNTRY_CLUB | 0 | 20.5863 | 0 | 0 | 1.4247 | 0 | 8
0211-FTZAP-FT | 0 | 19.7041 | 0 | 0 | 2.3068 | 0 | 5
0212-AA | 0 | 20.9836 | 0 | 0 | 1.0274 | 0 | 9
0212-DD (ASD) | 0 | 20.8301 | 0 | 0 | 1.1808 | 0 | 5
0212-FF | 0 | 20.1589 | 0 | 0 | 1.8521 | 0 | 17
0212-G | 0 | 19.5562 | 0 | 0 | 2.4548 | 0 | 36
0212-GG | 0 | 20.6247 | 0 | 0 | 1.3863 | 0 | 32
0212-H | 0 | 19.6137 | 0 | 0 | 2.3973 | 0 | 18
0212-I | 0 | 19.4027 | 0 | 0 | 2.6082 | 0 | 8
0212-K | 0 | 20.8219 | 0 | 0 | 1.189 | 0 | 48
0212-K-PH-02 | 0 | 20.9753 | 0 | 0 | 1.0356 | 0 | 7
0212-L | 0 | 21.1863 | 0 | 0 | 0.82466 | 0 | 38
0212-M | 0 | 20.3151 | 0 | 0 | 1.6959 | 0 | 8
0212-Q | 0 | 21.2247 | 0 | 0 | 0.7863 | 0 | 78
0212-S | 0 | 21.0411 | 0 | 0 | 0.96986 | 0 | 35
0212-T | 0 | 20.4 | 0 | 0 | 1.611 | 0 | 18
0212-W-PH-02 | 0 | 20.2904 | 0 | 0 | 1.7205 | 0 | 6
0212-Y | 0 | 20.937 | 0 | 0 | 1.074 | 0 | 18
0212-Z | 0 | 21.1945 | 0 | 0 | 0.81644 | 0 | 6
0217-F | 0 | 17.3781 | 0 | 0 | 4.6329 | 0 | 28
0217-I | 0 | 17.6466 | 0 | 0 | 4.3644 | 0 | 10
0217-K | 0 | 18.2685 | 0 | 0 | 3.7425 | 0 | 34
0217-L | 0 | 18.2685 | 0 | 0 | 3.7425 | 0 | 22
0217-O | 0 | 17.674 | 0 | 0 | 4.337 | 0 | 17
0217-S | 0 | 18.0767 | 0 | 0 | 3.9342 | 0 | 18
0217-V | 0 | 18.9781 | 0 | 0 | 3.0329 | 0 | 5
0220-A-FIRE-01 | 0 | 18.3397 | 0 | 0 | 3.6712 | 0 | 2
0220-P | 0 | 15.8274 | 0 | 0 | 6.1836 | 0 | 14
0221-H | 0 | 15.8055 | 0 | 0 | 6.2055 | 0 | 22
0221-K | 0 | 15.6137 | 0 | 0 | 6.3973 | 0 | 42
0221-M | 0 | 15.7726 | 0 | 0 | 6.2384 | 0 | 24
0221-P | 0 | 17.1342 | 0 | 0 | 4.8767 | 0 | 25
0221-Q | 0 | 17.1342 | 0 | 0 | 4.8767 | 0 | 29
0221-R | 0 | 17.5918 | 0 | 0 | 4.4192 | 0 | 22
0221-U | 0 | 17.5288 | 0 | 0 | 4.4822 | 0 | 18
0221-W | 0 | 17.6548 | 0 | 0 | 4.3562 | 0 | 13
0221-Y-PH2-RFS | 0 | 17.5671 | 0 | 0 | 4.4438 | 0 | 2
0222-CC | 0 | 19.6055 | 0 | 0 | 2.4055 | 0 | 9
0222-G | 0 | 18.9068 | 0 | 0 | 3.1041 | 0 | 10
0222-GG | 0 | 19.326 | 0 | 0 | 2.6849 | 0 | 20
0222-KK | 0 | 20.3233 | 0 | 0 | 1.6877 | 0 | 56
0222-N | 0 | 15.6493 | 0 | 0 | 6.3616 | 0 | 31
0222-NN | 0 | 20.3781 | 0 | 0 | 1.6329 | 0 | 56
0222-TT | 0 | 20.3425 | 0 | 0 | 1.6685 | 0 | 11
0222-W | 0 | 15.4877 | 0 | 0 | 6.5233 | 0 | 40
0222-X | 0 | 15.8438 | 0 | 0 | 6.1671 | 0 | 32
0222-Y | 0 | 15.8932 | 0 | 0 | 6.1178 | 0 | 24
0230-A | 0 | 17.2493 | 0 | 0 | 4.7616 | 0 | 16
0230-F | 0 | 17.589 | 0 | 0 | 4.4219 | 0 | 31
0237-B | 0 | 16.3589 | 0 | 0 | 5.6521 | 0 | 22
0237-N | 0 | 15.6493 | 0 | 0 | 6.3616 | 0 | 25
0237-P | 0 | 15.3671 | 0 | 0 | 6.6438 | 0 | 45
0237-S | 0 | 15.6795 | 0 | 0 | 6.3315 | 0 | 32
0239.1-A-FT | 0 | 20.1233 | 0 | 0 | 1.8877 | 0 | 4
0240-Z-FT | 0 | 19.5753 | 0 | 0 | 2.4356 | 0 | 2
0350-B | 0 | 17.3781 | 0 | 0 | 4.6329 | 0 | 29
0350-C | 0 | 17.2658 | 0 | 0 | 4.7452 | 0 | 8
0350-D | 0 | 18.9753 | 0 | 0 | 3.0356 | 0 | 34
0350-H | 0 | 17.7808 | 0 | 0 | 4.2301 | 0 | 40
0350-I | 0 | 17.6932 | 0 | 0 | 4.3178 | 0 | 24
0350-J | 0 | 18.5699 | 0 | 0 | 3.4411 | 0 | 24
0350-N-FT | 0 | 18.9342 | 0 | 0 | 3.0767 | 0 | 8
0350-O (ASD) | 0 | 18.9534 | 0 | 0 | 3.0575 | 0 | 5
0441-A-TH | 0 | 21.8 | 0 | 0 | 0.21096 | 0 | 5
0442-I | 0 | 15.1562 | 0 | 0 | 6.8548 | 0 | 13
0442-L | 0 | 18.9562 | 0 | 0 | 3.0548 | 0 | 29
0442-M | 0 | 15.3178 | 0 | 0 | 6.6932 | 0 | 14
0444-A-PH-02 | 0 | 20.4575 | 0 | 0 | 1.5534 | 0 | 26
0444-B-FT-02 | 0 | 20.411 | 0 | 0 | 1.6 | 0 | 2
0444-CFSP | 0 | 18.9562 | 0 | 0 | 3.0548 | 0 | 8
0445-D | 0 | 17.7507 | 0 | 0 | 4.2603 | 0 | 31
0445-F | 0 | 17.4164 | 0 | 0 | 4.5945 | 0 | 14
0445-J | 0 | 19.4027 | 0 | 0 | 2.6082 | 0 | 29
0445-K | 0 | 18.3178 | 0 | 0 | 3.6932 | 0 | 41
0445-M | 0 | 19.3068 | 0 | 0 | 2.7041 | 0 | 14
0445-X | 0 | 20.3123 | 0 | 0 | 1.6986 | 0 | 16
0448-C-FT | 0 | 19.0082 | 0 | 0 | 3.0027 | 0 | 2
0520-A | 0 | 16.6356 | 0 | 0 | 5.3753 | 0 | 25
0520-E | 0 | 17.4411 | 0 | 0 | 4.5699 | 0 | 35
0520-G | 0 | 16.5753 | 0 | 0 | 5.4356 | 0 | 19
0520-J | 0 | 17.1342 | 0 | 0 | 4.8767 | 0 | 17
0520-K | 0 | 17.4822 | 0 | 0 | 4.5288 | 0 | 48
0520-M | 0 | 17.2301 | 0 | 0 | 4.7808 | 0 | 30
0520-O (ASD) | 0 | 20.6466 | 0 | 0 | 1.3644 | 0 | 12
0520-P (ASD) | 0 | 20.8712 | 0 | 0 | 1.1397 | 0 | 12
0859-SUNHILL_RANCH | 0 | 20.6274 | 0 | 0 | 1.3836 | 0 | 3
0908-A | 0 | 17.9808 | 0 | 0 | 4.0301 | 0 | 39
0908-B | 0 | 18.8356 | 0 | 0 | 3.1753 | 0 | 25
0908-C | 0 | 18.1151 | 0 | 0 | 3.8959 | 0 | 39
0908-I | 0 | 19.4219 | 0 | 0 | 2.589 | 0 | 19
0908-I-FT | 0 | 19.7068 | 0 | 0 | 2.3041 | 0 | 9
0908-J | 0 | 19.2493 | 0 | 0 | 2.7616 | 0 | 11
0908-K | 0 | 18.7068 | 0 | 0 | 3.3041 | 0 | 10
0908-M | 0 | 20.5726 | 0 | 0 | 1.4384 | 0 | 8
0908-M-PH-02 | 0 | 21.7452 | 0 | 0 | 0.26575 | 0 | 3
0971-F | 0 | 17.1726 | 0 | 0 | 4.8384 | 0 | 34
0971-H | 0 | 17.3808 | 0 | 0 | 4.6301 | 0 | 3
0971-L | 0 | 17.1726 | 0 | 0 | 4.8384 | 0 | 33
0971-N | 0 | 20.9753 | 0 | 0 | 1.0356 | 0 | 28
0971-O | 0 | 16.6356 | 0 | 0 | 5.3753 | 0 | 37
0971-P | 0 | 16.7918 | 0 | 0 | 5.2192 | 0 | 23
0972-B | 0 | 16.3589 | 0 | 0 | 5.6521 | 0 | 26
0972-E | 0 | 16.3973 | 0 | 0 | 5.6137 | 0 | 31
0973-B | 0 | 15.7945 | 0 | 0 | 6.2164 | 0 | 29
0974-A | 0 | 16.9534 | 0 | 0 | 5.0575 | 0 | 5
0974-F | 0 | 16.8685 | 0 | 0 | 5.1425 | 0 | 3
1001-SF | 0 | 21.5205 | 0 | 0 | 0.49041 | 0 | 3
1030-A | 0 | 14.2384 | 0 | 0 | 7.7726 | 0 | 17
1030-D | 0 | 18.726 | 0 | 0 | 3.2849 | 0 | 41
1030-E | 0 | 16.8877 | 0 | 0 | 5.1233 | 0 | 36
1030-G | 0 | 16.5753 | 0 | 0 | 5.4356 | 0 | 25
1030-H | 0 | 15.789 | 0 | 0 | 6.2219 | 0 | 26
1030-I | 0 | 15.6356 | 0 | 0 | 6.3753 | 0 | 29
1030-K | 0 | 16.5753 | 0 | 0 | 5.4356 | 0 | 26
1030-L | 0 | 16.2329 | 0 | 0 | 5.7781 | 0 | 24
1030-M | 0 | 16.0356 | 0 | 0 | 5.9753 | 0 | 31
1030-P | 0 | 16.5753 | 0 | 0 | 5.4356 | 0 | 33
1030-Q | 0 | 16.4603 | 0 | 0 | 5.5507 | 0 | 31
1030-R | 0 | 16.6274 | 0 | 0 | 5.3836 | 0 | 38
1030-S | 0 | 15.6137 | 0 | 0 | 6.3973 | 0 | 13
1233B | 0 | 20.4712 | 0 | 0 | 1.5397 | 0 | 13
2056530 | 0 | 19.1671 | 0 | 0 | 2.8438 | 0 | 12
2100760 | 0 | 19.0384 | 0 | 0 | 2.9726 | 0 | 2
2110680 | 0 | 17.8438 | 0 | 0 | 4.1671 | 0 | 2
2160090 | 0 | 17.6247 | 0 | 0 | 4.3863 | 0 | 2
2164020 | 0 | 20.0384 | 0 | 0 | 1.9726 | 0 | 5
2301470 | 0 | 12.8712 | 0 | 0 | 9.1397 | 0 | 2
2304390 | 0 | 14.3918 | 0 | 0 | 7.6192 | 0 | 5
2304490 | 0 | 12.7452 | 0 | 0 | 9.2658 | 0 | 2
2314651 | 0 | 13.2712 | 0 | 0 | 8.7397 | 0 | 2
2322800 | 0 | 13.3534 | 0 | 0 | 8.6575 | 0 | 3
2329341 | 0 | 15.7644 | 0 | 0 | 6.2466 | 0 | 2
2333870 | 0 | 13.2 | 0 | 0 | 8.811 | 0 | 2
2340870 | 0 | 13.2356 | 0 | 0 | 8.7753 | 0 | 2
2341150 | 0 | 14.3096 | 0 | 0 | 7.7014 | 0 | 8
2351120 | 0 | 14.1918 | 0 | 0 | 7.8192 | 0 | 2
2351740 | 0 | 13.4822 | 0 | 0 | 8.5288 | 0 | 2
2351940 | 0 | 13.6 | 0 | 0 | 8.411 | 0 | 2
2359400 | 0 | 14.7589 | 0 | 0 | 7.2521 | 0 | 9
2359950 | 0 | 14.0274 | 0 | 0 | 7.9836 | 0 | 2
2360002 | 0 | 14.3452 | 0 | 0 | 7.6658 | 0 | 2
2370140 | 0 | 14.0521 | 0 | 0 | 7.9589 | 0 | 4
2376070 | 0 | 13.7945 | 0 | 0 | 8.2164 | 0 | 2
2376477 | 0 | 14.526 | 0 | 0 | 7.4849 | 0 | 6
2378967 | 0 | 14.6137 | 0 | 0 | 7.3973 | 0 | 3
2379011 | 0 | 14.3753 | 0 | 0 | 7.6356 | 0 | 4
2379020 | 0 | 14.2192 | 0 | 0 | 7.7918 | 0 | 2
2379021 | 0 | 13.9836 | 0 | 0 | 8.0274 | 0 | 2
2382280 | 0 | 12.7534 | 0 | 0 | 9.2575 | 0 | 2
2382750 | 0 | 13.5452 | 0 | 0 | 8.4658 | 0 | 4
2382755 | 0 | 14.3096 | 0 | 0 | 7.7014 | 0 | 8
2384500 | 0 | 14.8685 | 0 | 0 | 7.1425 | 0 | 5
2385500 | 0 | 13.3781 | 0 | 0 | 8.6329 | 0 | 11
2391251 | 0 | 14.1671 | 0 | 0 | 7.8438 | 0 | 3
2393470 | 0 | 14.3945 | 0 | 0 | 7.6164 | 0 | 3
2394170 | 0 | 14.2301 | 0 | 0 | 7.7808 | 0 | 2
2394310 | 0 | 14.1726 | 0 | 0 | 7.8384 | 0 | 2
2397600 | 0 | 14.1918 | 0 | 0 | 7.8192 | 0 | 2
2399990 | 0 | 14.5233 | 0 | 0 | 7.4877 | 0 | 2
2400760 | 0 | 14.7507 | 0 | 0 | 7.2603 | 0 | 3
2401700 | 0 | 14.2795 | 0 | 0 | 7.7315 | 0 | 2
2403287 | 0 | 15.811 | 0 | 0 | 6.2 | 0 | 22
2403288 | 0 | 17.4795 | 0 | 0 | 4.5315 | 0 | 8
2403289 | 0 | 15.8301 | 0 | 0 | 6.1808 | 0 | 2
2407230 | 0 | 14.6767 | 0 | 0 | 7.3342 | 0 | 20
240A | 0 | 20.3425 | 0 | 0 | 1.6685 | 0 | 4
2415353 | 0 | 15.4082 | 0 | 0 | 6.6027 | 0 | 2
2416260 | 0 | 14.4986 | 0 | 0 | 7.5123 | 0 | 2
2423150 | 0 | 15.0795 | 0 | 0 | 6.9315 | 0 | 2
2423335 | 0 | 17.2192 | 0 | 0 | 4.7918 | 0 | 3
2424322 | 0 | 15.1562 | 0 | 0 | 6.8548 | 0 | 2
2433461 | 0 | 17.7068 | 0 | 0 | 4.3041 | 0 | 9
2433462 | 0 | 19.3425 | 0 | 0 | 2.6685 | 0 | 28
2450632 | 0 | 15.3671 | 0 | 0 | 6.6438 | 0 | 2
2450990 | 0 | 16.8795 | 0 | 0 | 5.1315 | 0 | 3
2462530 | 0 | 15.7096 | 0 | 0 | 6.3014 | 0 | 2
2468330 | 0 | 15.189 | 0 | 0 | 6.8219 | 0 | 2
2471052 | 0 | 15.2384 | 0 | 0 | 6.7726 | 0 | 2
2471680 | 0 | 15.1205 | 0 | 0 | 6.8904 | 0 | 2
2477491 | 0 | 16.3041 | 0 | 0 | 5.7068 | 0 | 2
2477800 | 0 | 16.1342 | 0 | 0 | 5.8767 | 0 | 4
2478260 | 0 | 15.6384 | 0 | 0 | 6.3726 | 0 | 2
2482601 | 0 | 17.1945 | 0 | 0 | 4.8164 | 0 | 3
2486660 | 0 | 18.1836 | 0 | 0 | 3.8274 | 0 | 7
2487850 | 0 | 15.9616 | 0 | 0 | 6.0493 | 0 | 4
2505201 | 0 | 18.7589 | 0 | 0 | 3.2521 | 0 | 7
2505207 | 0 | 17.2137 | 0 | 0 | 4.7973 | 0 | 8
2508350 | 0 | 16.0082 | 0 | 0 | 6.0027 | 0 | 2
2514610 | 0 | 17.2082 | 0 | 0 | 4.8027 | 0 | 1
2523270 | 0 | 16.3096 | 0 | 0 | 5.7014 | 0 | 3
2550400 | 0 | 18.7288 | 0 | 0 | 3.2822 | 0 | 3
2560220 | 0 | 16.589 | 0 | 0 | 5.4219 | 0 | 3
2564130 | 0 | 17.6959 | 0 | 0 | 4.3151 | 0 | 2
2592690 | 0 | 17.6986 | 0 | 0 | 4.3123 | 0 | 16
2652099 | 0 | 20.1014 | 0 | 0 | 1.9096 | 0 | 2
2919418 | 0 | 18.1479 | 0 | 0 | 3.863 | 0 | 6
2920314 | 0 | 12.6247 | 0 | 0 | 9.3863 | 0 | 4
2931040 | 0 | 14.5233 | 0 | 0 | 7.4877 | 0 | 4
2931340 | 0 | 12.8493 | 0 | 0 | 9.1616 | 0 | 30
2936725 | 0 | 13.3918 | 0 | 0 | 8.6192 | 0 | 3
2945281 | 0 | 17.611 | 0 | 0 | 4.4 | 0 | 2
2945285 | 0 | 12.6219 | 0 | 0 | 9.389 | 0 | 2
2948251 | 0 | 13.7534 | 0 | 0 | 8.2575 | 0 | 2
2951570 | 0 | 13.8904 | 0 | 0 | 8.1205 | 0 | 9
2952360 | 0 | 12.2027 | 0 | 0 | 9.8082 | 0 | 3
2952900 | 0 | 13.9534 | 0 | 0 | 8.0575 | 0 | 6
2954560 | 0 | 12.5808 | 0 | 0 | 9.4301 | 0 | 2
2955790 | 0 | 12.6822 | 0 | 0 | 9.3288 | 0 | 3
2959671 | 0 | 13.3753 | 0 | 0 | 8.6356 | 0 | 4
2960080 | 0 | 13.1945 | 0 | 0 | 8.8164 | 0 | 4
2963380 | 0 | 12.9507 | 0 | 0 | 9.0603 | 0 | 7
2963420 | 0 | 13.1973 | 0 | 0 | 8.8137 | 0 | 5
2966020 | 0 | 12.2219 | 0 | 0 | 9.789 | 0 | 2
2966600 | 0 | 12.8192 | 0 | 0 | 9.1918 | 0 | 7
2968201 | 0 | 12.6219 | 0 | 0 | 9.389 | 0 | 2
2968940 | 0 | 12.3233 | 0 | 0 | 9.6877 | 0 | 3
2969320 | 0 | 12.5507 | 0 | 0 | 9.4603 | 0 | 2
2969690 | 0 | 13.0795 | 0 | 0 | 8.9315 | 0 | 4
2976520 | 0 | 13.7068 | 0 | 0 | 8.3041 | 0 | 2
2984901 | 0 | 17.2219 | 0 | 0 | 4.789 | 0 | 1
2985080 | 0 | 12.8 | 0 | 0 | 9.211 | 0 | 3
2990359 | 0 | 20.6411 | 0 | 0 | 1.3699 | 0 | 1
300000413639 | 0 | 20.9534 | 0 | 0 | 1.0575 | 0 | 2
300000432859 | 0 | 18.2137 | 0 | 0 | 3.7973 | 0 | 3
300000432932 | 0 | 21.2137 | 0 | 0 | 0.79726 | 0 | 66
300000432959 | 0 | 20.4521 | 0 | 0 | 1.5589 | 0 | 2
300000432961 | 0 | 20.274 | 0 | 0 | 1.737 | 0 | 2
300000432987 | 0 | 20.4575 | 0 | 0 | 1.5534 | 0 | 2
300000433001 | 0 | 19.0384 | 0 | 0 | 2.9726 | 0 | 2
300000433002 | 0 | 20.4521 | 0 | 0 | 1.5589 | 0 | 2
300000433147 | 0 | 20.3288 | 0 | 0 | 1.6822 | 0 | 3
300000550290 | 0 | 20.1233 | 0 | 0 | 1.8877 | 0 | 2
350380-190 | 0 | 12.411 | 0 | 0 | 9.6 | 0 | 3
350465-150 | 0 | 12.726 | 0 | 0 | 9.2849 | 0 | 1
355C-TU | 0 | 21.2986 | 0 | 0 | 0.71233 | 0 | 4
358007-080 | 0 | 12.5808 | 0 | 0 | 9.4301 | 0 | 4
442G | 0 | 20.1699 | 0 | 0 | 1.8411 | 0 | 3
442S | 0 | 20.4767 | 0 | 0 | 1.5342 | 0 | 3
442U | 0 | 20.1753 | 0 | 0 | 1.8356 | 0 | 3
442W | 0 | 20.2959 | 0 | 0 | 1.7151 | 0 | 2
442X | 0 | 19.6027 | 0 | 0 | 2.4082 | 0 | 2
448GGG | 0 | 20.4438 | 0 | 0 | 1.5671 | 0 | 2
448HHH | 0 | 20.4575 | 0 | 0 | 1.5534 | 0 | 8
448JJJ | 0 | 20.9178 | 0 | 0 | 1.0932 | 0 | 4
448K | 0 | 21.2575 | 0 | 0 | 0.75342 | 0 | 3
448NNN | 0 | 20.6055 | 0 | 0 | 1.4055 | 0 | 9
448OOO | 0 | 20.8493 | 0 | 0 | 1.1616 | 0 | 11
448P CC-FIRE-01 | 0 | 17.4192 | 0 | 0 | 4.5918 | 0 | 16
448Q CC-FIRE-01 | 0 | 14.3753 | 0 | 0 | 7.6356 | 0 | 27
448S | 0 | 20.8932 | 0 | 0 | 1.1178 | 0 | 13
448SSS | 0 | 20.7945 | 0 | 0 | 1.2164 | 0 | 9
448U | 0 | 20.5288 | 0 | 0 | 1.4822 | 0 | 11
448V | 0 | 20.4904 | 0 | 0 | 1.5205 | 0 | 6
448W | 0 | 20.5123 | 0 | 0 | 1.4986 | 0 | 5
448WW | 0 | 20.3781 | 0 | 0 | 1.6329 | 0 | 5
448X | 0 | 20.5068 | 0 | 0 | 1.5041 | 0 | 8
448ZZ | 0 | 20.3233 | 0 | 0 | 1.6877 | 0 | 10
449HH | 0 | 18.2493 | 0 | 0 | 3.7616 | 0 | 7
449II | 0 | 18.137 | 0 | 0 | 3.874 | 0 | 15
449JJ | 0 | 18.3233 | 0 | 0 | 3.6877 | 0 | 10
450272-120 | 0 | 13.3836 | 0 | 0 | 8.6274 | 0 | 3
530000011456 | 0 | 14.3507 | 0 | 0 | 7.6603 | 0 | 2
530000069509 | 0 | 16.2137 | 0 | 0 | 5.7973 | 0 | 2
530000086143 | 0 | 16.8986 | 0 | 0 | 5.1123 | 0 | 2
530000089264 | 0 | 17.0986 | 0 | 0 | 4.9123 | 0 | 3
530000090084 | 0 | 17.2192 | 0 | 0 | 4.7918 | 0 | 4
530000097345 | 0 | 17.2795 | 0 | 0 | 4.7315 | 0 | 2
530000100653 | 0 | 17.4164 | 0 | 0 | 4.5945 | 0 | 3
530000100768 | 0 | 17.4027 | 0 | 0 | 4.6082 | 0 | 5
530000102136 | 0 | 16.9589 | 0 | 0 | 5.0521 | 0 | 3
530000108896 | 0 | 17.4904 | 0 | 0 | 4.5205 | 0 | 2
530000109933 | 0 | 17.3562 | 0 | 0 | 4.6548 | 0 | 5
530000111408 | 0 | 17.3836 | 0 | 0 | 4.6274 | 0 | 2
530000112954 | 0 | 17.5973 | 0 | 0 | 4.4137 | 0 | 4
530000113511 | 0 | 17.4986 | 0 | 0 | 4.5123 | 0 | 2
530000113588 | 0 | 17.5863 | 0 | 0 | 4.4247 | 0 | 2
530000121125 | 0 | 17.5288 | 0 | 0 | 4.4822 | 0 | 2
530000122456 | 0 | 17.5288 | 0 | 0 | 4.4822 | 0 | 2
530000122881 | 0 | 18.4822 | 0 | 0 | 3.5288 | 0 | 3
530000123945 | 0 | 19.0274 | 0 | 0 | 2.9836 | 0 | 4
530000123997 | 0 | 17.5288 | 0 | 0 | 4.4822 | 0 | 8
530000125402 | 0 | 18.874 | 0 | 0 | 3.137 | 0 | 3
530000130148 | 0 | 18.6027 | 0 | 0 | 3.4082 | 0 | 2
530000134408 | 0 | 18.7041 | 0 | 0 | 3.3068 | 0 | 3
530000142988 | 0 | 18.7616 | 0 | 0 | 3.2493 | 0 | 2
530000144402 | 0 | 18.8274 | 0 | 0 | 3.1836 | 0 | 2
530000144413 | 0 | 18.7945 | 0 | 0 | 3.2164 | 0 | 3
530000147263 | 0 | 18.874 | 0 | 0 | 3.137 | 0 | 4
530000148021 | 0 | 19.2849 | 0 | 0 | 2.726 | 0 | 3
530000149782 | 0 | 19.0356 | 0 | 0 | 2.9753 | 0 | 2
530000155165 | 0 | 19.3397 | 0 | 0 | 2.6712 | 0 | 4
530000161574 | 0 | 19.8932 | 0 | 0 | 2.1178 | 0 | 2
530000165126 | 0 | 19.3233 | 0 | 0 | 2.6877 | 0 | 5
530000168358 | 0 | 19.6767 | 0 | 0 | 2.3342 | 0 | 4
530000169969 | 0 | 20.2712 | 0 | 0 | 1.7397 | 0 | 2
530000171476 | 0 | 19.9836 | 0 | 0 | 2.0274 | 0 | 4
530000174046 | 0 | 19.537 | 0 | 0 | 2.474 | 0 | 2
530000179525 | 0 | 19.4603 | 0 | 0 | 2.5507 | 0 | 3
530000182683 | 0 | 20.0411 | 0 | 0 | 1.9699 | 0 | 5
530000196755 | 0 | 20.2164 | 0 | 0 | 1.7945 | 0 | 3
530000203397 | 0 | 20.0658 | 0 | 0 | 1.9452 | 0 | 2
530000203667 | 0 | 19.7205 | 0 | 0 | 2.2904 | 0 | 2
530000203726 | 0 | 20.0658 | 0 | 0 | 1.9452 | 0 | 2
530000204281 | 0 | 20.5836 | 0 | 0 | 1.4274 | 0 | 1
530000204688 | 0 | 21.1918 | 0 | 0 | 0.81918 | 0 | 2
530000210119 | 0 | 19.874 | 0 | 0 | 2.137 | 0 | 2
530000210595 | 0 | 20.7781 | 0 | 0 | 1.2329 | 0 | 2
530000211305 | 0 | 21.2 | 0 | 0 | 0.81096 | 0 | 6
530000218724 | 0 | 20.1288 | 0 | 0 | 1.8822 | 0 | 3
530000218854 | 0 | 20.1315 | 0 | 0 | 1.8795 | 0 | 2
530000221660 | 0 | 20.4466 | 0 | 0 | 1.5644 | 0 | 4
530000225468 | 0 | 20.463 | 0 | 0 | 1.5479 | 0 | 2
530000228417 | 0 | 20.7233 | 0 | 0 | 1.2877 | 0 | 1
530000231506 | 0 | 20.8685 | 0 | 0 | 1.1425 | 0 | 10
530000234069 | 0 | 20.7836 | 0 | 0 | 1.2274 | 0 | 3
530000240763 | 0 | 20.8685 | 0 | 0 | 1.1425 | 0 | 3
530000244354 | 0 | 20.7507 | 0 | 0 | 1.2603 | 0 | 2
530000245373 | 0 | 20.674 | 0 | 0 | 1.337 | 0 | 2
530000253278 | 0 | 21.9589 | 0 | 0 | 0.052055 | 0 | 1
530000253820 | 0 | 21.3644 | 0 | 0 | 0.64658 | 0 | 2
530000260563 | 0 | 20.9863 | 0 | 0 | 1.0247 | 0 | 2
530000278043 | 0 | 21.4822 | 0 | 0 | 0.52877 | 0 | 2
530000282324 | 0 | 21.5836 | 0 | 0 | 0.4274 | 0 | 6
530000285144 | 0 | 21.7178 | 0 | 0 | 0.29315 | 0 | 2
530000287527 | 0 | 21.9534 | 0 | 0 | 0.057534 | 0 | 2
79F | 0 | 19.6301 | 0 | 0 | 2.3808 | 0 | 3
79HH | 0 | 21.8192 | 0 | 0 | 0.19178 | 0 | 2
79J | 0 | 20.2329 | 0 | 0 | 1.7781 | 0 | 4
79TT | 0 | 19.4301 | 0 | 0 | 2.5808 | 0 | 3
79V | 0 | 20.6986 | 0 | 0 | 1.3123 | 0 | 2
79W | 0 | 20.4301 | 0 | 0 | 1.5808 | 0 | 3
C1023/C354_RFS_FREEWAY_X | 0 | 20.3808 | 0 | 0 | 1.6301 | 0 | 5
C1215 CWLONG SPAN/DESI R12 | 0 | 13.7068 | 0 | 0 | 8.3041 | 0 | 5
C1215 PH 4 POLE REPLACE/R | 0 | 14.3397 | 0 | 0 | 7.6712 | 0 | 10
C1233,PA LONGSPAN/DESIM R3 | 0 | 13.8466 | 0 | 0 | 8.1644 | 0 | 6
C1250 AERIAL MARKING R1 | 0 | 12.7151 | 0 | 0 | 9.2959 | 0 | 2
C1458 PH 2 #A RECONDUC R5 | 0 | 14.4411 | 0 | 0 | 7.5699 | 0 | 2
C217,RIN:LG SPAN/DESIMI R3 | 0 | 13.6301 | 0 | 0 | 8.3808 | 0 | 3
C217: 2013 FIRE HARDENING | 0 | 14.3342 | 0 | 0 | 7.6767 | 0 | 4
C220 PH 2 H RECONDUCT R1 | 0 | 14.4521 | 0 | 0 | 7.5589 | 0 | 32
C220 PH 2 J RECONDUCT R6 | 0 | 14.5781 | 0 | 0 | 7.4329 | 0 | 25
C220 PH 2 M RECONDUCTOR | 0 | 14.8384 | 0 | 0 | 7.1726 | 0 | 56
C220 PH 4 B POLE CHGO R3 | 0 | 14.4082 | 0 | 0 | 7.6027 | 0 | 30
C220 PH 4 E POLE CHGOUT | 0 | 13.8795 | 0 | 0 | 8.1315 | 0 | 3
C220 PH 4 F POLE CHGO R2 | 0 | 13.9616 | 0 | 0 | 8.0493 | 0 | 14
C220 PH 4 G POLE CHGO R2 | 0 | 14.8274 | 0 | 0 | 7.1836 | 0 | 14
C221 PH4 #E POLE REPLA R1 | 0 | 14.8082 | 0 | 0 | 7.2027 | 0 | 7
C221 PH4 C POLE REPLA R1 | 0 | 14.7781 | 0 | 0 | 7.2329 | 0 | 16
C221:ERI 2012 REBUILD | 0 | 14.6658 | 0 | 0 | 7.3452 | 0 | 2
C222 FIRE RISK MITIG PRO R2 | 0 | 13.1836 | 0 | 0 | 8.8274 | 0 | 31
C222 FIRE RISK MITIG PROJP | 0 | 12.9699 | 0 | 0 | 9.0411 | 0 | 52
C222 PH 1 #L RECONDUC R1 | 0 | 14.6 | 0 | 0 | 7.411 | 0 | 4
C222 PH 1 #O RECONDUC R1 | 0 | 14.4548 | 0 | 0 | 7.5562 | 0 | 39
C222 PH 1 #Q RECONDUC R3 | 0 | 14.6767 | 0 | 0 | 7.3342 | 0 | 15
C222 PH 1 J RECONDUC R6 | 0 | 14.7562 | 0 | 0 | 7.2548 | 0 | 16
C222 PH 1 M RECONDUC R6 | 0 | 14.7534 | 0 | 0 | 7.2575 | 0 | 17
C222 PH 2 V RECONDUCTOR | 0 | 14.8548 | 0 | 0 | 7.1562 | 0 | 35
C222 PH4 SEC2 APOLE CH R1 | 0 | 14.0603 | 0 | 0 | 7.9507 | 0 | 18
C222 PH4 SEC2 BPOLE CH R1 | 0 | 14.3479 | 0 | 0 | 7.663 | 0 | 12
C233, MN: RECONDUCTOR R4 | 0 | 13.0795 | 0 | 0 | 8.9315 | 0 | 36
C236 PH 2 A RECONDUCTOR | 0 | 14.4795 | 0 | 0 | 7.5315 | 0 | 18
C236 PH 2 C RECONDUCTOR | 0 | 15.3507 | 0 | 0 | 6.6603 | 0 | 20
C237 PH 2 A RECONDUCTOR | 0 | 14.6438 | 0 | 0 | 7.3671 | 0 | 27
C237 PH 2 L RECONDUCTOR | 0 | 14.7589 | 0 | 0 | 7.2521 | 0 | 30
C239: RELOCATION TO MITI R5 | 0 | 13.4356 | 0 | 0 | 8.5753 | 0 | 2
C240 PH 2 A RECONDUCT R1 | 0 | 14.8274 | 0 | 0 | 7.1836 | 0 | 32
C240 PH 2 H RECONDUCT R1 | 0 | 14.8877 | 0 | 0 | 7.1233 | 0 | 9
C350,LI:LG SPA/DESIMILAR W | 0 | 13.8329 | 0 | 0 | 8.1781 | 0 | 8
C357:2011 CFSP WS,TW ON R12 | 0 | 14.2164 | 0 | 0 | 7.7945 | 0 | 6
C357:2011 CFSP WS,TW ON R4 | 0 | 13.5616 | 0 | 0 | 8.4493 | 0 | 7
C441 BRLINE CFSP W/S(P1 R1 | 0 | 14.926 | 0 | 0 | 7.0849 | 0 | 30
C441 PH 4 POLE REPLACE R2 | 0 | 13.8219 | 0 | 0 | 8.189 | 0 | 16
C441 PHASE 4RECONDCTR P R6 | 0 | 13.2822 | 0 | 0 | 8.7288 | 0 | 7
C441: REBUILD P40714 TO R13 | 0 | 13.3973 | 0 | 0 | 8.6137 | 0 | 10
C442 PH 2 J RECONDUCT R8 | 0 | 14.9671 | 0 | 0 | 7.0438 | 0 | 9
C442 PH 2 K RECONDUCT R7 | 0 | 15.1562 | 0 | 0 | 6.8548 | 0 | 33
C442 PH 4 APOLE CHGOUT R1 | 0 | 14.1589 | 0 | 0 | 7.8521 | 0 | 5
C442 PH 4 CPOLE CHGOUT R1 | 0 | 14.5534 | 0 | 0 | 7.4575 | 0 | 11
C442 PH 4 HPOLE CHGOUT/RE | 0 | 14.6137 | 0 | 0 | 7.3973 | 0 | 21
C444,BU:2011 CFSP RCNDCT R8 | 0 | 12.7342 | 0 | 0 | 9.2767 | 0 | 15
C521,AV:LG SPAN/DESIMILAR | 0 | 14.1178 | 0 | 0 | 7.8932 | 0 | 4
C73 PH 2 I RECONDUCTO R1 | 0 | 14.8959 | 0 | 0 | 7.1151 | 0 | 8
C73 PH 2 JPOLE CHGOUT/ R1 | 0 | 15.2575 | 0 | 0 | 6.7534 | 0 | 6
C73 PH 4 CPOLE CHGOUT R11 | 0 | 15.0055 | 0 | 0 | 7.0055 | 0 | 40
C73 PH 4 EPOLE CHGOUT R11 | 0 | 14.3068 | 0 | 0 | 7.7041 | 0 | 29
C73 PH 4 FPOLE CHGOUT/ R8 | 0 | 14.1973 | 0 | 0 | 7.8137 | 0 | 7
C78 PH2 F RECONDUCTOR | 0 | 15.4082 | 0 | 0 | 6.6027 | 0 | 12
C78 PH4 APOLE CHGOUT/R R1 | 0 | 14.0027 | 0 | 0 | 8.0082 | 0 | 8
C79 PH 1 #O RECONDUCTOR | 0 | 14.8521 | 0 | 0 | 7.1589 | 0 | 14
C79 PH 1 N RECONDUCTO R2 | 0 | 14.4822 | 0 | 0 | 7.5288 | 0 | 6
C79 PH4 SEC 2 #G POLE R6 | 0 | 14.5671 | 0 | 0 | 7.4438 | 0 | 15
C79 PH4 SEC 2 #J POLE R9 | 0 | 14.6192 | 0 | 0 | 7.3918 | 0 | 4
C79 PH4 SEC 2 F POLE R1 | 0 | 14.6192 | 0 | 0 | 7.3918 | 0 | 14
C79 PH4 SEC 2 H POLE R1 | 0 | 14.526 | 0 | 0 | 7.4849 | 0 | 22
C79 PH4 SEC 2 K POLE R7 | 0 | 14.463 | 0 | 0 | 7.5479 | 0 | 43
C79 PH4 SEC 2 L POLE R1 | 0 | 14.3753 | 0 | 0 | 7.6356 | 0 | 15
C908 FAIRFIELD FARMS LON R5 | 0 | 12.9726 | 0 | 0 | 9.0384 | 0 | 7
C908:LONG SPAN RFS REL R2 | 0 | 12.8904 | 0 | 0 | 9.1205 | 0 | 7
C972,CRE:LG SPAN/DESIMILAR | 0 | 13.7041 | 0 | 0 | 8.3068 | 0 | 4
C974 E RECONDUCTOR R1 | 0 | 15.2 | 0 | 0 | 6.811 | 0 | 24
CNF-C157 | 0 | 18.1342 | 0 | 0 | 3.8767 | 0 | 63
CNF-C222 | 0 | 19.7589 | 0 | 0 | 2.2521 | 0 | 76
CNF-C440 I | 0 | 19.726 | 0 | 0 | 2.2849 | 0 | 5
CNF-C442 II | 0 | 17.3671 | 0 | 0 | 4.6438 | 0 | 27
CNF-C449 | 0 | 18.9014 | 0 | 0 | 3.1096 | 0 | 12
CNF-C79A | 0 | 19.726 | 0 | 0 | 2.2849 | 0 | 2
CNF-TL625B | 0 | 17.8548 | 0 | 0 | 4.1562 | 0 | 8
CNF-TL682 | 0 | 19.0658 | 0 | 0 | 2.9452 | 0 | 43
CPE1-D | 0 | 15.0767 | 0 | 0 | 6.9342 | 0 | 28
DCRI C176 St12035_MWR_POP-FIRE-01 | 0 | 18.3397 | 0 | 0 | 3.6712 | 0 | 2
ESH C0442 A TH | 0 | 20.9753 | 0 | 0 | 1.0356 | 0 | 2
FiRM C973 WILDCAT CYN R1 FTZ - 1 | 0 | 13.6822 | 0 | 0 | 8.3288 | 0 | 3
FiRM CPE1 PH 4 B | 0 | 14.3753 | 0 | 0 | 7.6356 | 0 | 18
Track 2 530000153582 | 0 | 18.6685 | 0 | 0 | 3.3425 | 0 | 4
Track 2 530000153622 | 0 | 18.6384 | 0 | 0 | 3.3726 | 0 | 13
Track 2 530000153794 | 0 | 18.6411 | 0 | 0 | 3.3699 | 0 | 9
Track 2 530000153928 | 0 | 19.5644 | 0 | 0 | 2.4466 | 0 | 6
Average | 0.73361 | 17.0603 | 0.043001 | 0.15437 | 4.9507 | 0.031182 | 20.3156
Unhardened faults per year per 100 miles | 4.9021
Hardened faults per year per 100 miles | 3.5548
Reduction | 27.48%

## Summary by Cause Category
Cause | Unhardened Faults | Unhardened years | Unhardned faults per operating year Average | Hardened Faults | Hardened years | Hardned faults per operating year Average | Poles | Reduction
Crew Contact | 0.0081967 | 17.0603 | 0.054773 | 0.0013661 | 4.9507 | 0.031458 | 20.3156 | 42.57%
Customer Contact | 0.17077 | 17.0603 | 1.1411 | 0.013661 | 4.9507 | 0.31458 | 20.3156 | 72.43%
Equipment | 0.35109 | 17.0603 | 2.3461 | 0.076503 | 4.9507 | 1.7617 | 20.3156 | 24.91%
Foreign Object | 0.02459 | 17.0603 | 0.16432 | 0.0040984 | 4.9507 | 0.094375 | 20.3156 | 42.57%
Miscellaneous | 0.0013661 | 17.0603 | 0.0091288 | 0 | 4.9507 | 0 | 20.3156 | 100%
SDGE/Contractor Contact | 0.0081967 | 17.0603 | 0.054773 | 0.0013661 | 4.9507 | 0.031458 | 20.3156 | 42.57%
Third Party Contact | 0.0013661 | 17.0603 | 0.0091288 | 0.02459 | 4.9507 | 0.56625 | 20.3156 | -6103%
Tree Contact | 0.0095628 | 17.0603 | 0.063901 | 0 | 4.9507 | 0 | 20.3156 | 100%
Weather | 0.15847 | 17.0603 | 1.0589 | 0.032787 | 4.9507 | 0.755 | 20.3156 | 28.7%
Average | 0.081512 | 17.0603 | 0.54468 | 0.017152 | 4.9507 | 0.39498 | 20.3156 | 27.48%