## Raw Data
Cause | check GIS dates | Facilityid11 | Final_CheckDate (copy) | FromFacility | Occurrence | P6 Finish1 | P6 Start1 | Prim_Cause Description | Prim_Cause Description (group) | Sec_Cause_Description | ToFacility | Workorderdate1 | Sum of Hardened years | Sum of Unhardened years
502 | FALSE | P114072 | Before | P114072 | 2004-01-19 07:36 |  |  | Arrester (lightning) failure | Equipment Failure |  |  | 2016-01-25 | 4.937 | 16.0767
502 | FALSE | P212238 | Before | STA 220-44 | 2001-04-01 23:52 |  |  | Arrester (lightning) failure | Equipment Failure |  | P212238 | 2016-10-31 | 4.1699 | 16.8438
510 | FALSE | P17619 | Before | P17619 | 2008-10-04 05:10 |  |  | Conductor contact/wire slap | Equipment Failure |  | P17620 | 2016-05-20 | 4.6192 | 16.3945
513 | FALSE | P40824 | After | P40824 | 2016-02-18 04:28 |  |  | Conductor failure/wire down | Equipment Failure |  | P40825 | 2015-12-05 | 5.0767 | 15.937
513 | FALSE | P40824 | After | P40825 | 2016-02-18 04:34 |  |  | Conductor failure/wire down | Equipment Failure |  | P40824 | 2015-12-05 | 5.0767 | 15.937
513 | FALSE | P41589 | Before | P41589 | 2006-01-23 09:23 |  |  | Conductor failure/wire down | Equipment Failure |  |  | 2016-04-11 | 4.726 | 16.2877
513 | FALSE | P41967 | Before | P41967 | 2009-12-27 03:19 |  |  | Conductor failure/wire down | Equipment Failure |  | P41968 | 2015-03-27 | 5.7699 | 15.2438
513 | FALSE | P41967 | Before | P41967 | 2010-03-20 01:11 |  |  | Conductor failure/wire down | Equipment Failure |  | P41968 | 2015-03-27 | 5.7699 | 15.2438
513 | FALSE | P190313 | Before | P190313 | 2004-10-20 05:57 |  |  | Conductor failure/wire down | Equipment Failure |  | P510937 | 2013-10-02 | 7.2521 | 13.7616
513 | FALSE | P214108 | Before | P719560 | 2014-11-14 09:05 |  |  | Conductor failure/wire down | Equipment Failure |  | P214108 | 2015-01-13 | 5.9699 | 15.0438
513 | FALSE | P273284 | Before | P273284 | 2015-02-11 14:30 |  |  | Conductor failure/wire down | Equipment Failure |  | P273285 | 2020-03-02 | 0.83288 | 20.1808
513 | FALSE | P610498 | Before | P610497 | 2013-04-14 06:41 |  |  | Conductor failure/wire down | Equipment Failure |  | P610498 | 2015-04-27 | 5.6849 | 15.3288
513 | FALSE | P610498 | Before | P610497 | 2013-04-14 06:49 |  |  | Conductor failure/wire down | Equipment Failure |  | P610498 | 2015-04-27 | 5.6849 | 15.3288
513 | FALSE | P41589 | Before | P41589 | 2003-04-21 10:15 |  |  | Conductor failure/wire down | Equipment Failure | Insulator/pin failure/wire floating |  | 2016-04-11 | 4.726 | 16.2877
513 | FALSE | P111077 | Before | P111081 | 2007-05-28 15:06 |  |  | Conductor failure/wire down | Equipment Failure | Line-Xfmr deenerg for safety | P111077 | 2016-04-08 | 4.7342 | 16.2795
513 | FALSE | P275376 | Before | P275376 | 2014-03-26 18:10 |  |  | Conductor failure/wire down | Equipment Failure | Line-Xfmr deenerg for safety | P275377 | 2016-02-01 | 4.9178 | 16.0959
516 | FALSE | P476493 | Before | P476493 | 2010-11-08 01:26 |  |  | Connector/jumper/splice/elbow/rack | Equipment Failure | Crossarm failure |  | 2019-05-21 | 1.6164 | 19.3973
554 | FALSE | P111079 | Before | P111079 | 2006-04-21 14:07 |  |  | Crossarm failure | Equipment Failure |  | STA 222-496 | 2016-04-08 | 4.7342 | 16.2795
554 | FALSE | P172724 | Before | P172724 | 2004-11-01 21:14 |  |  | Crossarm failure | Equipment Failure |  |  | 2015-03-28 | 5.7671 | 15.2466
554 | FALSE | P971426 | Before | P971426 | 2011-07-11 17:15 |  |  | Crossarm failure | Equipment Failure |  |  | 2016-02-08 | 4.8986 | 16.1151
554 | FALSE | P17608 | Before | P17608 | 2007-05-16 18:20 |  |  | Crossarm failure | Equipment Failure | Line-Xfmr deenerg for safety |  | 2016-05-20 | 4.6192 | 16.3945
554 | FALSE | P18540 | After | P18540 | 2017-07-13 12:17 |  |  | Crossarm failure | Equipment Failure | Line-Xfmr deenerg for safety |  | 2014-03-21 | 6.7863 | 14.2274
554 | FALSE | P111080 | Before | P111080 | 2007-03-13 15:04 |  |  | Crossarm failure | Equipment Failure | Line-Xfmr deenerg for safety |  | 2016-04-08 | 4.7342 | 16.2795
554 | FALSE | P275369 | Before | P275369 | 2011-07-06 13:04 |  |  | Crossarm failure | Equipment Failure | Pole broke/rotted/on fire |  | 2016-02-01 | 4.9178 | 16.0959
518 | FALSE | P41541 | After | P41541 | 2018-10-15 07:08 |  |  | Cutout failure | Equipment Failure |  |  | 2016-04-11 | 4.726 | 16.2877
518 | FALSE | P211287 | Before | P211287 | 2008-12-10 21:10 |  |  | Cutout failure | Equipment Failure |  |  | 2016-04-08 | 4.7342 | 16.2795
518 | FALSE | P376431 | After | P376431 | 2020-11-06 23:46 |  |  | Cutout failure | Equipment Failure |  |  | 2016-06-03 | 4.5808 | 16.4329
512 | FALSE | P17708 | Before | P17708 | 2009-07-01 08:52 |  |  | Faulted cable | Equipment Failure |  | D3290085200 | 2015-02-13 | 5.8849 | 15.1288
512 | FALSE | P178017 | Before | P178017 | 2006-11-17 17:13 |  |  | Faulted cable | Equipment Failure |  | D2457991540 | 2016-05-06 | 4.6575 | 16.3562
512 | FALSE | P275841 | After | P275841 | 2018-06-16 00:56 |  |  | Faulted cable | Equipment Failure |  | D2342086710 | 2016-12-02 | 4.0822 | 16.9315
512 | FALSE | P870360 | Before | P870360 | 2013-09-04 12:02 |  |  | Faulted cable | Equipment Failure |  | H2499786539 | 2016-06-03 | 4.5808 | 16.4329
520 | FALSE | P176532 | After | P176532 | 2018-12-09 20:51 |  |  | Fuse holder/fuse cabinet failed | Equipment Failure |  |  | 2016-05-27 | 4.6 | 16.4137
522 | FALSE | P114679 | Before | P114679 | 2012-06-13 15:44 |  |  | Fuse overloaded/inadequate fuse size | Equipment Failure |  |  | 2015-01-13 | 5.9699 | 15.0438
528 | FALSE | P18540 | After | P18540 | 2019-03-14 09:51 |  |  | Hardware failure | Equipment Failure |  | P18541 | 2014-03-21 | 6.7863 | 14.2274
528 | FALSE | P41967 | Before | P41967 | 2013-09-13 04:23 |  |  | Hardware failure | Equipment Failure | Conductor failure/wire down | P41968 | 2015-03-27 | 5.7699 | 15.2438
530 | FALSE | P17756 | Before | P17756 | 2013-02-05 06:48 |  |  | Insulator/pin failure/wire floating | Equipment Failure | Conductor contact/wire slap |  | 2015-02-13 | 5.8849 | 15.1288
530 | FALSE | P275363 | Before | P275363 | 2009-01-10 21:56 |  |  | Insulator/pin failure/wire floating | Equipment Failure | Conductor contact/wire slap | P275364 | 2016-02-01 | 4.9178 | 16.0959
530 | FALSE | P372221 | Before | P372221 | 2007-01-12 00:10 |  |  | Insulator/pin failure/wire floating | Equipment Failure | Pole broke/rotted/on fire |  | 2014-09-11 | 6.3096 | 14.7041
410 | FALSE | P274663 | Before | P274663 | 2012-08-11 14:37 |  |  | Lightning Arrester/Transformer failure | Equipment Failure | Transformer faulted/mechanical | STA 78-139 | 2019-06-10 | 1.5616 | 19.4521
410 | FALSE | P276319 | Before | P276319 | 2014-08-03 20:51 |  |  | Lightning Arrester/Transformer failure | Equipment Failure | Transformer faulted/mechanical | STA 73-467 | 2015-07-09 | 5.4849 | 15.5288
410 | FALSE | P313103 | Before | P313103 | 2004-08-13 08:18 |  |  | Lightning Arrester/Transformer failure | Equipment Failure | Transformer faulted/mechanical | STA 237-371 | 2020-09-19 | 0.28219 | 20.7315
410 | FALSE | P41585 | Before | P41587 | 2006-03-11 21:00 |  |  | Lightning Arrester/Transformer failure | Equipment Failure | Wind - wires slap/pole down | P41585 | 2016-04-11 | 4.726 | 16.2877
515 | FALSE | P19715 | Before | P19715 | 2014-05-13 04:49 |  |  | OH connector failure (jumper/splice/squeeze-on) | Equipment Failure |  |  | 2016-03-21 | 4.7836 | 16.2301
515 | FALSE | P111072 | Before | P111072 | 2015-01-15 12:38 |  |  | OH connector failure (jumper/splice/squeeze-on) | Equipment Failure |  |  | 2016-04-08 | 4.7342 | 16.2795
515 | FALSE | P215852 | Before | P215852 | 2004-10-23 16:53 |  |  | OH connector failure (jumper/splice/squeeze-on) | Equipment Failure |  |  | 2016-04-08 | 4.7342 | 16.2795
515 | FALSE | P312752 | Before | P312752 | 2015-09-08 09:55 |  |  | OH connector failure (jumper/splice/squeeze-on) | Equipment Failure |  |  | 2016-03-03 | 4.8329 | 16.1808
515 | FALSE | P610466 | Before | P610466 | 2006-09-05 10:07 |  |  | OH connector failure (jumper/splice/squeeze-on) | Equipment Failure |  |  | 2014-12-22 | 6.0301 | 14.9836
515 | FALSE | P17726 | Before | P17727 | 2013-10-08 11:14 |  |  | OH connector failure (jumper/splice/squeeze-on) | Equipment Failure | Conductor failure/wire down | P17726 | 2015-02-13 | 5.8849 | 15.1288
515 | FALSE | P111819 | Before | P214038 | 2003-06-10 16:19 |  |  | OH connector failure (jumper/splice/squeeze-on) | Equipment Failure | Conductor failure/wire down | P111819 | 2014-03-06 | 6.8274 | 14.1863
515 | FALSE | P218931 | Before | P218931 | 2012-12-31 03:37 |  |  | OH connector failure (jumper/splice/squeeze-on) | Equipment Failure | Conductor failure/wire down | P519397 | 2015-07-27 | 5.4356 | 15.5781
515 | FALSE | P610498 | Before | P610497 | 2013-04-13 09:38 |  |  | OH connector failure (jumper/splice/squeeze-on) | Equipment Failure | Conductor failure/wire down | P610498 | 2015-04-27 | 5.6849 | 15.3288
515 | FALSE | P219920 | Before | P219920 | 2010-10-20 17:35 |  |  | OH connector failure (jumper/splice/squeeze-on) | Equipment Failure | Pole broke/rotted/on fire |  | 2015-07-09 | 5.4849 | 15.5288
515 | FALSE | P330216 | After | P330216 | 2020-03-18 00:28 |  |  | OH connector failure (jumper/splice/squeeze-on) | Equipment Failure | Primary wire down | Z173131 | 2016-04-01 | 4.7534 | 16.2603
532 | FALSE | P40838 | Before | P40838 | 2012-01-25 10:15 |  |  | Pole broke/rotted/on fire | Equipment Failure | Line-Xfmr deenerg for safety |  | 2016-04-08 | 4.7342 | 16.2795
532 | FALSE | P310513 | Before | P310513 | 2005-07-25 10:00 |  |  | Pole broke/rotted/on fire | Equipment Failure | Line-Xfmr deenerg for safety |  | 2016-05-04 | 4.663 | 16.3507
536 | FALSE | P227574 | After | P227574 | 2020-09-06 16:54 |  |  | Recloser/service restorer failure/contact | Equipment Failure |  |  | 2013-05-03 | 7.6685 | 13.3452
550 | FALSE | P212292 | Before | P212292 | 2005-09-23 09:56 |  |  | Transformer faulted/mechanical | Equipment Failure |  | STA 220-59 | 2016-03-03 | 4.8329 | 16.1808
550 | FALSE | P413864 | Before | P413864 | 2008-08-07 16:54 |  |  | Transformer faulted/mechanical | Equipment Failure |  | STA 222-60 | 2012-12-05 | 8.0767 | 12.937
502 | TRUE | P110715 | After | P110715 | 2018-09-18 16:05 | 2018-05-29 | 2018-03-12 | Arrester (lightning) failure | Equipment Failure |  |  | 2013-07-16 | 2.5945 | 18.4192
502 | TRUE | P166383 | Before | P166383 | 2013-01-26 05:52 | 2016-02-24 | 2015-06-29 | Arrester (lightning) failure | Equipment Failure |  |  | 2020-07-28 | 4.8548 | 16.1589
502 | TRUE | P412623 | Before | P412623 | 2013-10-28 09:45 | 2018-04-05 | 2016-10-14 | Arrester (lightning) failure | Equipment Failure |  |  | 2015-08-12 | 2.7425 | 18.2712
502 | TRUE | P572189 | Before | P572189 | 2017-08-05 09:03 | 2020-12-14 | 2020-05-21 | Arrester (lightning) failure | Equipment Failure |  |  | 2020-09-26 | 0.046575 | 20.9671
502 | TRUE | P613606 | Before | P613606 | 2001-07-29 23:09 | 2018-06-07 | 2018-01-25 | Arrester (lightning) failure | Equipment Failure |  |  | 2018-04-03 | 2.5699 | 18.4438
502 | TRUE | P161495 | Before | P161495 | 2011-05-19 21:55 | 2018-06-15 | 2018-03-07 | Arrester (lightning) failure | Equipment Failure | Crossarm failure |  | 2011-05-01 | 2.5479 | 18.4658
502 | TRUE | P412648 | Before | P412648 | 2016-07-11 13:19 | 2018-04-05 | 2016-10-14 | Arrester (lightning) failure | Equipment Failure | Line-Xfmr deenerg for safety |  | 2015-08-12 | 2.7425 | 18.2712
502 | TRUE | P211225 | Before | P211225 | 2013-05-23 14:20 | 2016-06-02 | 2016-04-18 | Arrester (lightning) failure | Equipment Failure | Transformer faulted/mechanical | STA 237-1145 | 2012-08-13 | 4.5836 | 16.4301
502 | TRUE | P417375 | After | P417375 | 2020-03-23 16:12 | 2019-10-08 | 2019-04-25 | Arrester failure | Equipment Failure |  |  | 2017-03-30 | 1.2329 | 19.7808
504 | TRUE | P218047 | Before | P218047 | 2013-06-28 03:55 | 2020-05-15 | 2020-01-22 | Capacitor failure | Equipment Failure |  | 212-661 CW | 2013-02-28 | 0.63014 | 20.3836
504 | TRUE | P875195 | Before | P875195 | 2007-11-05 08:59 | 2016-07-20 | 2016-02-29 | Capacitor failure | Equipment Failure |  | 240-790CW | 2020-10-02 | 4.4521 | 16.5616
510 | TRUE | P19529 | Before | P19530 | 2016-12-16 06:36 | 2019-12-27 | 2019-06-10 | Conductor contact/wire slap | Equipment Failure |  | P19529 | 2019-12-05 | 1.0137 | 20
510 | TRUE | P312927 | Before | P312927 | 2015-01-24 07:04 | 2019-06-14 | 2019-02-09 | Conductor contact/wire slap | Equipment Failure |  |  | 2019-05-15 | 1.5507 | 19.463
510 | TRUE | P312927 | Before | P312927 | 2015-01-24 14:23 | 2019-06-14 | 2019-02-09 | Conductor contact/wire slap | Equipment Failure |  |  | 2019-05-15 | 1.5507 | 19.463
510 | TRUE | P616240 | Before | P616240 | 2008-12-15 09:58 | 2017-05-12 | 2016-12-15 | Conductor contact/wire slap | Equipment Failure |  |  | 2016-05-12 | 3.6411 | 17.3726
510 | TRUE | P616239 | Before | P616239 | 2008-10-31 10:41 | 2017-05-12 | 2016-12-15 | Conductor contact/wire slap | Equipment Failure | Line-Xfmr deenerg for safety | P616241 | 2016-05-12 | 3.6411 | 17.3726
513 | TRUE | P17060 | Before | P17060 | 2018-02-03 13:36 | 2019-01-10 | 2018-06-01 | Conductor failure/wire down | Equipment Failure |  | P17059 | 2020-09-08 | 1.9753 | 19.0384
513 | TRUE | P19162 | Before | P213431 | 2009-02-04 14:07 | 2020-09-11 | 2020-06-22 | Conductor failure/wire down | Equipment Failure |  | P19162 | 2014-10-29 | 0.30411 | 20.7096
513 | TRUE | P19517 | Before | P19517 | 2012-12-25 06:34 | 2019-12-27 | 2019-06-10 | Conductor failure/wire down | Equipment Failure |  |  | 2019-12-05 | 1.0137 | 20
513 | TRUE | P19531 | Before | P19531 | 2003-01-01 06:37 | 2019-12-27 | 2019-06-10 | Conductor failure/wire down | Equipment Failure |  | P19532 | 2019-12-05 | 1.0137 | 20
513 | TRUE | P41201 | Before | P41201 | 2005-03-23 11:31 | 2020-04-22 | 2020-03-06 | Conductor failure/wire down | Equipment Failure |  | P41202 | 2020-04-17 | 0.69315 | 20.3205
513 | TRUE | P41976 | Before | P41976 | 2003-01-12 20:24 | 2019-12-12 | 2016-10-21 | Conductor failure/wire down | Equipment Failure |  | P41977 | 2016-04-08 | 1.0548 | 19.9589
513 | TRUE | P45801 | Before | P45801 | 2019-04-10 06:14 | 2020-05-29 | 2020-03-10 | Conductor failure/wire down | Equipment Failure |  |  | 2020-06-20 | 0.59178 | 20.4219
513 | TRUE | P113859 | Before | P113860 | 2003-06-26 17:22 | 2019-09-19 | 2019-06-24 | Conductor failure/wire down | Equipment Failure |  | P113859 | 2011-09-28 | 1.2849 | 19.7288
513 | TRUE | P115835 | Before | P115835 | 2019-11-20 21:35 | 2020-04-16 | 2019-03-28 | Conductor failure/wire down | Equipment Failure |  | P163664 | 2020-02-07 | 0.70959 | 20.3041
513 | TRUE | P116143 | Before | P417184 | 2016-09-17 02:59 | 2019-01-10 | 2018-06-01 | Conductor failure/wire down | Equipment Failure |  | P116143 | 2020-09-08 | 1.9753 | 19.0384
513 | TRUE | P116556 | Before | P116556 | 2009-09-06 08:30 | 2017-10-06 | 2017-03-17 | Conductor failure/wire down | Equipment Failure |  | P116557 | 2017-06-11 | 3.2384 | 17.7753
513 | TRUE | P119029 | Before | P119029 | 2003-04-20 17:31 | 2018-06-08 | 2018-03-12 | Conductor failure/wire down | Equipment Failure |  |  | 2018-05-04 | 2.5671 | 18.4466
513 | TRUE | P175471 | Before | P163173 | 2001-11-10 05:50 | 2016-05-24 | 2016-04-19 | Conductor failure/wire down | Equipment Failure |  | P175471 | 2020-09-08 | 4.6082 | 16.4055
513 | TRUE | P177582 | Before | P177582 | 2004-06-19 02:51 | 2020-02-05 | 2019-11-01 | Conductor failure/wire down | Equipment Failure |  | P475745 | 2020-02-18 | 0.90411 | 20.1096
513 | TRUE | P211296 | Before | P211295 | 2007-09-30 05:50 | 2017-11-17 | 2016-12-15 | Conductor failure/wire down | Equipment Failure |  | P211296 | 2019-08-12 | 3.1233 | 17.8904
513 | TRUE | P214799 | Before | P214799 | 2007-09-21 03:23 | 2019-12-19 | 2018-08-20 | Conductor failure/wire down | Equipment Failure |  | P214800 | 2019-05-02 | 1.0356 | 19.9781
513 | TRUE | P214804 | Before | P214804 | 2013-01-13 07:50 | 2019-12-19 | 2018-08-20 | Conductor failure/wire down | Equipment Failure |  | P217690 | 2019-05-02 | 1.0356 | 19.9781
513 | TRUE | P216480 | Before | P216480 | 2011-12-16 13:44 | 2020-09-09 | 2020-06-01 | Conductor failure/wire down | Equipment Failure |  | P218479 | 2020-06-30 | 0.30959 | 20.7041
513 | TRUE | P217599 | Before | P217599 | 2007-12-02 11:06 | 2017-04-06 | 2017-01-14 | Conductor failure/wire down | Equipment Failure |  | P217600 | 2020-07-14 | 3.7397 | 17.274
513 | TRUE | P312927 | Before | P312927 | 2011-01-23 06:44 | 2019-06-14 | 2019-02-09 | Conductor failure/wire down | Equipment Failure |  | P517324 | 2019-05-15 | 1.5507 | 19.463
513 | TRUE | P316588 | Before | P316588 | 2013-01-06 15:59 | 2019-01-10 | 2018-06-01 | Conductor failure/wire down | Equipment Failure |  | P517425 | 2020-09-08 | 1.9753 | 19.0384
513 | TRUE | P410563 | Before | P410563 | 2016-10-11 11:52 | 2017-08-14 | 2016-08-30 | Conductor failure/wire down | Equipment Failure |  |  | 2020-11-30 | 3.3836 | 17.6301
513 | TRUE | P412625 | Before | P412625 | 2016-01-07 07:22 | 2018-04-05 | 2016-10-14 | Conductor failure/wire down | Equipment Failure |  | P412626 | 2015-08-12 | 2.7425 | 18.2712
513 | TRUE | P412625 | Before | P412626 | 2016-03-07 14:46 | 2018-04-05 | 2016-10-14 | Conductor failure/wire down | Equipment Failure |  | P412625 | 2015-08-12 | 2.7425 | 18.2712
513 | TRUE | P412625 | Before | P412626 | 2016-03-29 03:32 | 2018-04-05 | 2016-10-14 | Conductor failure/wire down | Equipment Failure |  | P412625 | 2015-08-12 | 2.7425 | 18.2712
513 | TRUE | P513062 | Before | P513062 | 2010-09-04 14:07 | 2018-05-15 | 2018-01-02 | Conductor failure/wire down | Equipment Failure |  |  | 2018-04-10 | 2.6329 | 18.3808
513 | TRUE | P41860 | Before | P41860 | 2005-12-11 07:15 | 2018-09-28 | 2018-08-25 | Conductor failure/wire down | Equipment Failure | Fire | P41861 | 2018-10-23 | 2.2603 | 18.7534
513 | TRUE | P176556 | Before | P202826 | 2017-03-27 11:39 | 2017-08-31 | 2017-02-08 | Conductor failure/wire down | Equipment Failure | Foreign object in distribution line | P176556 | 2017-08-31 | 3.337 | 17.6767
513 | TRUE | P41145 | Before | P41145 | 2015-09-01 08:54 | 2019-04-23 | 2018-10-07 | Conductor failure/wire down | Equipment Failure | Line-Xfmr deenerg for safety | P41146 | 2012-10-10 | 1.6932 | 19.3205
513 | TRUE | P115832 | Before | P115832 | 2013-04-22 06:28 | 2020-04-16 | 2019-03-28 | Conductor failure/wire down | Equipment Failure | Line-Xfmr deenerg for safety | P716003 | 2020-02-07 | 0.70959 | 20.3041
513 | TRUE | P216309 | Before | P216309 | 2014-08-29 14:49 | 2020-11-07 | 2020-09-11 | Conductor failure/wire down | Equipment Failure | Line-Xfmr deenerg for safety | P216310 | 2018-03-26 | 0.14795 | 20.8658
513 | TRUE | P514507 | Before | P514507 | 2011-03-09 14:25 | 2018-09-07 | 2018-07-23 | Conductor failure/wire down | Equipment Failure | Line-Xfmr deenerg for safety |  | 2018-08-31 | 2.3178 | 18.6959
513 | TRUE | P175939 | Before | P175939 | 2011-05-16 09:41 | 2020-11-13 | 2020-07-01 | Conductor failure/wire down | Equipment Failure | Load unbalance | P676351 | 2020-11-12 | 0.13151 | 20.8822
513 | TRUE | P19531 | Before | P19533 | 2003-01-26 06:36 | 2019-12-27 | 2019-06-10 | Conductor failure/wire down | Equipment Failure | Pole broke/rotted/on fire | P19531 | 2019-12-05 | 1.0137 | 20
516 | TRUE | P413166 | Before | P413166 | 2001-10-28 22:48 | 2018-09-26 | 2018-07-02 | Connector/jumper/splice/elbow/rack | Equipment Failure |  |  | 2018-09-10 | 2.2658 | 18.7479
516 | TRUE | P316588 | Before | P316588 | 2018-04-02 14:48 | 2019-01-10 | 2018-06-01 | Connector/jumper/splice/elbow/rack | Equipment Failure | Conductor failure/wire down | P316589 | 2020-09-08 | 1.9753 | 19.0384
554 | TRUE | P19587 | Before | P19587 | 2013-05-06 07:11 | 2019-12-27 | 2019-06-25 | Crossarm failure | Equipment Failure |  |  | 2009-07-01 | 1.0137 | 20
554 | TRUE | P210177 | Before | P210177 | 2007-11-30 05:42 | 2020-12-09 | 2020-03-12 | Crossarm failure | Equipment Failure |  |  | 2020-11-17 | 0.060274 | 20.9534
554 | TRUE | P211064 | Before | P211064 | 2005-08-25 15:03 | 2017-05-17 | 2017-01-30 | Crossarm failure | Equipment Failure |  |  | 2017-05-17 | 3.6274 | 17.3863
554 | TRUE | P214792 | Before | P214792 | 2002-12-11 12:18 | 2018-03-01 | 2017-12-11 | Crossarm failure | Equipment Failure |  |  | 2018-03-01 | 2.8384 | 18.1753
554 | TRUE | P378657 | Before | P378657 | 2017-05-24 09:18 | 2017-12-04 | 2017-10-02 | Crossarm failure | Equipment Failure |  |  | 2018-07-09 | 3.0767 | 17.937
554 | TRUE | P412624 | After | P412624 | 2018-04-25 16:10 | 2018-04-05 | 2016-10-14 | Crossarm failure | Equipment Failure |  |  | 2015-08-12 | 2.7425 | 18.2712
554 | TRUE | P416200 | Before | P416200 | 2018-09-13 17:42 | 2018-12-21 | 2018-08-17 | Crossarm failure | Equipment Failure |  |  | 2019-09-25 | 2.0301 | 18.9836
554 | TRUE | P778295 | Before | P778295 | 2003-11-23 17:16 | 2015-12-04 | 2015-04-22 | Crossarm failure | Equipment Failure |  | P778296 | 2015-12-04 | 5.0795 | 15.9342
554 | TRUE | P116820 | Before | P116820 | 2005-07-30 21:12 | 2018-03-01 | 2017-04-26 | Crossarm failure | Equipment Failure | Conductor failure/wire down | STA 971-196 | 2018-03-01 | 2.8384 | 18.1753
554 | TRUE | P317943 | Before | P317943 | 2019-02-23 15:19 | 2020-10-08 | 2020-07-13 | Crossarm failure | Equipment Failure | Conductor failure/wire down | P317945 | 2020-09-15 | 0.23014 | 20.7836
554 | TRUE | P19587 | Before | P19587 | 2013-05-06 13:36 | 2019-12-27 | 2019-06-25 | Crossarm failure | Equipment Failure | Line-Xfmr deenerg for safety |  | 2009-07-01 | 1.0137 | 20
554 | TRUE | P117218 | Before | P117218 | 2014-10-28 19:24 | 2020-05-13 | 2020-01-09 | Crossarm failure | Equipment Failure | Line-Xfmr deenerg for safety |  | 2015-01-13 | 0.63562 | 20.3781
518 | TRUE | P18010 | Before | P18010 | 2005-08-11 18:07 | 2017-05-02 | 2016-03-25 | Cutout failure | Equipment Failure |  |  | 2018-06-29 | 3.6685 | 17.3452
518 | TRUE | P18010 | Before | P18010 | 2005-11-10 09:36 | 2017-05-02 | 2016-03-25 | Cutout failure | Equipment Failure |  |  | 2018-06-29 | 3.6685 | 17.3452
518 | TRUE | P41995 | Before | P41995 | 2012-03-07 07:19 | 2019-12-12 | 2016-10-21 | Cutout failure | Equipment Failure |  |  | 2016-06-04 | 1.0548 | 19.9589
518 | TRUE | P112513 | Before | P112513 | 2019-01-26 08:14 | 2020-10-08 | 2020-07-13 | Cutout failure | Equipment Failure |  |  | 2020-09-15 | 0.23014 | 20.7836
518 | TRUE | P112586 | Before | P112586 | 2003-09-27 15:27 | 2018-03-01 | 2016-12-20 | Cutout failure | Equipment Failure |  |  | 2014-01-16 | 2.8384 | 18.1753
518 | TRUE | P115164 | Before | P115164 | 2012-05-13 12:57 | 2019-10-29 | 2019-01-22 | Cutout failure | Equipment Failure |  |  | 2019-04-16 | 1.1753 | 19.8384
518 | TRUE | P117857 | After | P117857 | 2020-03-24 06:36 | 2017-05-11 | 2016-08-22 | Cutout failure | Equipment Failure |  |  | 2020-07-28 | 3.6438 | 17.3699
518 | TRUE | P204314 | Before | P204314 | 2017-05-30 09:09 | 2020-09-15 | 2020-03-10 | Cutout failure | Equipment Failure |  |  | 2020-07-25 | 0.29315 | 20.7205
518 | TRUE | P214799 | Before | P214799 | 2007-09-11 10:21 | 2019-12-19 | 2018-08-20 | Cutout failure | Equipment Failure |  |  | 2019-05-02 | 1.0356 | 19.9781
518 | TRUE | P217600 | Before | P217600 | 2015-10-04 08:46 | 2017-04-06 | 2017-01-14 | Cutout failure | Equipment Failure |  |  | 2020-07-14 | 3.7397 | 17.274
518 | TRUE | P370071 | Before | P370071 | 2014-02-06 19:30 | 2016-05-20 | 2015-12-02 | Cutout failure | Equipment Failure |  |  | 2020-02-29 | 4.6192 | 16.3945
518 | TRUE | P510277 | Before | P510277 | 2010-11-12 18:49 | 2019-12-23 | 2019-06-10 | Cutout failure | Equipment Failure |  |  | 2020-04-22 | 1.0247 | 19.989
518 | TRUE | P13273 | Before | P13273 | 2013-10-06 10:06 | 2017-03-13 | 2016-09-26 | Cutout failure | Equipment Failure | Capacitor failure | 972-919CW | 2013-02-15 | 3.8055 | 17.2082
518 | TRUE | P412648 | Before | P412648 | 2016-03-24 14:14 | 2018-04-05 | 2016-10-14 | Cutout failure | Equipment Failure | Line-Xfmr deenerg for safety |  | 2015-08-12 | 2.7425 | 18.2712
512 | TRUE | P111589 | Before | P111589 | 2002-10-22 17:16 | 2018-03-01 | 2017-05-03 | Faulted cable | Equipment Failure |  | D7614476147 | 2017-05-26 | 2.8384 | 18.1753
512 | TRUE | P115164 | Before | P115164 | 2013-10-01 20:46 | 2019-10-29 | 2019-01-22 | Faulted cable | Equipment Failure |  | D3923076905 | 2019-04-16 | 1.1753 | 19.8384
512 | TRUE | P213266 | Before | P213266 | 2011-11-07 11:09 | 2020-04-16 | 2019-03-28 | Faulted cable | Equipment Failure |  | D3996076910 | 2016-02-05 | 0.70959 | 20.3041
512 | TRUE | P213267 | Before | P213267 | 2018-09-07 07:20 | 2020-04-16 | 2019-03-28 | Faulted cable | Equipment Failure |  | H4019076790 | 2020-02-07 | 0.70959 | 20.3041
512 | TRUE | P213271 | Before | P213271 | 2012-08-23 15:05 | 2020-04-16 | 2019-03-28 | Faulted cable | Equipment Failure |  | D4005276959 | 2020-02-07 | 0.70959 | 20.3041
512 | TRUE | P316594 | Before | P316594 | 2008-07-12 22:08 | 2019-01-10 | 2018-01-08 | Faulted cable | Equipment Failure |  | D4401571860 | 2020-12-29 | 1.9753 | 19.0384
512 | TRUE | P412648 | Before | P412648 | 2010-10-01 11:45 | 2018-04-05 | 2016-10-14 | Faulted cable | Equipment Failure |  | H3434189401 | 2015-08-12 | 2.7425 | 18.2712
512 | TRUE | P513743 | Before | P513743 | 2013-03-14 20:14 | 2018-03-29 | 2017-12-01 | Faulted cable | Equipment Failure |  | D4462070860 | 2020-11-25 | 2.7616 | 18.2521
512 | TRUE | P616732 | Before | P616732 | 2004-08-24 22:15 | 2017-08-17 | 2017-07-06 | Faulted cable | Equipment Failure |  | D4536034400 | 2020-12-15 | 3.3753 | 17.6384
512 | TRUE | P817313 | Before | P817313 | 2003-08-30 15:54 | 2018-06-08 | 2018-03-19 | Faulted cable | Equipment Failure |  | H3944577597 | 2020-08-26 | 2.5671 | 18.4466
512 | TRUE | P273610 | After | P273610 | 2019-11-07 09:58 | 2015-12-04 | 2015-04-22 | Faulted cable | Equipment Failure | Interruption to serving Dist. Circ. | D200733 | 2015-12-04 | 5.0795 | 15.9342
508 | TRUE | P112447 | Before | P112447 | 2001-08-15 11:48 | 2019-09-13 | 2019-04-22 | Flashover/equip contam/overload | Equipment Failure |  |  | 2013-02-21 | 1.3014 | 19.7123
508 | TRUE | P112447 | Before | P112447 | 2001-08-18 10:03 | 2019-09-13 | 2019-04-22 | Flashover/equip contam/overload | Equipment Failure |  |  | 2013-02-21 | 1.3014 | 19.7123
522 | TRUE | P113838 | After | P113838 | 2020-11-26 16:15 | 2019-12-23 | 2015-09-01 | Fuse - overload/inadequate size/fatigue | Equipment Failure |  |  | 2019-12-13 | 1.0247 | 19.989
522 | TRUE | P173170 | After | P173170 | 2020-08-26 10:22 | 2015-11-21 | 2015-10-10 | Fuse - overload/inadequate size/fatigue | Equipment Failure |  |  | 2010-10-01 | 5.1151 | 15.8986
520 | TRUE | P119038 | Before | P119038 | 2010-04-04 14:14 | 2018-06-08 | 2018-03-12 | Fuse holder/fuse cabinet failed | Equipment Failure |  |  | 2018-05-04 | 2.5671 | 18.4466
520 | TRUE | P211409 | After | P211409 | 2018-09-13 16:19 | 2016-12-16 | 2016-07-13 | Fuse holder/fuse cabinet failed | Equipment Failure |  |  | 2016-08-23 | 4.0438 | 16.9699
520 | TRUE | P218274 | Before | P218274 | 2007-01-25 04:16 | 2017-02-09 | 2016-12-04 | Fuse holder/fuse cabinet failed | Equipment Failure |  |  | 2018-03-26 | 3.8932 | 17.1205
520 | TRUE | P317990 | After | P317990 | 2018-06-29 12:45 | 2016-01-25 | 2015-10-09 | Fuse holder/fuse cabinet failed | Equipment Failure |  |  | 2018-08-01 | 4.937 | 16.0767
520 | TRUE | P511470 | Before | P511470 | 2011-05-31 09:41 | 2017-11-17 | 2016-12-15 | Fuse holder/fuse cabinet failed | Equipment Failure |  |  | 2019-08-12 | 3.1233 | 17.8904
520 | TRUE | P512483 | Before | P512483 | 2006-07-15 08:07 | 2018-07-25 | 2018-02-14 | Fuse holder/fuse cabinet failed | Equipment Failure |  |  | 2019-02-02 | 2.4384 | 18.5753
522 | TRUE | P19533 | Before | P19533 | 2007-09-01 13:00 | 2019-12-27 | 2019-06-10 | Fuse overloaded/inadequate fuse size | Equipment Failure |  |  | 2019-12-05 | 1.0137 | 20
522 | TRUE | P114287 | Before | P114287 | 2017-01-08 09:34 | 2017-03-30 | 2016-10-24 | Fuse overloaded/inadequate fuse size | Equipment Failure |  |  | 2019-09-10 | 3.7589 | 17.2548
522 | TRUE | P162173 | Before | P162173 | 2012-10-11 12:40 | 2016-05-24 | 2016-04-19 | Fuse overloaded/inadequate fuse size | Equipment Failure |  |  | 2020-09-08 | 4.6082 | 16.4055
522 | TRUE | P212520 | Before | P212520 | 2016-01-08 06:16 | 2017-02-09 | 2016-12-04 | Fuse overloaded/inadequate fuse size | Equipment Failure |  |  | 2018-03-26 | 3.8932 | 17.1205
522 | TRUE | P213217 | Before | P213217 | 2017-04-01 16:47 | 2019-10-08 | 2019-04-25 | Fuse overloaded/inadequate fuse size | Equipment Failure |  |  | 2019-10-08 | 1.2329 | 19.7808
522 | TRUE | P216307 | Before | P216307 | 2015-09-02 08:48 | 2020-11-07 | 2020-09-11 | Fuse overloaded/inadequate fuse size | Equipment Failure |  |  | 2018-03-26 | 0.14795 | 20.8658
522 | TRUE | P217466 | Before | P217466 | 2016-02-27 10:04 | 2019-12-19 | 2019-04-22 | Fuse overloaded/inadequate fuse size | Equipment Failure |  |  | 2019-12-30 | 1.0356 | 19.9781
522 | TRUE | P218509 | Before | P218509 | 2014-05-27 18:25 | 2018-06-08 | 2017-11-29 | Fuse overloaded/inadequate fuse size | Equipment Failure |  |  | 2015-05-06 | 2.5671 | 18.4466
522 | TRUE | P218509 | Before | P218509 | 2014-05-27 23:57 | 2018-06-08 | 2017-11-29 | Fuse overloaded/inadequate fuse size | Equipment Failure |  |  | 2015-05-06 | 2.5671 | 18.4466
522 | TRUE | P475949 | Before | P475949 | 2016-12-03 09:33 | 2019-12-12 | 2019-10-23 | Fuse overloaded/inadequate fuse size | Equipment Failure |  |  | 2020-12-03 | 1.0548 | 19.9589
522 | TRUE | P972535 | Before | P972535 | 2015-01-09 16:05 | 2020-09-15 | 2020-03-10 | Fuse overloaded/inadequate fuse size | Equipment Failure |  |  | 2017-11-17 | 0.29315 | 20.7205
528 | TRUE | P213993 | Before | P213993 | 2020-02-10 12:05 | 2020-04-17 | 2019-12-11 | Hardware failure | Equipment Failure |  |  | 2020-04-22 | 0.70685 | 20.3068
528 | TRUE | P213993 | Before | P213993 | 2020-02-10 12:10 | 2020-04-17 | 2019-12-11 | Hardware failure | Equipment Failure |  |  | 2020-04-22 | 0.70685 | 20.3068
530 | TRUE | P412637 | Before | P412637 | 2008-09-17 15:32 | 2018-04-05 | 2016-10-14 | Insulator/pin failure/wire floating | Equipment Failure | Crossarm failure |  | 2015-08-12 | 2.7425 | 18.2712
410 | TRUE | P13274 | After | P13274 | 2019-03-06 01:21 | 2017-03-13 | 2016-09-26 | Lightning Arrester/Transformer failure | Equipment Failure |  |  | 2020-08-26 | 3.8055 | 17.2082
410 | TRUE | P172678 | Before | P172678 | 2003-09-02 16:09 | 2017-08-30 | 2017-02-04 | Lightning Arrester/Transformer failure | Equipment Failure |  |  | 2018-03-13 | 3.3397 | 17.674
410 | TRUE | P515477 | After | P515477 | 2018-10-12 21:20 | 2017-04-06 | 2017-01-14 | Lightning Arrester/Transformer failure | Equipment Failure |  |  | 2020-07-14 | 3.7397 | 17.274
410 | TRUE | P515477 | After | P515477 | 2019-03-06 01:18 | 2017-04-06 | 2017-01-14 | Lightning Arrester/Transformer failure | Equipment Failure |  |  | 2020-07-14 | 3.7397 | 17.274
410 | TRUE | P613606 | Before | P613606 | 2003-12-25 19:08 | 2018-06-07 | 2018-01-25 | Lightning Arrester/Transformer failure | Equipment Failure |  |  | 2018-04-03 | 2.5699 | 18.4438
410 | TRUE | P610754 | Before | P610754 | 2014-08-20 07:43 | 2018-06-07 | 2017-12-26 | Lightning Arrester/Transformer failure | Equipment Failure | Arrester (lightning) failure |  | 2020-10-22 | 2.5699 | 18.4438
410 | TRUE | P42037 | Before | P42037 | 2012-08-21 14:07 | 2019-12-12 | 2016-10-21 | Lightning Arrester/Transformer failure | Equipment Failure | Conductor contact/wire slap |  | 2016-06-04 | 1.0548 | 19.9589
410 | TRUE | P113858 | Before | P113858 | 2007-03-22 17:02 | 2019-09-19 | 2019-06-24 | Lightning Arrester/Transformer failure | Equipment Failure | Conductor failure/wire down | P113859 | 2011-03-01 | 1.2849 | 19.7288
410 | TRUE | P115836 | Before | P163664 | 2012-09-09 16:11 | 2020-04-16 | 2019-03-28 | Lightning Arrester/Transformer failure | Equipment Failure | Conductor failure/wire down | P115836 | 2010-12-01 | 0.70959 | 20.3041
410 | TRUE | P411943 | Before | P411943 | 2008-05-22 13:31 | 2019-09-19 | 2019-06-24 | Lightning Arrester/Transformer failure | Equipment Failure | Conductor failure/wire down | P612230 | 2014-07-31 | 1.2849 | 19.7288
410 | TRUE | P17664 | Before | P17664 | 2005-02-24 18:13 | 2016-07-15 | 2016-06-25 | Lightning Arrester/Transformer failure | Equipment Failure | Cutout failure |  | 2016-04-08 | 4.4658 | 16.5479
410 | TRUE | P107547 | Before | P107547 | 2012-08-16 13:37 | 2020-02-05 | 2019-11-01 | Lightning Arrester/Transformer failure | Equipment Failure | Cutout failure |  | 2020-02-18 | 0.90411 | 20.1096
410 | TRUE | P19533 | Before | P19533 | 2003-09-04 15:31 | 2019-12-27 | 2019-06-10 | Lightning Arrester/Transformer failure | Equipment Failure | Fuse holder/fuse cabinet failed |  | 2019-12-05 | 1.0137 | 20
410 | TRUE | P228375 | Before | P228375 | 2010-10-19 15:35 | 2018-07-25 | 2018-02-14 | Lightning Arrester/Transformer failure | Equipment Failure | Load unbalance | 520-33R | 2018-07-11 | 2.4384 | 18.5753
410 | TRUE | P114914 | Before | P311259 | 2015-03-02 10:45 | 2017-01-19 | 2016-10-04 | Lightning Arrester/Transformer failure | Equipment Failure | OH connector failure (jumper/splice/squeeze-on) | P114914 | 2018-03-26 | 3.9507 | 17.063
410 | TRUE | P310528 | Before | P310528 | 2011-09-15 15:19 | 2020-04-24 | 2020-02-27 | Lightning Arrester/Transformer failure | Equipment Failure | Pole broke/rotted/on fire |  | 2020-04-12 | 0.68767 | 20.326
410 | TRUE | P36016 | Before | P36016 | 2005-02-24 17:39 | 2018-06-08 | 2018-03-19 | Lightning Arrester/Transformer failure | Equipment Failure | Transformer faulted/mechanical | STA 215-712 | 2020-08-26 | 2.5671 | 18.4466
410 | TRUE | P41277 | Before | P41277 | 2005-08-15 09:11 | 2018-07-23 | 2018-07-01 | Lightning Arrester/Transformer failure | Equipment Failure | Transformer faulted/mechanical | STA 445-96 | 2020-09-08 | 2.4438 | 18.5699
410 | TRUE | P114273 | Before | P114273 | 2007-03-22 18:14 | 2017-04-19 | 2016-12-09 | Lightning Arrester/Transformer failure | Equipment Failure | Transformer faulted/mechanical | STA 175-16 | 2020-12-29 | 3.7041 | 17.3096
410 | TRUE | P211064 | Before | P211064 | 2015-07-18 09:39 | 2017-05-17 | 2017-01-30 | Lightning Arrester/Transformer failure | Equipment Failure | Transformer faulted/mechanical | STA 176-210 | 2017-05-17 | 3.6274 | 17.3863
410 | TRUE | P218395 | Before | P311538 | 2004-08-13 07:45 | 2019-04-05 | 2018-05-21 | Lightning Arrester/Transformer failure | Equipment Failure | Transformer faulted/mechanical | P218395 | 2018-08-30 | 1.7425 | 19.2712
410 | TRUE | P311685 | Before | P311685 | 2005-09-20 06:30 | 2019-04-05 | 2018-06-27 | Lightning Arrester/Transformer failure | Equipment Failure | Transformer faulted/mechanical | Sta. 217-181 | 2019-01-25 | 1.7425 | 19.2712
410 | TRUE | P514111 | After | P514111 | 2016-10-24 18:51 | 2016-01-25 | 2015-10-09 | Lightning Arrester/Transformer failure | Equipment Failure | Transformer faulted/mechanical |  | 2018-08-01 | 4.937 | 16.0767
410 | TRUE | P611658 | Before | P611658 | 2015-07-18 07:01 | 2017-10-06 | 2016-12-01 | Lightning Arrester/Transformer failure | Equipment Failure | Transformer faulted/mechanical | STA 971-613 | 2017-10-04 | 3.2384 | 17.7753
410 | TRUE | P715914 | Before | P715914 | 2014-03-01 10:15 | 2019-01-23 | 2018-08-24 | Lightning Arrester/Transformer failure | Equipment Failure | Transformer faulted/mechanical | STA 350242 | 2019-01-10 | 1.9397 | 19.074
515 | TRUE | P19585 | Before | P19585 | 2019-11-28 11:37 | 2019-12-27 | 2019-06-25 | OH connector failure (jumper/splice/squeeze-on) | Equipment Failure |  |  | 2015-01-20 | 1.0137 | 20
515 | TRUE | P19586 | Before | P19586 | 2015-08-13 20:33 | 2019-12-27 | 2019-06-25 | OH connector failure (jumper/splice/squeeze-on) | Equipment Failure |  |  | 2019-08-27 | 1.0137 | 20
515 | TRUE | P42037 | Before | P42037 | 2016-03-28 21:58 | 2019-12-12 | 2016-10-21 | OH connector failure (jumper/splice/squeeze-on) | Equipment Failure |  |  | 2016-06-04 | 1.0548 | 19.9589
515 | TRUE | P111573 | After | P111573 | 2019-09-04 14:48 | 2018-03-01 | 2017-05-03 | OH connector failure (jumper/splice/squeeze-on) | Equipment Failure |  |  | 2017-05-26 | 2.8384 | 18.1753
515 | TRUE | P112872 | Before | P112872 | 2015-07-07 06:06 | 2020-08-27 | 2020-02-12 | OH connector failure (jumper/splice/squeeze-on) | Equipment Failure |  |  | 2016-09-13 | 0.34521 | 20.6685
515 | TRUE | P119035 | Before | P119035 | 2009-06-25 08:01 | 2018-06-08 | 2018-03-12 | OH connector failure (jumper/splice/squeeze-on) | Equipment Failure |  |  | 2018-05-04 | 2.5671 | 18.4466
515 | TRUE | P190447 | Before | P190447 | 2014-02-28 15:07 | 2018-06-08 | 2018-03-19 | OH connector failure (jumper/splice/squeeze-on) | Equipment Failure |  |  | 2020-08-26 | 2.5671 | 18.4466
515 | TRUE | P213206 | Before | P213206 | 2007-05-18 13:36 | 2019-08-01 | 2018-09-21 | OH connector failure (jumper/splice/squeeze-on) | Equipment Failure |  |  | 2019-04-05 | 1.4192 | 19.5945
515 | TRUE | P215656 | Before | P215656 | 2015-01-24 04:28 | 2019-09-13 | 2019-04-22 | OH connector failure (jumper/splice/squeeze-on) | Equipment Failure |  |  | 2019-09-13 | 1.3014 | 19.7123
515 | TRUE | P312919 | Before | P312919 | 2014-12-20 12:41 | 2019-06-14 | 2019-02-09 | OH connector failure (jumper/splice/squeeze-on) | Equipment Failure |  |  | 2019-05-15 | 1.5507 | 19.463
515 | TRUE | P312924 | Before | P312924 | 2016-08-09 08:43 | 2019-06-14 | 2019-02-09 | OH connector failure (jumper/splice/squeeze-on) | Equipment Failure |  |  | 2014-09-12 | 1.5507 | 19.463
515 | TRUE | P312927 | Before | P312927 | 2014-04-29 16:34 | 2019-06-14 | 2019-02-09 | OH connector failure (jumper/splice/squeeze-on) | Equipment Failure |  |  | 2019-05-15 | 1.5507 | 19.463
515 | TRUE | P378660 | Before | P378660 | 2017-11-10 07:52 | 2017-12-04 | 2017-10-02 | OH connector failure (jumper/splice/squeeze-on) | Equipment Failure |  |  | 2017-05-24 | 3.0767 | 17.937
515 | TRUE | P412648 | After | P412648 | 2019-05-30 11:42 | 2018-04-05 | 2016-10-14 | OH connector failure (jumper/splice/squeeze-on) | Equipment Failure |  |  | 2015-08-12 | 2.7425 | 18.2712
515 | TRUE | P514473 | Before | P514473 | 2011-09-07 14:34 | 2018-06-07 | 2018-01-25 | OH connector failure (jumper/splice/squeeze-on) | Equipment Failure |  |  | 2018-04-03 | 2.5699 | 18.4438
515 | TRUE | P518556 | Before | P518556 | 2012-03-13 23:51 | 2017-03-09 | 2016-12-01 | OH connector failure (jumper/splice/squeeze-on) | Equipment Failure |  |  | 2017-02-04 | 3.8164 | 17.1973
515 | TRUE | P18659 | Before | P18659 | 2012-03-20 03:37 | 2019-03-04 | 2018-09-04 | OH connector failure (jumper/splice/squeeze-on) | Equipment Failure | Conductor failure/wire down | P214133 | 2019-03-04 | 1.8301 | 19.1836
515 | TRUE | P228375 | Before | P512509 | 2012-04-22 05:07 | 2018-07-25 | 2018-02-14 | OH connector failure (jumper/splice/squeeze-on) | Equipment Failure | Conductor failure/wire down | P228375 | 2018-07-11 | 2.4384 | 18.5753
515 | TRUE | P19586 | Before | P19586 | 2016-11-24 06:29 | 2019-12-27 | 2019-06-25 | OH connector failure (jumper/splice/squeeze-on) | Equipment Failure | Wind - wires slap/pole down |  | 2019-08-27 | 1.0137 | 20
532 | TRUE | P17854 | Before | P17854 | 2003-12-26 13:15 | 2017-05-11 | 2016-08-22 | Pole broke/rotted/on fire | Equipment Failure |  |  | 2020-07-28 | 3.6438 | 17.3699
532 | TRUE | P105882 | After | P105882 | 2018-01-16 20:14 | 2016-07-15 | 2016-06-25 | Pole broke/rotted/on fire | Equipment Failure |  |  | 2018-01-17 | 4.4658 | 16.5479
532 | TRUE | P109613 | Before | P109613 | 2013-05-02 17:29 | 2018-07-25 | 2018-02-14 | Pole broke/rotted/on fire | Equipment Failure |  |  | 2018-07-11 | 2.4384 | 18.5753
532 | TRUE | P173172 | Before | P173172 | 2003-03-29 12:16 | 2015-11-21 | 2015-10-10 | Pole broke/rotted/on fire | Equipment Failure |  |  | 2020-09-08 | 5.1151 | 15.8986
532 | TRUE | P247679 | Before | P247679 | 2015-12-26 14:24 | 2016-05-20 | 2015-12-02 | Pole broke/rotted/on fire | Equipment Failure |  |  | 2020-02-29 | 4.6192 | 16.3945
532 | TRUE | P317486 | Before | P317486 | 2017-12-06 17:30 | 2018-08-31 | 2018-06-11 | Pole broke/rotted/on fire | Equipment Failure |  |  | 2017-12-07 | 2.337 | 18.6767
532 | TRUE | P514950 | Before | P514950 | 2019-06-24 14:04 | 2020-04-28 | 2020-04-01 | Pole broke/rotted/on fire | Equipment Failure |  |  | 2019-06-25 | 0.67671 | 20.337
532 | TRUE | P515224 | Before | P515224 | 2017-08-17 09:50 | 2018-06-07 | 2018-01-25 | Pole broke/rotted/on fire | Equipment Failure |  |  | 2018-04-03 | 2.5699 | 18.4438
532 | TRUE | P814894 | Before | P814894 | 2019-02-10 12:15 | 2020-08-27 | 2020-02-12 | Pole broke/rotted/on fire | Equipment Failure |  |  | 2019-02-10 | 0.34521 | 20.6685
532 | TRUE | P616116 | Before | P116279 | 2013-12-01 13:31 | 2018-05-10 | 2017-02-16 | Pole broke/rotted/on fire | Equipment Failure | Conductor failure/wire down | P616116 | 2013-12-02 | 2.6466 | 18.3671
532 | TRUE | P113596 | Before | P113596 | 2017-01-23 11:28 | 2017-06-30 | 2016-10-24 | Pole broke/rotted/on fire | Equipment Failure | Line-Xfmr deenerg for safety |  | 2020-11-10 | 3.5068 | 17.5068
532 | TRUE | P318007 | Before | P318007 | 2013-12-27 14:35 | 2019-06-14 | 2019-01-22 | Pole broke/rotted/on fire | Equipment Failure | Line-Xfmr deenerg for safety |  | 2013-12-27 | 1.5507 | 19.463
534 | TRUE | P133517 | Before | P133517 | 2003-01-09 18:13 | 2019-10-29 | 2019-01-22 | Pothead failure | Equipment Failure |  |  | 2019-04-16 | 1.1753 | 19.8384
534 | TRUE | P133549 | After | P133549 | 2019-12-17 09:11 | 2016-07-20 | 2016-05-31 | Pothead failure | Equipment Failure |  | P113549 | 2018-11-12 | 4.4521 | 16.5616
534 | TRUE | P211167 | Before | P211167 | 2003-08-24 16:31 | 2018-06-26 | 2017-11-16 | Pothead failure | Equipment Failure |  |  | 2018-06-04 | 2.5178 | 18.4959
536 | TRUE | P41245 | Before | P41245 | 2006-09-08 08:17 | 2020-09-10 | 2020-06-03 | Recloser/breaker faulted/mechanical | Equipment Failure |  | 445-3R | 2020-08-31 | 0.30685 | 20.7068
536 | TRUE | P41245 | Before | P41245 | 2006-10-10 15:23 | 2020-09-10 | 2020-06-03 | Recloser/breaker faulted/mechanical | Equipment Failure |  | 445-3R(WEST | 2020-08-31 | 0.30685 | 20.7068
536 | TRUE | P41726 | Before | P41726 | 2006-03-02 09:32 | 2020-05-13 | 2020-01-16 | Recloser/breaker faulted/mechanical | Equipment Failure |  | 445-647R | 2020-05-04 | 0.63562 | 20.3781
536 | TRUE | P117820 | Before | P117820 | 2015-05-31 17:19 | 2019-12-11 | 2019-08-31 | Recloser/breaker faulted/mechanical | Equipment Failure |  | 350-15R | 2019-10-03 | 1.0575 | 19.9562
540 | TRUE | P161896 | Before | P161896 | 2005-09-19 15:07 | 2020-05-13 | 2020-01-16 | Regulator faulted/mechanical | Equipment Failure |  | 445-613G | 2020-05-04 | 0.63562 | 20.3781
540 | TRUE | P100597 | Before | P100597 | 2011-08-28 13:22 | 2017-05-18 | 2017-02-01 | Regulator faulted/mechanical | Equipment Failure | Line-Xfmr deenerg for safety | 221-212G1 | 2017-05-18 | 3.6247 | 17.389
517 | TRUE | P19534 | Before | P159533 | 2019-11-04 15:11 | 2019-12-27 | 2019-06-10 | Tee (dead break) failure | Equipment Failure | Conductor failure/wire down | P19534 | 2019-12-05 | 1.0137 | 20
550 | TRUE | P718259 | Before | P718259 | 2020-09-30 16:27 | 2020-11-07 | 2020-09-11 | Transformer (station) failure/contact | Equipment Failure |  | STA 972-907 | 2020-11-05 | 0.14795 | 20.8658
550 | TRUE | P376421 | Same Day | P376421 | 2020-11-20 10:27 | 2020-11-20 | 2020-02-20 | Transformer (station) failure/contact | Equipment Failure | Interruption from an adjacent circuit | STA 157-33 | 2020-11-12 | 0.11233 | 20.9014
550 | TRUE | P117175 | Before | P117175 | 2012-12-13 12:02 | 2017-05-08 | 2016-11-23 | Transformer faulted/mechanical | Equipment Failure |  | STA 1030-564 | 2018-06-14 | 3.6521 | 17.3616
550 | TRUE | P117176 | Before | P117176 | 2007-04-24 16:34 | 2017-05-08 | 2016-11-23 | Transformer faulted/mechanical | Equipment Failure |  | STA 1030-585 | 2018-06-14 | 3.6521 | 17.3616
550 | TRUE | P117927 | Before | P117927 | 2016-09-20 06:52 | 2018-05-29 | 2018-03-12 | Transformer faulted/mechanical | Equipment Failure |  | STA 221-661 | 2018-06-29 | 2.5945 | 18.4192
550 | TRUE | P172681 | Before | P172681 | 2015-05-08 07:58 | 2017-08-30 | 2017-02-04 | Transformer faulted/mechanical | Equipment Failure |  | STA 78-258 | 2018-03-13 | 3.3397 | 17.674
550 | TRUE | P172684 | Before | P172684 | 2014-09-24 07:32 | 2017-08-30 | 2017-02-04 | Transformer faulted/mechanical | Equipment Failure |  | STA 78-92 | 2018-03-13 | 3.3397 | 17.674
550 | TRUE | P173034 | After | P134752 | 2019-09-29 10:07 | 2016-03-24 | 2015-05-28 | Transformer faulted/mechanical | Equipment Failure |  | P173034 | 2018-09-28 | 4.7753 | 16.2384
550 | TRUE | P311538 | Before | P311538 | 2005-09-26 07:38 | 2019-04-05 | 2018-05-21 | Transformer faulted/mechanical | Equipment Failure |  | STA 217-55 | 2018-08-30 | 1.7425 | 19.2712
550 | TRUE | P376421 | Before | P376421 | 2011-07-01 21:25 | 2020-11-20 | 2020-02-20 | Transformer faulted/mechanical | Equipment Failure |  | STA 157-33 | 2020-11-12 | 0.11233 | 20.9014
550 | TRUE | P418717 | Before | P418717 | 2005-04-22 07:35 | 2018-05-15 | 2017-12-11 | Transformer faulted/mechanical | Equipment Failure |  | STA 350-1829 | 2018-05-08 | 2.6329 | 18.3808
550 | TRUE | P472952 | After | P472952 | 2019-08-25 17:51 | 2016-05-20 | 2015-12-02 | Transformer faulted/mechanical | Equipment Failure |  | STA 240-443 | 2020-02-29 | 4.6192 | 16.3945
550 | TRUE | P475953 | Before | P475953 | 2010-06-02 14:56 | 2019-12-12 | 2019-10-23 | Transformer faulted/mechanical | Equipment Failure |  | STA 157-841 | 2020-12-03 | 1.0548 | 19.9589
550 | TRUE | P512491 | Before | P512491 | 2016-10-24 07:33 | 2018-07-25 | 2018-02-14 | Transformer faulted/mechanical | Equipment Failure |  |  | 2018-07-11 | 2.4384 | 18.5753
550 | TRUE | P515056 | Before | P515056 | 2016-08-21 15:57 | 2019-03-04 | 2018-09-04 | Transformer faulted/mechanical | Equipment Failure |  | STA 217-178 | 2019-03-04 | 1.8301 | 19.1836
550 | TRUE | P515517 | Before | P515517 | 2018-07-30 08:27 | 2020-03-10 | 2019-12-06 | Transformer faulted/mechanical | Equipment Failure |  | STA 222-471 | 2010-10-05 | 0.81096 | 20.2027
550 | TRUE | P572189 | Before | P572189 | 2017-03-16 14:51 | 2020-12-14 | 2020-05-21 | Transformer faulted/mechanical | Equipment Failure |  | STA 157-115 | 2020-09-26 | 0.046575 | 20.9671
550 | TRUE | P612459 | After | P612459 | 2018-10-04 05:53 | 2017-02-09 | 2016-11-14 | Transformer faulted/mechanical | Equipment Failure |  | STA 175-107 | 2018-03-26 | 3.8932 | 17.1205
550 | TRUE | P14991 | Before | P14991 | 2008-02-20 14:15 | 2019-09-13 | 2019-04-22 | Transformer faulted/mechanical | Equipment Failure | Line-Xfmr deenerg for safety | STA 217-224 | 2019-09-13 | 1.3014 | 19.7123
550 | TRUE | P41777 | Before | P41777 | 2010-01-20 11:23 | 2019-12-12 | 2016-10-21 | Transformer faulted/mechanical | Equipment Failure | Line-Xfmr deenerg for safety | STA. 444-140 | 2016-06-04 | 1.0548 | 19.9589
550 | TRUE | P274702 | Before | P274702 | 2012-07-17 08:57 | 2016-03-24 | 2015-05-28 | Transformer faulted/mechanical | Equipment Failure | Line-Xfmr deenerg for safety | STA 79-129 | 2018-09-28 | 4.7753 | 16.2384
552 | TRUE | P46574 | Before | P46574 | 2012-08-13 20:50 | 2019-12-12 | 2016-10-21 | Transformer overloaded/electrical | Equipment Failure |  | 444-75B | 2016-04-08 | 1.0548 | 19.9589
304 | FALSE | P173190 | Before | P173190 | 2005-10-04 14:04 |  |  | Animal contact | Foreign Object In Line | Pothead failure |  | 2015-12-07 | 5.0712 | 15.9425
304 | FALSE | P173190 | Before | P173190 | 2007-03-11 13:35 |  |  | Animal contact | Foreign Object In Line | Pothead failure |  | 2015-12-07 | 5.0712 | 15.9425
304 | FALSE | P173191 | Before | P173191 | 2007-09-13 08:01 |  |  | Animal contact | Foreign Object In Line | Transformer faulted/mechanical | STA 442-98 | 2016-10-11 | 4.2247 | 16.789
304 | FALSE | P811525 | After | P811525 | 2018-10-02 07:52 |  |  | Animal contact | Foreign Object In Line | Transformer faulted/mechanical | STA 222-476 | 2016-04-08 | 4.7342 | 16.2795
315 | FALSE | P413246 | After | P413246 | 2017-02-10 12:09 |  |  | Balloon contact | Foreign Object In Line | Fuse overloaded/inadequate fuse size |  | 2016-04-06 | 4.7397 | 16.274
308 | FALSE | P18901 | Before | P18901 | 2001-10-13 06:57 |  |  | Bird contact | Foreign Object In Line |  |  | 2016-03-21 | 4.7836 | 16.2301
308 | FALSE | P19722 | Before | P19722 | 2001-11-10 06:18 |  |  | Bird contact | Foreign Object In Line |  |  | 2015-05-27 | 5.6027 | 15.411
308 | FALSE | P114072 | Before | P114072 | 2009-10-10 14:38 |  |  | Bird contact | Foreign Object In Line | Arrester (lightning) failure |  | 2016-01-25 | 4.937 | 16.0767
308 | FALSE | P114072 | Before | P114072 | 2010-09-13 16:12 |  |  | Bird contact | Foreign Object In Line | Arrester (lightning) failure |  | 2016-01-25 | 4.937 | 16.0767
308 | FALSE | P42128 | Before | P42128 | 2011-07-05 08:53 |  |  | Bird contact | Foreign Object In Line | Conductor contact/wire slap | 444-3R | 2012-10-08 | 8.2356 | 12.7781
308 | FALSE | P216435 | Before | P216435 | 2011-11-21 06:47 |  |  | Bird contact | Foreign Object In Line | Conductor contact/wire slap |  | 2016-03-21 | 4.7836 | 16.2301
308 | FALSE | P218742 | After | P218742 | 2016-07-12 04:38 |  |  | Bird contact | Foreign Object In Line | Conductor contact/wire slap |  | 2016-04-06 | 4.7397 | 16.274
308 | FALSE | P610498 | Before | P610498 | 2012-11-16 07:57 |  |  | Bird contact | Foreign Object In Line | Conductor contact/wire slap | P610499 | 2015-04-27 | 5.6849 | 15.3288
308 | FALSE | P40839 | Before | P40839 | 2013-11-24 17:11 |  |  | Bird contact | Foreign Object In Line | Conductor failure/wire down | P40840 | 2016-04-08 | 4.7342 | 16.2795
308 | FALSE | P278723 | Before | P278723 | 2012-06-03 19:32 |  |  | Bird contact | Foreign Object In Line | Conductor failure/wire down | P278724 | 2019-02-13 | 1.8822 | 19.1315
308 | FALSE | P278724 | Before | P278724 | 2008-09-21 05:45 |  |  | Bird contact | Foreign Object In Line | Conductor failure/wire down | P278725 | 2019-02-13 | 1.8822 | 19.1315
308 | FALSE | P203753 | After | P203753 | 2020-06-12 07:10 |  |  | Bird contact | Foreign Object In Line | Cutout failure | 237-1164 | 2016-05-20 | 4.6192 | 16.3945
308 | FALSE | P40906 | After | P40906 | 2020-08-28 18:58 |  |  | Bird contact | Foreign Object In Line | Flashover due to contamination/overload/tracking |  | 2014-09-13 | 6.3041 | 14.7096
308 | FALSE | P678760 | Before | P678760 | 2010-07-30 06:46 |  |  | Bird contact | Foreign Object In Line | Grd. bank failure | STA 442-268GB | 2016-04-01 | 4.7534 | 16.2603
308 | FALSE | P176372 | After | P176372 | 2020-11-05 10:56 |  |  | Bird contact | Foreign Object In Line | Transformer (station) failure/contact | STA 240-388 | 2016-07-22 | 4.4466 | 16.5671
308 | FALSE | P252396 | After | P252396 | 2020-06-15 06:37 |  |  | Bird contact | Foreign Object In Line | Transformer (station) failure/contact | STA 441-295 | 2014-11-11 | 6.1425 | 14.8712
308 | FALSE | P252396 | After | P252396 | 2020-06-19 17:56 |  |  | Bird contact | Foreign Object In Line | Transformer (station) failure/contact | STA 441-295 | 2014-11-11 | 6.1425 | 14.8712
308 | FALSE | P116580 | Before | P116580 | 2013-04-08 07:06 |  |  | Bird contact | Foreign Object In Line | Transformer faulted/mechanical | STA 237-131 | 2016-03-11 | 4.811 | 16.2027
308 | FALSE | P275862 | Before | P275862 | 2007-06-23 10:56 |  |  | Bird contact | Foreign Object In Line | Transformer faulted/mechanical | STA 73-116 | 2016-12-02 | 4.0822 | 16.9315
308 | FALSE | P312944 | Before | P312944 | 2014-08-17 17:51 |  |  | Bird contact | Foreign Object In Line | Transformer faulted/mechanical | STA 237-272 | 2016-01-15 | 4.9644 | 16.0493
308 | FALSE | P377761 | After | P377761 | 2017-10-21 10:33 |  |  | Bird contact | Foreign Object In Line | Transformer faulted/mechanical | STA 78-215 | 2009-10-01 | 11.2575 | 9.7562
308 | FALSE | P511483 | Before | P511483 | 2005-07-14 07:43 |  |  | Bird contact | Foreign Object In Line | Transformer faulted/mechanical | 220-54 | 2015-08-31 | 5.3397 | 15.674
308 | FALSE | P777024 | Before | P777024 | 2012-09-29 10:49 |  |  | Bird contact | Foreign Object In Line | Transformer faulted/mechanical | STA 73-148 | 2014-12-23 | 6.0274 | 14.9863
310 | FALSE | P219466 | Before | P310516 | 2005-09-27 10:20 |  |  | Damage by gunshot | Foreign Object In Line | Line-Xfmr deenerg for safety | P219466 | 2016-05-04 | 4.663 | 16.3507
314 | FALSE | P275857 | Before | P275857 | 2013-09-01 14:11 |  |  | Foreign object in distribution line | Foreign Object In Line | Fuse holder/fuse cabinet failed |  | 2016-12-02 | 4.0822 | 16.9315
420 | FALSE | P18906 | Before | P18906 | 2002-02-10 10:52 |  |  | Tree contact due to storm/high wind | Foreign Object In Line | Conductor failure/wire down | P19717 | 2016-03-21 | 4.7836 | 16.2301
322 | FALSE | P173323 | Before | P173323 | 2002-11-10 00:13 |  |  | Tree fell on line | Foreign Object In Line |  | P173324 | 2014-12-23 | 6.0274 | 14.9863
322 | FALSE | P40498 | Before | P40498 | 2010-04-07 06:35 |  |  | Tree fell on line | Foreign Object In Line | Conductor contact/wire slap | P40499 | 2014-11-11 | 6.1425 | 14.8712
322 | FALSE | P19785 | Before | P17636 | 2008-09-19 22:26 |  |  | Tree fell on line | Foreign Object In Line | Conductor failure/wire down | P19785 | 2016-01-25 | 4.937 | 16.0767
322 | FALSE | P172862 | Before | P172862 | 2005-06-21 19:52 |  |  | Tree fell on line | Foreign Object In Line | Conductor failure/wire down | P375510 | 2014-12-23 | 6.0274 | 14.9863
322 | FALSE | P173199 | Before | P173199 | 2003-08-09 23:32 |  |  | Tree fell on line | Foreign Object In Line | Conductor failure/wire down | P973924 | 2016-10-11 | 4.2247 | 16.789
322 | FALSE | P214099 | Before | P214099 | 2005-09-21 07:20 |  |  | Tree fell on line | Foreign Object In Line | Conductor failure/wire down | P318180 | 2019-05-14 | 1.6356 | 19.3781
322 | FALSE | P178493 | Before | P178493 | 2016-01-07 04:19 |  |  | Tree fell on line | Foreign Object In Line | Pole broke/rotted/on fire |  | 2016-10-11 | 4.2247 | 16.789
322 | FALSE | P275379 | Before | P275379 | 2014-03-09 11:30 |  |  | Tree fell on line | Foreign Object In Line | Pole broke/rotted/on fire |  | 2016-02-01 | 4.9178 | 16.0959
322 | FALSE | P275379 | Before | P275379 | 2014-03-09 18:34 |  |  | Tree fell on line | Foreign Object In Line | Pole broke/rotted/on fire |  | 2016-02-01 | 4.9178 | 16.0959
426 | FALSE | P172823 | Before | P172823 | 2002-02-10 10:40 |  |  | Tree fell on line due to storm/wind | Foreign Object In Line | Conductor failure/wire down | P172824 | 2016-02-08 | 4.8986 | 16.1151
426 | FALSE | P173870 | Before | P173870 | 2008-10-13 23:55 |  |  | Tree fell on line due to storm/wind | Foreign Object In Line | Conductor failure/wire down |  | 2016-04-06 | 4.7397 | 16.274
426 | FALSE | P174991 | After | P478930J | 2013-09-05 14:00 |  |  | Tree fell on line due to storm/wind | Foreign Object In Line | Conductor failure/wire down | P174991 | 2011-08-01 | 9.4247 | 11.589
302 | TRUE | P318834 | Before | P318834 | 2010-05-15 10:11 | 2020-06-19 | 2020-03-26 | Aircraft | Foreign Object In Line | Pole broke/rotted/on fire |  | 2012-01-30 | 0.53425 | 20.4795
304 | TRUE | P19522 | Before | P19522 | 2018-11-26 05:54 | 2019-12-27 | 2019-06-10 | Animal contact | Foreign Object In Line | Conductor contact/wire slap | P19523 | 2019-12-05 | 1.0137 | 20
304 | TRUE | P219588 | Before | P219588 | 2019-03-14 06:49 | 2020-11-02 | 2020-01-30 | Animal contact | Foreign Object In Line | Conductor contact/wire slap |  | 2013-09-24 | 0.16164 | 20.8521
304 | TRUE | P511082 | Before | P511082 | 2010-06-03 14:02 | 2017-11-17 | 2017-05-30 | Animal contact | Foreign Object In Line | Fuse holder/fuse cabinet failed |  | 2017-11-17 | 3.1233 | 17.8904
304 | TRUE | P14694 | Before | P14694 | 2009-12-02 11:31 | 2016-05-11 | 2016-03-01 | Animal contact | Foreign Object In Line | Transformer faulted/mechanical | STA. 237-706 | 2018-03-26 | 4.6438 | 16.3699
304 | TRUE | P475826 | Before | P475826 | 2014-01-03 07:45 | 2018-10-02 | 2016-08-22 | Animal contact | Foreign Object In Line | Transformer faulted/mechanical | STA 240-149 | 2018-10-02 | 2.2493 | 18.7644
304 | TRUE | P818827 | Before | P818827 | 2006-06-23 09:08 | 2020-06-12 | 2020-04-28 | Animal contact | Foreign Object In Line | Transformer faulted/mechanical | STA 212-292 | 2020-05-16 | 0.55342 | 20.4603
304 | TRUE | P875593 | Before | P875593 | 2006-01-05 18:13 | 2020-09-15 | 2020-03-10 | Animal contact | Foreign Object In Line | Transformer faulted/mechanical | STA 157-520 | 2020-07-25 | 0.29315 | 20.7205
315 | TRUE | P112872 | Before | P112872 | 2020-03-03 16:25 | 2020-08-27 | 2020-02-12 | Balloon contact | Foreign Object In Line | Conductor contact/failure/overload/wire slap |  | 2016-09-13 | 0.34521 | 20.6685
315 | TRUE | P115222 | Before | P115222 | 2015-09-07 12:25 | 2017-02-09 | 2016-12-04 | Balloon contact | Foreign Object In Line | Conductor contact/wire slap |  | 2018-03-26 | 3.8932 | 17.1205
315 | TRUE | P213271 | Before | P817115 | 2017-08-19 16:55 | 2020-04-16 | 2019-03-28 | Balloon contact | Foreign Object In Line | Conductor contact/wire slap | P213271 | 2020-02-07 | 0.70959 | 20.3041
315 | TRUE | P214790 | After | P214790 | 2018-05-22 14:52 | 2018-03-01 | 2017-12-11 | Balloon contact | Foreign Object In Line | Conductor contact/wire slap | P214791 | 2018-03-01 | 2.8384 | 18.1753
315 | TRUE | P215732 | After | P215732 | 2019-03-14 14:42 | 2018-08-24 | 2016-12-06 | Balloon contact | Foreign Object In Line | Conductor contact/wire slap | P215733 | 2020-08-17 | 2.3562 | 18.6575
315 | TRUE | P317507 | Before | P317507 | 2018-06-04 13:24 | 2019-12-19 | 2019-04-22 | Balloon contact | Foreign Object In Line | Conductor contact/wire slap | P307516 | 2019-12-30 | 1.0356 | 19.9781
315 | TRUE | P475949 | Before | P475949 | 2010-05-31 10:24 | 2019-12-12 | 2019-10-23 | Balloon contact | Foreign Object In Line | Conductor contact/wire slap |  | 2020-12-03 | 1.0548 | 19.9589
315 | TRUE | P216503 | Before | P216503 | 2017-04-06 04:23 | 2020-08-05 | 2020-05-04 | Balloon contact | Foreign Object In Line | Conductor failure/wire down | P216504 | 2020-06-30 | 0.40548 | 20.6082
315 | TRUE | P17874 | After | P17874 | 2019-05-12 13:15 | 2017-08-02 | 2016-07-25 | Balloon contact | Foreign Object In Line | Pole broke/rotted/on fire |  | 2017-08-02 | 3.4164 | 17.5973
308 | TRUE | P19521 | Before | P19521 | 2001-10-24 06:51 | 2019-12-27 | 2019-06-10 | Bird contact | Foreign Object In Line |  | P19522 | 2019-12-05 | 1.0137 | 20
308 | TRUE | P876248 | Before | P876248 | 2002-06-10 08:44 | 2017-10-26 | 2017-08-28 | Bird contact | Foreign Object In Line |  |  | 2017-10-19 | 3.1836 | 17.8301
308 | TRUE | P217178 | Before | P217178 | 2007-06-09 11:34 | 2016-06-02 | 2016-04-18 | Bird contact | Foreign Object In Line | Arrester (lightning) failure | STA 237-993 | 2018-03-26 | 4.5836 | 16.4301
308 | TRUE | P213217 | After | P213217 | 2020-10-17 12:17 | 2019-10-08 | 2019-04-25 | Bird contact | Foreign Object In Line | Arrester failure |  | 2019-10-08 | 1.2329 | 19.7808
308 | TRUE | P216485 | Before | P216485 | 2010-08-16 09:31 | 2020-08-05 | 2020-05-04 | Bird contact | Foreign Object In Line | Capacitor failure | STA 212-247CF | 2020-06-30 | 0.40548 | 20.6082
308 | TRUE | P19522 | Before | P19522 | 2011-10-16 08:30 | 2019-12-27 | 2019-06-10 | Bird contact | Foreign Object In Line | Conductor contact/wire slap |  | 2019-12-05 | 1.0137 | 20
308 | TRUE | P19529 | Before | P19529 | 2005-03-17 06:25 | 2019-12-27 | 2019-06-10 | Bird contact | Foreign Object In Line | Conductor contact/wire slap |  | 2019-12-05 | 1.0137 | 20
308 | TRUE | P19529 | Before | P19529 | 2009-11-30 08:02 | 2019-12-27 | 2019-06-10 | Bird contact | Foreign Object In Line | Conductor contact/wire slap |  | 2019-12-05 | 1.0137 | 20
308 | TRUE | P19529 | Before | P19529 | 2009-12-30 06:42 | 2019-12-27 | 2019-06-10 | Bird contact | Foreign Object In Line | Conductor contact/wire slap |  | 2019-12-05 | 1.0137 | 20
308 | TRUE | P19529 | Before | P19529 | 2016-12-12 06:25 | 2019-12-27 | 2019-06-10 | Bird contact | Foreign Object In Line | Conductor contact/wire slap |  | 2019-12-05 | 1.0137 | 20
308 | TRUE | P19529 | Before | P19529 | 2016-12-14 06:19 | 2019-12-27 | 2019-06-10 | Bird contact | Foreign Object In Line | Conductor contact/wire slap |  | 2019-12-05 | 1.0137 | 20
308 | TRUE | P19529 | Before | P19529 | 2019-02-15 11:19 | 2019-12-27 | 2019-06-10 | Bird contact | Foreign Object In Line | Conductor contact/wire slap |  | 2019-12-05 | 1.0137 | 20
308 | TRUE | P19529 | Before | P19533 | 2007-04-15 06:12 | 2019-12-27 | 2019-06-10 | Bird contact | Foreign Object In Line | Conductor contact/wire slap | P19529 | 2019-12-05 | 1.0137 | 20
308 | TRUE | P46574 | Before | P46574 | 2015-06-15 12:35 | 2019-12-12 | 2016-10-21 | Bird contact | Foreign Object In Line | Conductor contact/wire slap |  | 2016-04-08 | 1.0548 | 19.9589
308 | TRUE | P76578 | After | P76578 | 2019-01-21 09:02 | 2018-10-02 | 2016-08-22 | Bird contact | Foreign Object In Line | Conductor contact/wire slap |  | 2018-10-02 | 2.2493 | 18.7644
308 | TRUE | P103768 | Before | P103768 | 2002-01-16 16:59 | 2017-03-30 | 2016-10-24 | Bird contact | Foreign Object In Line | Conductor contact/wire slap |  | 2019-09-10 | 3.7589 | 17.2548
308 | TRUE | P112502 | Before | P112502 | 2006-01-03 06:32 | 2020-10-08 | 2020-07-13 | Bird contact | Foreign Object In Line | Conductor contact/wire slap | P112503 | 2020-09-15 | 0.23014 | 20.7836
308 | TRUE | P117511 | Before | P117511 | 2004-08-22 07:48 | 2017-03-09 | 2016-12-01 | Bird contact | Foreign Object In Line | Conductor contact/wire slap |  | 2017-02-04 | 3.8164 | 17.1973
308 | TRUE | P227472 | Before | P227472 | 2008-10-20 07:24 | 2017-07-26 | 2017-06-05 | Bird contact | Foreign Object In Line | Conductor contact/wire slap |  | 2017-07-21 | 3.4356 | 17.5781
308 | TRUE | P311742 | After | P311742 | 2019-06-02 19:13 | 2016-07-25 | 2016-03-17 | Bird contact | Foreign Object In Line | Conductor contact/wire slap | P311743 | 2014-11-20 | 4.4384 | 16.5753
308 | TRUE | P311742 | Before | P311742 | 2013-11-11 05:56 | 2016-07-25 | 2016-03-17 | Bird contact | Foreign Object In Line | Conductor contact/wire slap | P311743 | 2014-11-20 | 4.4384 | 16.5753
308 | TRUE | P311743 | Before | P311744 | 2008-10-18 06:44 | 2016-07-25 | 2016-03-17 | Bird contact | Foreign Object In Line | Conductor contact/wire slap | P311743 | 2014-11-20 | 4.4384 | 16.5753
308 | TRUE | P511105 | Before | P511105 | 2013-06-22 16:12 | 2017-04-19 | 2016-12-09 | Bird contact | Foreign Object In Line | Conductor contact/wire slap |  | 2020-12-29 | 3.7041 | 17.3096
308 | TRUE | P13256 | Before | P13256 | 2016-12-12 05:56 | 2017-05-08 | 2016-10-17 | Bird contact | Foreign Object In Line | Conductor failure/wire down | P13262 | 2015-06-10 | 3.6521 | 17.3616
308 | TRUE | P13256 | Before | P13256 | 2016-12-12 06:56 | 2017-05-08 | 2016-10-17 | Bird contact | Foreign Object In Line | Conductor failure/wire down | P13262 | 2015-06-10 | 3.6521 | 17.3616
308 | TRUE | P19500 | Before | P19500 | 2009-05-25 08:18 | 2016-04-08 | 2014-12-20 | Bird contact | Foreign Object In Line | Conductor failure/wire down | P19501 | 2018-09-28 | 4.7342 | 16.2795
308 | TRUE | P19529 | Before | P19529 | 2002-02-24 09:30 | 2019-12-27 | 2019-06-10 | Bird contact | Foreign Object In Line | Conductor failure/wire down | P195280 | 2019-12-05 | 1.0137 | 20
308 | TRUE | P19529 | Before | P19529 | 2002-12-09 06:16 | 2019-12-27 | 2019-06-10 | Bird contact | Foreign Object In Line | Conductor failure/wire down | P19530 | 2019-12-05 | 1.0137 | 20
308 | TRUE | P19529 | Before | P19530 | 2016-12-20 06:15 | 2019-12-27 | 2019-06-10 | Bird contact | Foreign Object In Line | Conductor failure/wire down | P19529 | 2019-12-05 | 1.0137 | 20
308 | TRUE | P19568 | Before | P19568 | 2012-12-18 10:16 | 2019-12-27 | 2019-06-25 | Bird contact | Foreign Object In Line | Conductor failure/wire down | P19570 | 2015-08-24 | 1.0137 | 20
308 | TRUE | P112500 | Before | P112500 | 2005-02-20 06:22 | 2020-12-28 | 2020-10-30 | Bird contact | Foreign Object In Line | Conductor failure/wire down | P112499 | 2020-02-12 | 0.0082192 | 21.0055
308 | TRUE | P175942 | Before | P175942 | 2010-02-27 17:13 | 2020-11-13 | 2020-07-01 | Bird contact | Foreign Object In Line | Conductor failure/wire down | P175943 | 2018-04-18 | 0.13151 | 20.8822
308 | TRUE | P216106 | Before | P216105 | 2016-04-01 19:17 | 2017-08-17 | 2017-07-06 | Bird contact | Foreign Object In Line | Conductor failure/wire down | P216106 | 2020-12-15 | 3.3753 | 17.6384
308 | TRUE | P216301 | Before | P216301 | 2009-08-08 07:54 | 2017-05-08 | 2016-10-17 | Bird contact | Foreign Object In Line | Connector/jumper/splice/elbow/rack |  | 2018-03-26 | 3.6521 | 17.3616
308 | TRUE | P17664 | Before | P17664 | 2014-12-16 10:50 | 2016-07-15 | 2016-06-25 | Bird contact | Foreign Object In Line | Fuse holder/fuse cabinet failed |  | 2016-04-08 | 4.4658 | 16.5479
308 | TRUE | P19529 | Before | P19529 | 2002-09-28 10:57 | 2019-12-27 | 2019-06-10 | Bird contact | Foreign Object In Line | Fuse holder/fuse cabinet failed |  | 2019-12-05 | 1.0137 | 20
308 | TRUE | P710966 | Before | P710966 | 2015-02-08 09:12 | 2020-11-07 | 2020-09-11 | Bird contact | Foreign Object In Line | Fuse overloaded/inadequate fuse size |  | 2016-05-05 | 0.14795 | 20.8658
308 | TRUE | P116816 | Before | P116816 | 2008-06-06 08:57 | 2018-03-01 | 2017-04-26 | Bird contact | Foreign Object In Line | OH connector failure (jumper/splice/squeeze-on) |  | 2018-03-01 | 2.8384 | 18.1753
308 | TRUE | P813145 | Before | P813145 | 2007-06-21 05:42 | 2017-05-08 | 2016-11-23 | Bird contact | Foreign Object In Line | Pole broke/rotted/on fire |  | 2018-06-14 | 3.6521 | 17.3616
308 | TRUE | P475949 | Before |  | 2005-08-08 08:18 | 2019-12-12 | 2019-10-23 | Bird contact | Foreign Object In Line | Pothead failure | P475949 | 2020-12-03 | 1.0548 | 19.9589
308 | TRUE | P41320 | After | P41320 | 2019-07-19 17:06 | 2018-07-23 | 2018-07-01 | Bird contact | Foreign Object In Line | Transformer faulted/mechanical | STA 445-104 | 2020-09-08 | 2.4438 | 18.5699
308 | TRUE | P41575 | Before | P41575 | 2019-04-19 16:39 | 2020-05-29 | 2020-03-10 | Bird contact | Foreign Object In Line | Transformer faulted/mechanical | STA 445-132 | 2020-06-20 | 0.59178 | 20.4219
308 | TRUE | P41583 | Before | P41583 | 2013-06-26 09:25 | 2020-05-29 | 2020-03-10 | Bird contact | Foreign Object In Line | Transformer faulted/mechanical | STA 445-736 | 2011-08-01 | 0.59178 | 20.4219
308 | TRUE | P41619 | Before | P41619 | 2016-07-01 15:40 | 2018-05-29 | 2018-05-24 | Bird contact | Foreign Object In Line | Transformer faulted/mechanical | STA 445-783 | 2018-04-25 | 2.5945 | 18.4192
308 | TRUE | P46574 | Before | P46574 | 2004-07-02 18:05 | 2019-12-12 | 2016-10-21 | Bird contact | Foreign Object In Line | Transformer faulted/mechanical | STA 444-75B | 2016-04-08 | 1.0548 | 19.9589
308 | TRUE | P110715 | Before | P110715 | 2011-07-13 14:00 | 2018-05-29 | 2018-03-12 | Bird contact | Foreign Object In Line | Transformer faulted/mechanical | STA 221-667 | 2013-07-16 | 2.5945 | 18.4192
308 | TRUE | P112551 | Before | P112551 | 2017-11-24 13:59 | 2020-11-02 | 2020-01-30 | Bird contact | Foreign Object In Line | Transformer faulted/mechanical | STA 222-401 | 2020-09-14 | 0.16164 | 20.8521
308 | TRUE | P112744 | Before | P112744 | 2016-09-29 15:21 | 2018-03-01 | 2017-05-03 | Bird contact | Foreign Object In Line | Transformer faulted/mechanical | STA 971-181 | 2017-05-26 | 2.8384 | 18.1753
308 | TRUE | P117267 | Before | P117267 | 2014-06-20 05:29 | 2018-07-26 | 2018-01-30 | Bird contact | Foreign Object In Line | Transformer faulted/mechanical | STA 221-586 | 2019-12-18 | 2.4356 | 18.5781
308 | TRUE | P118746 | Before | P118746 | 2007-06-27 09:52 | 2019-02-08 | 2018-10-08 | Bird contact | Foreign Object In Line | Transformer faulted/mechanical | STA 908-124 | 2019-01-29 | 1.8959 | 19.1178
308 | TRUE | P136241 | Before | P136241 | 2009-01-25 08:14 | 2019-12-19 | 2019-04-22 | Bird contact | Foreign Object In Line | Transformer faulted/mechanical | STA 217-534 | 2019-12-30 | 1.0356 | 19.9781
308 | TRUE | P172681 | Before | P172681 | 2015-05-08 01:30 | 2017-08-30 | 2017-02-04 | Bird contact | Foreign Object In Line | Transformer faulted/mechanical | STA 78-258 | 2018-03-13 | 3.3397 | 17.674
308 | TRUE | P172725 | Before | P172725 | 2010-04-02 08:55 | 2016-03-23 | 2015-09-09 | Bird contact | Foreign Object In Line | Transformer faulted/mechanical | STA 78-91 | 2020-06-11 | 4.7781 | 16.2356
308 | TRUE | P215818 | Before | P215818 | 2006-01-23 07:16 | 2018-06-26 | 2017-11-16 | Bird contact | Foreign Object In Line | Transformer faulted/mechanical | STA 215-165 | 2018-06-04 | 2.5178 | 18.4959
308 | TRUE | P410323 | Before | P410323 | 2007-07-22 16:08 | 2019-12-19 | 2019-06-14 | Bird contact | Foreign Object In Line | Transformer faulted/mechanical | STA 350-113 | 2019-12-16 | 1.0356 | 19.9781
308 | TRUE | P413693 | Before | P413693 | 2006-08-16 09:40 | 2017-05-02 | 2016-03-25 | Bird contact | Foreign Object In Line | Transformer faulted/mechanical | 220-52 | 2018-06-29 | 3.6685 | 17.3452
308 | TRUE | P514153 | Before | P514153 | 2011-11-16 06:33 | 2017-11-17 | 2016-12-15 | Bird contact | Foreign Object In Line | Transformer faulted/mechanical | STA 1030-1147 | 2019-08-12 | 3.1233 | 17.8904
308 | TRUE | P610613 | Before | P610613 | 2006-07-02 05:50 | 2017-05-08 | 2016-08-10 | Bird contact | Foreign Object In Line | Transformer faulted/mechanical | STA 1030-738 | 2017-05-08 | 3.6521 | 17.3616
308 | TRUE | P615716 | Before | P615716 | 2016-04-08 16:23 | 2016-08-17 | 2016-07-08 | Bird contact | Foreign Object In Line | Transformer faulted/mechanical | STA 1030-206 | 2018-09-06 | 4.3753 | 16.6384
308 | TRUE | P718259 | Before | P718259 | 2017-08-30 13:40 | 2020-11-07 | 2020-09-11 | Bird contact | Foreign Object In Line | Transformer faulted/mechanical | STA 972-907 | 2020-11-05 | 0.14795 | 20.8658
310 | TRUE | P112743 | Before | P112744 | 2010-08-07 09:38 | 2018-03-01 | 2017-05-03 | Damage by gunshot | Foreign Object In Line | Conductor failure/wire down | P112743 | 2017-05-26 | 2.8384 | 18.1753
310 | TRUE | P410320 | Before | P410320 | 2013-09-13 02:06 | 2019-12-19 | 2019-06-14 | Damage by gunshot | Foreign Object In Line | Conductor failure/wire down | P410321 | 2019-12-16 | 1.0356 | 19.9781
310 | TRUE | P512484 | Before | P512485 | 2006-12-25 13:44 | 2018-07-25 | 2018-02-14 | Damage by gunshot | Foreign Object In Line | Conductor failure/wire down | P512484 | 2018-07-11 | 2.4384 | 18.5753
310 | TRUE | P611122 | Before | P219739 | 2012-09-20 19:42 | 2017-10-13 | 2017-06-08 | Damage by gunshot | Foreign Object In Line | Conductor failure/wire down | P611122 | 2020-08-28 | 3.2192 | 17.7945
312 | TRUE | P310492 | Before | P310492 | 2013-02-24 11:56 | 2019-03-04 | 2018-09-04 | Flashover/vegetation | Foreign Object In Line | Cutout failure |  | 2016-09-18 | 1.8301 | 19.1836
314 | TRUE | P112510 | Before | P112510 | 2020-07-23 08:20 | 2020-10-08 | 2020-07-13 | Foreign object | Foreign Object In Line | Conductor contact/failure/overload/wire slap | P112511 | 2020-09-15 | 0.23014 | 20.7836
314 | TRUE | P815212 | Before | P815212 | 2005-03-12 19:42 | 2017-03-30 | 2016-10-24 | Foreign object in distribution line | Foreign Object In Line |  |  | 2019-09-10 | 3.7589 | 17.2548
314 | TRUE | P41083 | Before | P41083 | 2010-02-16 13:44 | 2020-09-10 | 2020-06-22 | Foreign object in distribution line | Foreign Object In Line | Conductor contact/wire slap | P41082 | 2010-03-05 | 0.30685 | 20.7068
314 | TRUE | P228931 | Before | P228931 | 2016-07-11 10:27 | 2018-02-15 | 2017-11-05 | Foreign object in distribution line | Foreign Object In Line | Conductor contact/wire slap | P228932 | 2018-01-26 | 2.8767 | 18.137
314 | TRUE | P312915 | Before | P312915 | 2019-04-10 08:51 | 2019-06-14 | 2019-02-09 | Foreign object in distribution line | Foreign Object In Line | Conductor contact/wire slap |  | 2019-05-15 | 1.5507 | 19.463
314 | TRUE | P577691 | Before | P577691 | 2017-08-06 13:38 | 2020-04-13 | 2020-01-13 | Foreign object in distribution line | Foreign Object In Line | Conductor contact/wire slap |  | 2020-04-13 | 0.71781 | 20.2959
314 | TRUE | P112884 | Before | P112884 | 2005-06-12 16:49 | 2020-04-16 | 2019-03-28 | Foreign object in distribution line | Foreign Object In Line | Conductor failure/wire down | P112879 | 2020-02-07 | 0.70959 | 20.3041
314 | TRUE | P214141 | Before | P214141 | 2018-09-24 13:07 | 2019-02-04 | 2018-08-30 | Foreign object in distribution line | Foreign Object In Line | Conductor failure/wire down | P610912 | 2019-02-04 | 1.9068 | 19.1068
314 | TRUE | P676351 | Before | P676351 | 2006-03-09 16:20 | 2020-11-13 | 2020-07-01 | Foreign object in distribution line | Foreign Object In Line | Conductor failure/wire down | P175938 | 2020-11-12 | 0.13151 | 20.8822
314 | TRUE | P111589 | Before | P111589 | 2014-06-05 19:56 | 2018-03-01 | 2017-05-03 | Foreign object in distribution line | Foreign Object In Line | Fuse holder/fuse cabinet failed |  | 2017-05-26 | 2.8384 | 18.1753
314 | TRUE | P115165 | Before | P115165 | 2017-06-14 06:58 | 2019-10-29 | 2019-01-22 | Foreign object in distribution line | Foreign Object In Line | Transformer faulted/mechanical | STA 908-104 | 2019-04-16 | 1.1753 | 19.8384
430 | TRUE | P115513 | Before | P115513 | 2009-12-07 05:25 | 2017-08-14 | 2016-08-30 | Palm frond contact due to storm/wind | Foreign Object In Line | Conductor failure/wire down | P319261 | 2020-11-30 | 3.3836 | 17.6301
318 | TRUE | P175945 | Before | P175945 | 2018-11-23 09:01 | 2020-11-13 | 2020-07-01 | Tree contact | Foreign Object In Line | Conductor failure/wire down | P175946 | 2020-11-12 | 0.13151 | 20.8822
318 | TRUE | P514661 | Before | P514661 | 2011-05-30 17:26 | 2018-09-26 | 2018-07-02 | Tree contact | Foreign Object In Line | Conductor failure/wire down | P514662 | 2018-09-10 | 2.2658 | 18.7479
420 | TRUE | P215153 | Before | P215153 | 2010-01-18 13:31 | 2019-12-04 | 2019-09-24 | Tree contact due to storm/high wind | Foreign Object In Line | Conductor contact/wire slap | P817002 | 2019-12-02 | 1.0767 | 19.937
420 | TRUE | P215153 | Before | P215153 | 2010-01-19 14:00 | 2019-12-04 | 2019-09-24 | Tree contact due to storm/high wind | Foreign Object In Line | Conductor contact/wire slap | P817002 | 2019-12-02 | 1.0767 | 19.937
420 | TRUE | P217000 | Before | P21699 | 2002-11-27 15:43 | 2019-04-05 | 2018-06-27 | Tree contact due to storm/high wind | Foreign Object In Line | Conductor contact/wire slap | P217000 | 2019-01-25 | 1.7425 | 19.2712
420 | TRUE | P510223 | Before | P510223 | 2004-11-21 10:00 | 2020-11-02 | 2020-01-30 | Tree contact due to storm/high wind | Foreign Object In Line | Conductor contact/wire slap | P510224 | 2020-09-14 | 0.16164 | 20.8521
420 | TRUE | P114275 | Before | P166057 | 2007-03-03 11:34 | 2017-04-19 | 2016-12-09 | Tree contact due to storm/high wind | Foreign Object In Line | Conductor failure/wire down | P114275 | 2020-12-29 | 3.7041 | 17.3096
322 | TRUE | P14085 | Before | P14085 | 2016-07-23 19:06 | 2016-08-22 | 2016-02-25 | Tree fell on line | Foreign Object In Line | Conductor contact/wire slap |  | 2020-06-11 | 4.3616 | 16.6521
322 | TRUE | P41266 | Before | P41266 | 2013-07-30 12:45 | 2020-09-10 | 2020-06-03 | Tree fell on line | Foreign Object In Line | Conductor contact/wire slap | P45601 | 2015-02-20 | 0.30685 | 20.7068
322 | TRUE | P74062 | Before | P74062 | 2012-02-12 10:50 | 2018-10-02 | 2016-08-22 | Tree fell on line | Foreign Object In Line | Conductor contact/wire slap | P877134 | 2018-10-02 | 2.2493 | 18.7644
322 | TRUE | P219431 | Before | P219432 | 2019-12-17 06:48 | 2020-04-16 | 2019-03-28 | Tree fell on line | Foreign Object In Line | Conductor contact/wire slap | P219431 | 2020-02-07 | 0.70959 | 20.3041
322 | TRUE | P311257 | Before | P311257 | 2002-10-29 17:44 | 2017-01-19 | 2016-10-04 | Tree fell on line | Foreign Object In Line | Conductor contact/wire slap | P311258 | 2018-03-26 | 3.9507 | 17.063
322 | TRUE | P412314 | Before | P412314 | 2005-07-03 15:05 | 2020-08-27 | 2020-02-12 | Tree fell on line | Foreign Object In Line | Conductor contact/wire slap |  | 2020-04-24 | 0.34521 | 20.6685
322 | TRUE | P611658 | Before | P611658 | 2006-06-29 16:49 | 2017-10-06 | 2016-12-01 | Tree fell on line | Foreign Object In Line | Conductor contact/wire slap | P611659 | 2017-10-04 | 3.2384 | 17.7753
322 | TRUE | P14700J | Before | P14699 | 2015-02-12 20:06 | 2016-06-02 | 2016-04-15 | Tree fell on line | Foreign Object In Line | Conductor failure/wire down | P14700J | 2016-05-12 | 4.5836 | 16.4301
322 | TRUE | P175945 | Before | P175945 | 2017-09-05 14:49 | 2020-11-13 | 2020-07-01 | Tree fell on line | Foreign Object In Line | Conductor failure/wire down | P175946 | 2020-11-12 | 0.13151 | 20.8822
322 | TRUE | P316588 | Before | P316588 | 2003-03-09 09:44 | 2019-01-10 | 2018-06-01 | Tree fell on line | Foreign Object In Line | Conductor failure/wire down | P517425 | 2020-09-08 | 1.9753 | 19.0384
322 | TRUE | P317736 | Before | P317736 | 2004-03-19 16:42 | 2016-08-22 | 2016-02-25 | Tree fell on line | Foreign Object In Line | Conductor failure/wire down | P317737 | 2020-06-11 | 4.3616 | 16.6521
322 | TRUE | P416781 | Before | P416781 | 2007-09-02 14:26 | 2016-04-09 | 2015-09-29 | Tree fell on line | Foreign Object In Line | Conductor failure/wire down | P416782 | 2018-07-26 | 4.7315 | 16.2822
322 | TRUE | P116912 | Before | P116912 | 2003-07-29 19:42 | 2016-03-02 | 2015-11-02 | Tree fell on line | Foreign Object In Line | Line-Xfmr deenerg for safety | P116913 | 2018-07-09 | 4.8356 | 16.1781
426 | TRUE | P113842 | Before | P113843 | 2001-12-09 14:17 | 2019-12-23 | 2015-09-01 | Tree fell on line due to storm/wind | Foreign Object In Line |  | P113842 | 2019-12-13 | 1.0247 | 19.989
426 | TRUE | P113160 | Before | P113153 | 2016-01-31 15:09 | 2018-03-01 | 2016-11-22 | Tree fell on line due to storm/wind | Foreign Object In Line | Conductor contact/wire slap | P113160 | 2017-10-17 | 2.8384 | 18.1753
426 | TRUE | P211170 | Before | P211170 | 2009-12-07 14:25 | 2018-06-26 | 2017-11-16 | Tree fell on line due to storm/wind | Foreign Object In Line | Conductor contact/wire slap |  | 2018-06-04 | 2.5178 | 18.4959
426 | TRUE | P17862 | Before | P17862 | 2008-12-17 09:21 | 2017-08-02 | 2016-07-25 | Tree fell on line due to storm/wind | Foreign Object In Line | Conductor failure/wire down | P116633 | 2017-08-02 | 3.4164 | 17.5973
426 | TRUE | P114200 | Before | P114200 | 2004-10-27 03:44 | 2019-01-25 | 2018-04-09 | Tree fell on line due to storm/wind | Foreign Object In Line | Conductor failure/wire down |  | 2019-01-25 | 1.9342 | 19.0795
426 | TRUE | P114294 | Before | P114243 | 2002-02-10 10:16 | 2017-03-30 | 2016-10-24 | Tree fell on line due to storm/wind | Foreign Object In Line | Conductor failure/wire down | P114294 | 2019-09-10 | 3.7589 | 17.2548
426 | TRUE | P115840 | Before | P211160 | 2004-12-29 06:18 | 2018-06-26 | 2017-11-16 | Tree fell on line due to storm/wind | Foreign Object In Line | Conductor failure/wire down | P115840 | 2018-06-04 | 2.5178 | 18.4959
426 | TRUE | P116149 | Before | P116149 | 2003-01-11 10:13 | 2019-01-10 | 2018-06-01 | Tree fell on line due to storm/wind | Foreign Object In Line | Conductor failure/wire down | P714753 | 2020-09-08 | 1.9753 | 19.0384
426 | TRUE | P117357 | Before | P117357 | 2011-11-02 08:09 | 2020-08-27 | 2020-02-12 | Tree fell on line due to storm/wind | Foreign Object In Line | Conductor failure/wire down | P117358 | 2020-04-24 | 0.34521 | 20.6685
426 | TRUE | P311972 | Before | P311973 | 2006-01-15 14:18 | 2017-08-17 | 2017-07-06 | Tree fell on line due to storm/wind | Foreign Object In Line | Conductor failure/wire down | P311972 | 2020-12-15 | 3.3753 | 17.6384
426 | TRUE | P214141 | Before | P214141 | 2014-04-30 11:21 | 2019-02-04 | 2018-08-30 | Tree fell on line due to storm/wind | Foreign Object In Line | Guy wire failure | P214142 | 2019-02-04 | 1.9068 | 19.1068
426 | TRUE | P173170 | Before | P173170 | 2014-04-30 06:11 | 2015-11-21 | 2015-10-10 | Tree fell on line due to storm/wind | Foreign Object In Line | Pole broke/rotted/on fire | P173172 | 2010-10-01 | 5.1151 | 15.8986
206 | FALSE | P196115 | Before | P196115 | 2003-10-27 07:57 |  |  | Fire | Miscellaneous |  | P17794 | 2016-11-21 | 4.1123 | 16.9014
206 | FALSE | P116838 | Before | P116838 | 2007-10-22 01:31 |  |  | Fire | Miscellaneous | Conductor failure/wire down | P116840 | 2016-03-21 | 4.7836 | 16.2301
206 | TRUE | P316594 | Before | P216899 | 2007-10-23 11:34 | 2019-01-10 | 2018-01-08 | Fire | Miscellaneous | Conductor failure/wire down | P316594 | 2020-12-29 | 1.9753 | 19.0384
206 | TRUE | P873781 | Before | P873781 | 2003-10-29 12:35 | 2020-07-25 | 2020-06-30 | Fire | Miscellaneous | Conductor failure/wire down | P970848 | 2020-07-29 | 0.43562 | 20.5781
206 | TRUE | P19585 | Before | P19585 | 2004-07-13 14:14 | 2019-12-27 | 2019-06-25 | Fire | Miscellaneous | Pole broke/rotted/on fire |  | 2015-01-20 | 1.0137 | 20
206 | TRUE | P711836 | Before | P711836 | 2007-10-23 10:45 | 2016-10-19 | 2016-04-18 | Fire | Miscellaneous | Pole broke/rotted/on fire |  | 2020-08-13 | 4.2027 | 16.811
206 | TRUE | P713311 | Before | P713311 | 2003-11-04 16:15 | 2018-05-29 | 2018-03-12 | Fire | Miscellaneous | Pole broke/rotted/on fire |  | 2018-06-29 | 2.5945 | 18.4192
626 | FALSE | P675865 | Before | P675865 | 2008-10-06 12:39 |  |  | SDG&E Contr. Line fault/tree trimming | SDGE/Contractor Contact | Transformer faulted/mechanical | STA 358-119 | 2016-04-22 | 4.6959 | 16.3178
610 | FALSE | P317311 | Before | P317311 | 2015-07-19 20:26 |  |  | SDG&E Crew Vehicle Contact | SDGE/Contractor Contact | Conductor contact/wire slap | P717201 | 2016-04-15 | 4.7151 | 16.2986
632 | TRUE | P211139 | Before | P211139 | 2018-07-11 12:50 | 2019-04-05 | 2018-05-21 | SDG&E Contr. Crew error | SDGE/Contractor Contact | Conductor contact/wire slap |  | 2018-08-30 | 1.7425 | 19.2712
632 | TRUE | P311990 | Before | P311990 | 2017-07-21 10:48 | 2017-08-25 | 2017-07-03 | SDG&E Contr. Crew error | SDGE/Contractor Contact | Conductor contact/wire slap | P311992 | 2018-06-14 | 3.3534 | 17.6603
632 | TRUE | P116774 | Before | P116773 | 2010-06-18 14:31 | 2016-06-24 | 2016-04-05 | SDG&E Contr. Crew error | SDGE/Contractor Contact | Conductor failure/wire down | P116774 | 2018-09-28 | 4.5233 | 16.4904
632 | TRUE | P119034 | Before | P119033 | 2009-07-27 01:55 | 2018-06-08 | 2018-03-12 | SDG&E Contr. Crew error | SDGE/Contractor Contact | Conductor failure/wire down | P119034 | 2018-05-04 | 2.5671 | 18.4466
632 | TRUE | P227903 | Before | P227903 | 2009-10-19 12:41 | 2017-04-19 | 2016-12-09 | SDG&E Contr. Crew error | SDGE/Contractor Contact | OH connector failure (jumper/splice/squeeze-on) |  | 2011-06-22 | 3.7041 | 17.3096
624 | TRUE | P17838 | Before | P17838 | 2016-09-06 08:47 | 2017-05-11 | 2016-08-22 | SDG&E Contr. Line fault/hot wash | SDGE/Contractor Contact | Conductor contact/wire slap |  | 2020-07-28 | 3.6438 | 17.3699
626 | TRUE | P115833 | Before | P115833 | 2009-02-17 12:17 | 2020-04-16 | 2019-03-28 | SDG&E Contr. Line fault/tree trimming | SDGE/Contractor Contact | OH connector failure (jumper/splice/squeeze-on) |  | 2020-02-07 | 0.70959 | 20.3041
632 | TRUE | P112456 | Before | P112456 | 2020-07-24 12:29 | 2020-09-14 | 2020-06-29 | SDG&E contractor crew error | SDGE/Contractor Contact | Foreign object | P112455 | 2020-09-14 | 0.29589 | 20.7178
632 | TRUE | P41254 | Before | P41254 | 2020-07-31 11:03 | 2020-09-10 | 2020-06-03 | SDG&E contractor crew error | SDGE/Contractor Contact | OH connector failure (jumper/splice/squeeze-on) |  | 2020-08-31 | 0.30685 | 20.7068
612 | TRUE | P116147 | Before | P116147 | 2018-07-20 10:55 | 2019-01-10 | 2018-06-01 | SDG&E Crew error | SDGE/Contractor Contact |  |  | 2020-09-08 | 1.9753 | 19.0384
612 | TRUE | P17835 | Before | P17835 | 2016-05-19 08:08 | 2016-06-24 | 2016-04-05 | SDG&E Crew error | SDGE/Contractor Contact | Conductor contact/wire slap |  | 2013-03-12 | 4.5233 | 16.4904
612 | TRUE | P117820 | Before | P117820 | 2006-07-08 11:12 | 2019-12-11 | 2019-08-31 | SDG&E Crew error | SDGE/Contractor Contact | Conductor contact/wire slap | 350-15R | 2019-10-03 | 1.0575 | 19.9562
612 | TRUE | P212405 | Before | P203334 | 2010-10-14 10:39 | 2017-08-18 | 2016-12-15 | SDG&E Crew error | SDGE/Contractor Contact | Conductor contact/wire slap | P212405 | 2019-05-01 | 3.3726 | 17.6411
612 | TRUE | P214138 | Before | P214138 | 2011-01-13 10:14 | 2019-02-04 | 2018-08-30 | SDG&E Crew error | SDGE/Contractor Contact | Conductor contact/wire slap |  | 2019-02-04 | 1.9068 | 19.1068
602 | TRUE | P102678 | Before | P102678 | 2015-06-04 09:08 | 2016-04-08 | 2014-12-20 | SDG&E Crew Heavy equip contact/dig in | SDGE/Contractor Contact | Conductor contact/wire slap |  | 2011-03-01 | 4.7342 | 16.2795
704 | FALSE | P719046 | Before | P719044 | 2004-11-18 10:13 |  |  | Line fault/tree trimming | Third Party Contact | Conductor failure/wire down | P719046 | 2016-01-25 | 4.937 | 16.0767
704 | FALSE | P312280 | Before | P312280 | 2005-07-21 11:54 |  |  | Line fault/tree trimming | Third Party Contact | Pole broke/rotted/on fire |  | 2016-03-21 | 4.7836 | 16.2301
710 | FALSE | P176525 | After | P176524 | 2018-08-27 13:07 |  |  | Vehicle contact | Third Party Contact | Conductor contact/wire slap | P176525 | 2016-05-27 | 4.6 | 16.4137
710 | FALSE | P17895 | Before | P17895 | 2010-10-22 02:29 |  |  | Vehicle contact | Third Party Contact | Pole broke/rotted/on fire |  | 2015-11-09 | 5.1479 | 15.8658
710 | FALSE | P173190 | After | P173190 | 2016-08-12 14:41 |  |  | Vehicle contact | Third Party Contact | Pole broke/rotted/on fire |  | 2015-12-07 | 5.0712 | 15.9425
710 | FALSE | P212975 | Before | P212975 | 2006-01-26 11:36 |  |  | Vehicle contact | Third Party Contact | Pole broke/rotted/on fire |  | 2016-01-15 | 4.9644 | 16.0493
710 | FALSE | P319768 | Before | P319768 | 2005-11-13 01:25 |  |  | Vehicle contact | Third Party Contact | Pole broke/rotted/on fire |  | 2015-07-27 | 5.4356 | 15.5781
710 | FALSE | P372539 | Before | P372539 | 2009-06-02 16:05 |  |  | Vehicle contact | Third Party Contact | Pole broke/rotted/on fire |  | 2015-03-19 | 5.7918 | 15.2219
710 | FALSE | P572043 | After | P572043 | 2011-08-07 09:04 |  |  | Vehicle contact | Third Party Contact | Pole broke/rotted/on fire |  | 2011-01-01 | 10.0055 | 11.0082
710 | FALSE | P774670 | Before | P774670 | 2014-03-24 09:49 |  |  | Vehicle contact | Third Party Contact | Pole broke/rotted/on fire | P774671 | 2014-04-10 | 6.7315 | 14.2822
702 | TRUE | P110880 | Before | P110880 | 2004-05-24 13:17 | 2018-09-01 | 2018-06-17 | Heavy equp contact/digin | Third Party Contact | Conductor contact/wire slap | P110882 | 2019-12-18 | 2.3342 | 18.6795
702 | TRUE | P112206 | Before | P112206 | 2003-11-14 14:55 | 2017-05-08 | 2016-08-10 | Heavy equp contact/digin | Third Party Contact | Conductor contact/wire slap | P112347 | 2017-05-08 | 3.6521 | 17.3616
702 | TRUE | P117113 | Before | P117113 | 2002-06-25 10:09 | 2018-12-21 | 2018-08-17 | Heavy equp contact/digin | Third Party Contact | Conductor failure/wire down | P210551 | 1997-01-01 | 2.0301 | 18.9836
702 | TRUE | P477375 | Before | P477375 | 2005-11-16 17:33 | 2020-04-13 | 2020-01-13 | Heavy equp contact/digin | Third Party Contact | Conductor failure/wire down | P573516 | 2020-04-13 | 0.71781 | 20.2959
702 | TRUE | P215484 | Before | P215484 | 2008-03-20 11:53 | 2017-01-10 | 2016-08-22 | Heavy equp contact/digin | Third Party Contact | Guy wire failure |  | 2018-06-28 | 3.9753 | 17.0384
702 | TRUE | P117511 | Before | P117511 | 2005-06-14 11:57 | 2017-03-09 | 2016-12-01 | Heavy equp contact/digin | Third Party Contact | Pole broke/rotted/on fire |  | 2017-02-04 | 3.8164 | 17.1973
704 | TRUE | P113155 | After | P113155 | 2019-11-12 09:11 | 2018-03-01 | 2016-11-22 | Line fault/tree trimming | Third Party Contact | Conductor contact/wire slap | P719289 | 2017-10-17 | 2.8384 | 18.1753
704 | TRUE | P14084 | Before | P14084 | 2001-09-17 09:07 | 2016-08-22 | 2016-02-25 | Line fault/tree trimming | Third Party Contact | Conductor failure/wire down | P14085 | 2020-06-11 | 4.3616 | 16.6521
704 | TRUE | P710124 | Before | P710124 | 2002-04-17 15:22 | 2019-10-08 | 2019-04-25 | Line fault/tree trimming | Third Party Contact | Tree contact |  | 2019-10-08 | 1.2329 | 19.7808
708 | TRUE | P117391 | After | P117391 | 2019-06-21 10:14 | 2018-12-21 | 2018-08-17 | Personnel contact | Third Party Contact | Conductor failure/wire down | P716355 | 2017-08-26 | 2.0301 | 18.9836
710 | TRUE | P17696 | Before | P17696 | 2005-08-27 14:47 | 2016-07-15 | 2016-05-18 | Vehicle contact | Third Party Contact | Conductor contact/wire slap |  | 2016-04-15 | 4.4658 | 16.5479
710 | TRUE | P411356 | Before | P411356 | 2005-09-08 12:28 | 2019-04-05 | 2018-06-25 | Vehicle contact | Third Party Contact | Conductor contact/wire slap | P411357 | 2013-08-21 | 1.7425 | 19.2712
710 | TRUE | P14988 | Before | P14988 | 2003-04-12 07:20 | 2019-09-13 | 2019-04-22 | Vehicle contact | Third Party Contact | Conductor failure/wire down |  | 2019-09-13 | 1.3014 | 19.7123
710 | TRUE | P113838 | Before | P113838 | 2001-05-30 16:12 | 2019-12-23 | 2015-09-01 | Vehicle contact | Third Party Contact | Conductor failure/wire down | P113836 | 2019-12-13 | 1.0247 | 19.989
710 | TRUE | P114924 | Before | P114924 | 2009-05-29 05:15 | 2017-11-21 | 2016-11-28 | Vehicle contact | Third Party Contact | Conductor failure/wire down | P816321 | 2020-08-03 | 3.1123 | 17.9014
710 | TRUE | P211163 | Before | P211163 | 2018-01-26 15:53 | 2018-06-26 | 2017-11-16 | Vehicle contact | Third Party Contact | Conductor failure/wire down | P211164 | 2018-06-04 | 2.5178 | 18.4959
710 | TRUE | P370104 | Before | P370103 | 2005-01-19 20:08 | 2016-02-24 | 2015-06-29 | Vehicle contact | Third Party Contact | Conductor failure/wire down | P370104 | 2020-07-28 | 4.8548 | 16.1589
710 | TRUE | P616190 | Before | P616190 | 2017-10-14 13:03 | 2020-12-28 | 2020-10-30 | Vehicle contact | Third Party Contact | Cutout failure |  | 2020-11-23 | 0.0082192 | 21.0055
710 | TRUE | P474547 | Before | P474547 | 2004-11-22 10:37 | 2020-04-13 | 2020-01-13 | Vehicle contact | Third Party Contact | Guy wire failure | P474548 | 2020-04-13 | 0.71781 | 20.2959
710 | TRUE | P474547 | Before | P474547 | 2007-02-13 15:17 | 2020-04-13 | 2020-01-13 | Vehicle contact | Third Party Contact | Guy wire failure | P474548 | 2020-04-13 | 0.71781 | 20.2959
710 | TRUE | P474547 | Before | P474547 | 2009-10-29 23:12 | 2020-04-13 | 2020-01-13 | Vehicle contact | Third Party Contact | Guy wire failure |  | 2020-04-13 | 0.71781 | 20.2959
710 | TRUE | P474547 | Before | P474547 | 2012-08-30 13:44 | 2020-04-13 | 2020-01-13 | Vehicle contact | Third Party Contact | Guy wire failure |  | 2020-04-13 | 0.71781 | 20.2959
710 | TRUE | P211169 | Before | P211169 | 2005-02-25 17:34 | 2018-06-26 | 2017-11-16 | Vehicle contact | Third Party Contact | OH connector failure (jumper/splice/squeeze-on) |  | 2018-06-04 | 2.5178 | 18.4959
710 | TRUE | P14990 | Before | P14990 | 2017-03-04 06:29 | 2019-09-13 | 2019-04-22 | Vehicle contact | Third Party Contact | Pole broke/rotted/on fire |  | 2019-09-13 | 1.3014 | 19.7123
710 | TRUE | P17079 | Before | P17079 | 2007-08-16 05:59 | 2019-01-25 | 2018-04-09 | Vehicle contact | Third Party Contact | Pole broke/rotted/on fire |  | 2019-01-25 | 1.9342 | 19.0795
710 | TRUE | P17682 | Before | P17684 | 2006-10-25 10:31 | 2016-07-15 | 2016-05-18 | Vehicle contact | Third Party Contact | Pole broke/rotted/on fire | P17682 | 2013-06-25 | 4.4658 | 16.5479
710 | TRUE | P17691 | Before | P17691 | 2013-11-11 02:42 | 2016-07-15 | 2016-05-18 | Vehicle contact | Third Party Contact | Pole broke/rotted/on fire |  | 2018-05-12 | 4.4658 | 16.5479
710 | TRUE | P18310 | Before | P18310 | 2008-06-22 00:23 | 2019-01-10 | 2018-06-01 | Vehicle contact | Third Party Contact | Pole broke/rotted/on fire |  | 2020-09-08 | 1.9753 | 19.0384
710 | TRUE | P18658 | Before | P18658 | 2015-05-08 11:01 | 2019-03-04 | 2018-09-04 | Vehicle contact | Third Party Contact | Pole broke/rotted/on fire |  | 2015-05-11 | 1.8301 | 19.1836
710 | TRUE | P18735 | Before | P18737 | 2014-08-08 00:27 | 2018-05-15 | 2017-12-27 | Vehicle contact | Third Party Contact | Pole broke/rotted/on fire | P18735 | 2015-04-01 | 2.6329 | 18.3808
710 | TRUE | P19278 | Before | P418825 | 2011-03-05 19:06 | 2016-06-02 | 2016-04-15 | Vehicle contact | Third Party Contact | Pole broke/rotted/on fire | P19278 | 2016-05-12 | 4.5836 | 16.4301
710 | TRUE | P41245 | Before | P41245 | 2002-02-11 02:01 | 2020-09-10 | 2020-06-03 | Vehicle contact | Third Party Contact | Pole broke/rotted/on fire |  | 2020-08-31 | 0.30685 | 20.7068
710 | TRUE | P78900 | Before | P78900 | 2002-02-16 10:09 | 2017-08-31 | 2017-02-08 | Vehicle contact | Third Party Contact | Pole broke/rotted/on fire |  | 2017-08-31 | 3.337 | 17.6767
710 | TRUE | P108912 | Before | P108912 | 2010-03-07 12:02 | 2019-12-12 | 2016-10-21 | Vehicle contact | Third Party Contact | Pole broke/rotted/on fire |  | 2016-04-08 | 1.0548 | 19.9589
710 | TRUE | P110886 | Before | P110886 | 2007-02-07 19:10 | 2018-09-01 | 2018-06-17 | Vehicle contact | Third Party Contact | Pole broke/rotted/on fire |  | 2018-08-15 | 2.3342 | 18.6795
710 | TRUE | P111562 | Before | P111562 | 2005-01-07 15:47 | 2017-04-17 | 2016-11-02 | Vehicle contact | Third Party Contact | Pole broke/rotted/on fire | P111563 | 2017-09-28 | 3.7096 | 17.3041
710 | TRUE | P112204 | Before | P112204 | 2015-05-13 12:54 | 2017-05-08 | 2016-08-10 | Vehicle contact | Third Party Contact | Pole broke/rotted/on fire |  | 2017-05-08 | 3.6521 | 17.3616
710 | TRUE | P112206 | After | P112206 | 2018-06-14 04:14 | 2017-05-08 | 2016-08-10 | Vehicle contact | Third Party Contact | Pole broke/rotted/on fire |  | 2017-05-08 | 3.6521 | 17.3616
710 | TRUE | P112233 | Before | P112233 | 2003-08-27 15:22 | 2017-11-21 | 2016-11-28 | Vehicle contact | Third Party Contact | Pole broke/rotted/on fire |  | 2020-08-03 | 3.1123 | 17.9014
710 | TRUE | P112347 | Before | P112347 | 2003-11-05 10:50 | 2017-05-08 | 2016-08-10 | Vehicle contact | Third Party Contact | Pole broke/rotted/on fire |  | 2019-01-23 | 3.6521 | 17.3616
710 | TRUE | P116880 | Before | P116880 | 2018-01-27 12:30 | 2019-09-12 | 2019-03-25 | Vehicle contact | Third Party Contact | Pole broke/rotted/on fire |  | 2018-01-27 | 1.3041 | 19.7096
710 | TRUE | P117391 | Before | P117391 | 2017-08-25 15:37 | 2018-12-21 | 2018-08-17 | Vehicle contact | Third Party Contact | Pole broke/rotted/on fire |  | 2017-08-26 | 2.0301 | 18.9836
710 | TRUE | P139444 | Before | P139444 | 2003-01-02 06:34 | 2016-05-20 | 2015-12-02 | Vehicle contact | Third Party Contact | Pole broke/rotted/on fire |  | 2020-02-29 | 4.6192 | 16.3945
710 | TRUE | P172225 | Before | P172225 | 2011-02-05 13:50 | 2020-04-13 | 2020-01-13 | Vehicle contact | Third Party Contact | Pole broke/rotted/on fire | P477375 | 2020-04-13 | 0.71781 | 20.2959
710 | TRUE | P172225 | Before | P474547 | 2015-02-18 23:48 | 2020-04-13 | 2020-01-13 | Vehicle contact | Third Party Contact | Pole broke/rotted/on fire | P172225 | 2020-04-13 | 0.71781 | 20.2959
710 | TRUE | P200077 | Before | P200077 | 2017-05-09 07:09 | 2019-12-19 | 2019-04-22 | Vehicle contact | Third Party Contact | Pole broke/rotted/on fire |  | 2019-12-30 | 1.0356 | 19.9781
710 | TRUE | P212405 | After | P212405 | 2019-04-22 14:48 | 2017-08-18 | 2016-12-15 | Vehicle contact | Third Party Contact | Pole broke/rotted/on fire |  | 2019-05-01 | 3.3726 | 17.6411
710 | TRUE | P212838 | After | P212838 | 2019-06-11 08:20 | 2016-10-19 | 2016-04-18 | Vehicle contact | Third Party Contact | Pole broke/rotted/on fire |  | 2019-06-06 | 4.2027 | 16.811
710 | TRUE | P216053 | Before | P216053 | 2010-03-14 18:28 | 2018-02-15 | 2017-11-05 | Vehicle contact | Third Party Contact | Pole broke/rotted/on fire |  | 2018-01-26 | 2.8767 | 18.137
710 | TRUE | P217465 | Before | P217465 | 2007-07-29 19:54 | 2019-12-19 | 2019-04-22 | Vehicle contact | Third Party Contact | Pole broke/rotted/on fire |  | 2019-12-30 | 1.0356 | 19.9781
710 | TRUE | P249955 | Before | P249955 | 2014-08-23 07:16 | 2017-12-04 | 2017-10-02 | Vehicle contact | Third Party Contact | Pole broke/rotted/on fire |  | 2018-07-09 | 3.0767 | 17.937
710 | TRUE | P249955 | Before | P249955 | 2015-04-24 10:24 | 2017-12-04 | 2017-10-02 | Vehicle contact | Third Party Contact | Pole broke/rotted/on fire |  | 2018-07-09 | 3.0767 | 17.937
710 | TRUE | P252107 | After | P252107 | 2018-06-27 15:41 | 2017-03-21 | 2016-11-08 | Vehicle contact | Third Party Contact | Pole broke/rotted/on fire | N/A | 2018-06-27 | 3.7836 | 17.2301
710 | TRUE | P318998 | Before | P318998 | 2001-09-03 04:27 | 2017-05-26 | 2016-10-31 | Vehicle contact | Third Party Contact | Pole broke/rotted/on fire |  | 2020-09-08 | 3.6027 | 17.411
710 | TRUE | P319998 | Before | P319998 | 2005-11-06 06:09 | 2017-05-26 | 2016-10-31 | Vehicle contact | Third Party Contact | Pole broke/rotted/on fire |  | 2020-09-08 | 3.6027 | 17.411
710 | TRUE | P378647 | Before | P378647 | 2008-09-04 03:23 | 2017-12-04 | 2017-10-02 | Vehicle contact | Third Party Contact | Pole broke/rotted/on fire |  | 2018-07-09 | 3.0767 | 17.937
710 | TRUE | P412416 | Before | P412416 | 2009-04-16 16:16 | 2019-10-29 | 2019-01-22 | Vehicle contact | Third Party Contact | Pole broke/rotted/on fire |  | 2019-04-16 | 1.1753 | 19.8384
710 | TRUE | P413406 | Before | P413406 | 2003-03-03 06:20 | 2018-03-01 | 2016-11-22 | Vehicle contact | Third Party Contact | Pole broke/rotted/on fire |  | 2017-10-17 | 2.8384 | 18.1753
710 | TRUE | P416258 | Before | P416259 | 2015-01-07 19:11 | 2019-01-25 | 2018-04-09 | Vehicle contact | Third Party Contact | Pole broke/rotted/on fire | P416258 | 2019-01-25 | 1.9342 | 19.0795
710 | TRUE | P416783 | Before | P416783 | 2004-07-04 19:48 | 2016-04-09 | 2015-09-29 | Vehicle contact | Third Party Contact | Pole broke/rotted/on fire | STA 222-66 | 2018-07-26 | 4.7315 | 16.2822
710 | TRUE | P417818 | Before | P417818 | 2011-01-15 22:16 | 2017-11-21 | 2016-11-28 | Vehicle contact | Third Party Contact | Pole broke/rotted/on fire |  | 2020-08-03 | 3.1123 | 17.9014
710 | TRUE | P418724 | Before | P418724 | 2011-12-27 22:39 | 2019-09-25 | 2019-02-08 | Vehicle contact | Third Party Contact | Pole broke/rotted/on fire | P418734 | 2011-07-29 | 1.2685 | 19.7452
710 | TRUE | P474547 | Before | P474547 | 2011-12-12 21:06 | 2020-04-13 | 2020-01-13 | Vehicle contact | Third Party Contact | Pole broke/rotted/on fire |  | 2020-04-13 | 0.71781 | 20.2959
710 | TRUE | P511297 | Before | P511297 | 2007-07-14 02:48 | 2017-08-14 | 2016-11-03 | Vehicle contact | Third Party Contact | Pole broke/rotted/on fire |  | 2018-07-02 | 3.3836 | 17.6301
710 | TRUE | P512396 | Before | P512396 | 2019-09-06 21:10 | 2019-09-12 | 2019-03-25 | Vehicle contact | Third Party Contact | Pole broke/rotted/on fire | P114616 | 2013-12-04 | 1.3041 | 19.7096
710 | TRUE | P519650 | Before | P519650 | 2008-11-21 09:22 | 2019-01-10 | 2018-01-08 | Vehicle contact | Third Party Contact | Pole broke/rotted/on fire | STA 230-1376 | 2020-12-29 | 1.9753 | 19.0384
710 | TRUE | P617984 | After | P617984 | 2017-05-06 23:57 | 2016-08-19 | 2016-06-13 | Vehicle contact | Third Party Contact | Pole broke/rotted/on fire |  | 2017-05-07 | 4.3699 | 16.6438
710 | TRUE | P816321 | Before | P816321 | 2008-11-04 00:14 | 2017-11-21 | 2016-11-28 | Vehicle contact | Third Party Contact | Pole broke/rotted/on fire |  | 2020-08-03 | 3.1123 | 17.9014
710 | TRUE | P817313 | Before | P817313 | 2017-04-04 22:33 | 2018-06-08 | 2018-03-19 | Vehicle contact | Third Party Contact | Pole broke/rotted/on fire |  | 2020-08-26 | 2.5671 | 18.4466
710 | TRUE | P876235 | Before | P876235 | 2015-02-15 05:55 | 2017-10-26 | 2017-08-28 | Vehicle contact | Third Party Contact | Pole broke/rotted/on fire |  | 2017-10-19 | 3.1836 | 17.8301
100 | FALSE | P40838 | After | P40838 | 2017-04-07 21:04 |  |  | Undetermined | Undetermined |  |  | 2016-04-08 | 4.7342 | 16.2795
100 | FALSE | P179178 | Before | P179178 | 2001-10-04 04:48 |  |  | Undetermined | Undetermined |  |  | 2014-01-16 | 6.9616 | 14.0521
100 | FALSE | P179178 | Before | P179178 | 2001-11-26 07:04 |  |  | Undetermined | Undetermined |  |  | 2014-01-16 | 6.9616 | 14.0521
100 | FALSE | P318190 | Before | P318190 | 2001-09-24 04:10 |  |  | Undetermined | Undetermined |  |  | 2016-10-31 | 4.1699 | 16.8438
100 | TRUE | P19585 | Before | P19585 | 2001-10-16 06:46 | 2019-12-27 | 2019-06-25 | Undetermined | Undetermined |  |  | 2015-01-20 | 1.0137 | 20
100 | TRUE | P112257 | Before | P112257 | 2003-06-14 13:39 | 2017-07-26 | 2016-12-15 | Undetermined | Undetermined |  |  | 2019-09-04 | 3.4356 | 17.5781
100 | TRUE | P119294 | Before | P119294 | 2014-06-27 19:47 | 2018-09-01 | 2018-06-17 | Undetermined | Undetermined |  |  | 2018-08-15 | 2.3342 | 18.6795
100 | TRUE | P211371 | After | P211371 | 2016-12-24 21:25 | 2016-10-06 | 2016-07-18 | Undetermined | Undetermined |  |  | 2016-10-06 | 4.2384 | 16.7753
100 | TRUE | P253196 | Before | P253196 | 2019-07-04 10:01 | 2020-08-05 | 2020-05-04 | Undetermined | Undetermined |  |  | 2019-08-27 | 0.40548 | 20.6082
100 | TRUE | P512493 | Before | P512493 | 2001-10-13 18:38 | 2018-07-25 | 2018-02-14 | Undetermined | Undetermined |  |  | 2018-07-11 | 2.4384 | 18.5753
100 | TRUE | P513013 | Before | P513013 | 2001-12-10 18:33 | 2017-03-21 | 2016-11-08 | Undetermined | Undetermined |  |  | 2020-10-02 | 3.7836 | 17.2301
404 | FALSE | P17960 | Before | P17960 | 2015-12-22 08:06 |  |  | Circ. Flashover/storm/high winds/undet. | Weather Related | Conductor contact/wire slap |  | 2016-01-25 | 4.937 | 16.0767
404 | FALSE | P19451 | Before | P19451 | 2007-10-22 05:30 |  |  | Circ. Flashover/storm/high winds/undet. | Weather Related | Conductor failure/wire down | P117233 | 2015-05-27 | 5.6027 | 15.411
404 | FALSE | P316929 | Before | P316929 | 2010-01-19 14:51 |  |  | Circ. Flashover/storm/high winds/undet. | Weather Related | Cutout failure |  | 2011-10-01 | 9.2575 | 11.7562
404 | FALSE | P41267 | Before | P41267 | 2013-02-20 02:45 |  |  | Circ. Flashover/storm/high winds/undet. | Weather Related | Wind - wires slap/pole down | P41269 | 2015-02-20 | 5.8658 | 15.1479
408 | FALSE | P41967 | Before | P41967 | 2014-11-19 00:07 |  |  | Ice or snow/Equipment failure | Weather Related | Circuit failure |  | 2015-03-27 | 5.7699 | 15.2438
408 | FALSE | P41596 | Before | P41596 | 2008-03-16 04:35 |  |  | Ice or snow/Equipment failure | Weather Related | Conductor failure/wire down | P41597 | 2016-04-11 | 4.726 | 16.2877
408 | FALSE | P41948 | Before | P41948 | 2008-03-16 07:52 |  |  | Ice or snow/Equipment failure | Weather Related | Conductor failure/wire down | P41954 | 2015-05-26 | 5.6055 | 15.4082
408 | FALSE | P316929 | Before | P316929 | 2010-01-21 12:39 |  |  | Ice or snow/Equipment failure | Weather Related | Cutout failure |  | 2011-10-01 | 9.2575 | 11.7562
412 | FALSE | P17607 | Before | P17607 | 2007-12-31 22:21 |  |  | Wind - wires slap/pole down | Weather Related |  | P17608 | 2016-05-20 | 4.6192 | 16.3945
412 | FALSE | P172729 | Before | P172729 | 2001-12-07 20:57 |  |  | Wind - wires slap/pole down | Weather Related |  |  | 2019-06-10 | 1.5616 | 19.4521
412 | FALSE | P873423 | Before | P373196 | 2003-03-29 05:28 |  |  | Wind - wires slap/pole down | Weather Related |  | P873423 | 2016-10-11 | 4.2247 | 16.789
412 | FALSE | P17776 | Before | P17776 | 2002-02-10 00:36 |  |  | Wind - wires slap/pole down | Weather Related | Conductor contact/wire slap | 220-1 | 2015-03-02 | 5.8384 | 15.1753
412 | FALSE | P111819 | Before | P111818 | 2011-02-02 07:18 |  |  | Wind - wires slap/pole down | Weather Related | Conductor contact/wire slap | P111819 | 2014-03-06 | 6.8274 | 14.1863
412 | FALSE | P172817 | Before | P172817 | 2014-11-05 20:38 |  |  | Wind - wires slap/pole down | Weather Related | Conductor contact/wire slap |  | 2016-02-08 | 4.8986 | 16.1151
412 | FALSE | P17617 | Before | P17618 | 2016-01-31 15:17 |  |  | Wind - wires slap/pole down | Weather Related | Conductor failure/wire down | P17617 | 2016-05-20 | 4.6192 | 16.3945
412 | FALSE | P19461 | Before | P19461 | 2003-11-27 01:59 |  |  | Wind - wires slap/pole down | Weather Related | Conductor failure/wire down | P19462 | 2015-05-27 | 5.6027 | 15.411
412 | FALSE | P40884 | Before | P40884 | 2007-10-22 02:39 |  |  | Wind - wires slap/pole down | Weather Related | Conductor failure/wire down |  | 2014-02-11 | 6.8904 | 14.1233
412 | FALSE | P41585 | Before | P41586 | 2012-02-14 05:35 |  |  | Wind - wires slap/pole down | Weather Related | Conductor failure/wire down | P41585 | 2016-04-11 | 4.726 | 16.2877
412 | FALSE | P41586 | Before | P41586 | 2012-02-27 21:34 |  |  | Wind - wires slap/pole down | Weather Related | Conductor failure/wire down |  | 2016-04-11 | 4.726 | 16.2877
412 | FALSE | P41967 | Before | P41967 | 2011-03-08 15:55 |  |  | Wind - wires slap/pole down | Weather Related | Conductor failure/wire down | P41968 | 2015-03-27 | 5.7699 | 15.2438
412 | FALSE | P42128 | Before | P42128 | 2005-04-09 00:29 |  |  | Wind - wires slap/pole down | Weather Related | Conductor failure/wire down | P42129 | 2012-10-08 | 8.2356 | 12.7781
412 | FALSE | P115172 | Before | P115172 | 2004-12-17 11:39 |  |  | Wind - wires slap/pole down | Weather Related | Conductor failure/wire down | P115173 | 2016-03-21 | 4.7836 | 16.2301
412 | FALSE | P163727 | Before | P163727 | 2008-03-03 08:04 |  |  | Wind - wires slap/pole down | Weather Related | Conductor failure/wire down | P112586 | 2016-05-20 | 4.6192 | 16.3945
412 | FALSE | P416864 | Before | P416864 | 2003-01-08 16:43 |  |  | Wind - wires slap/pole down | Weather Related | Conductor failure/wire down |  | 2016-03-03 | 4.8329 | 16.1808
412 | FALSE | P219920 | Before | P219920 | 2004-10-20 10:11 |  |  | Wind - wires slap/pole down | Weather Related | Fuse overloaded/inadequate fuse size |  | 2015-07-09 | 5.4849 | 15.5288
412 | FALSE | P311305 | Before | P311305 | 2003-12-16 06:31 |  |  | Wind - wires slap/pole down | Weather Related | Insulator/pin failure/wire floating | P311306 | 2014-08-08 | 6.4027 | 14.611
412 | FALSE | P178017 | Before | P178017 | 2004-12-17 08:26 |  |  | Wind - wires slap/pole down | Weather Related | OH connector failure (jumper/splice/squeeze-on) |  | 2016-05-06 | 4.6575 | 16.3562
412 | FALSE | P176372 | Before | P176372 | 2010-01-19 15:12 |  |  | Wind - wires slap/pole down | Weather Related | Pole broke/rotted/on fire |  | 2016-07-22 | 4.4466 | 16.5671
412 | FALSE | P619513 | Before | P711508 | 2002-02-10 10:00 |  |  | Wind - wires slap/pole down | Weather Related | Pole broke/rotted/on fire | P619513 | 2016-03-03 | 4.8329 | 16.1808
412 | FALSE | P19480 | After | Z214433 | 2020-02-26 05:32 |  |  | Wire slap/pole down/wire down (weather related) | Weather Related | Conductor contact/failure/overload/wire slap | P19480 | 2015-05-27 | 5.6027 | 15.411
404 | TRUE | P19585 | Before | P19585 | 2001-10-01 06:34 | 2019-12-27 | 2019-06-25 | Circ. Flashover/storm/high winds/undet. | Weather Related |  |  | 2015-01-20 | 1.0137 | 20
404 | TRUE | P514940 | Before | P514940 | 2002-11-28 05:02 | 2019-12-19 | 2019-04-22 | Circ. Flashover/storm/high winds/undet. | Weather Related |  |  | 2019-12-30 | 1.0356 | 19.9781
404 | TRUE | P312304 | Before | P312304 | 2010-01-21 13:39 | 2020-09-25 | 2020-02-12 | Circ. Flashover/storm/high winds/undet. | Weather Related | Conductor failure/wire down | P312306 | 2020-07-08 | 0.26575 | 20.7479
404 | TRUE | P103145 | After | P103145 | 2018-12-06 18:02 | 2016-05-24 | 2016-04-19 | Circ. Flashover/storm/high winds/undet. | Weather Related | Crossarm failure |  | 2020-09-08 | 4.6082 | 16.4055
404 | TRUE | P172683 | Before | P172683 | 2003-01-06 07:50 | 2017-08-30 | 2017-02-04 | Circ. Flashover/storm/high winds/undet. | Weather Related | Crossarm failure | P172683 | 2018-03-13 | 3.3397 | 17.674
404 | TRUE | P212271 | Before | P212271 | 2005-09-20 10:31 | 2016-10-12 | 2016-06-27 | Circ. Flashover/storm/high winds/undet. | Weather Related | Cutout failure |  | 2015-08-31 | 4.2219 | 16.7918
404 | TRUE | P613213 | Before | P613213 | 2007-10-22 00:45 | 2016-07-20 | 2016-05-31 | Circ. Flashover/storm/high winds/undet. | Weather Related | Pole broke/rotted/on fire |  | 2018-11-12 | 4.4521 | 16.5616
404 | TRUE | P41099 | Before | P41099 | 2015-08-27 13:40 | 2020-04-22 | 2020-03-06 | Circ. Flashover/storm/high winds/undet. | Weather Related | Recloser/breaker faulted/mechanical |  | 2010-03-05 | 0.69315 | 20.3205
408 | TRUE | P41976 | Before | P41976 | 2013-02-08 22:54 | 2019-12-12 | 2016-10-21 | Ice or snow/Equipment failure | Weather Related | Conductor failure/wire down | P41977 | 2016-04-08 | 1.0548 | 19.9589
408 | TRUE | P45526 | Before | P45526 | 2010-01-19 15:41 | 2018-06-03 | 2018-03-29 | Ice or snow/Equipment failure | Weather Related | Conductor failure/wire down | P41608 | 2018-06-03 | 2.5808 | 18.4329
408 | TRUE | P312309 | Before | P312309 | 2013-02-20 05:08 | 2020-09-25 | 2020-02-12 | Ice or snow/Equipment failure | Weather Related | Conductor failure/wire down | P312310 | 2014-12-11 | 0.26575 | 20.7479
408 | TRUE | P517812 | Before | P517812 | 2010-12-20 17:35 | 2019-10-08 | 2019-04-25 | Ice or snow/Equipment failure | Weather Related | Crossarm failure |  | 2019-10-08 | 1.2329 | 19.7808
408 | TRUE | P610754 | Before | P610754 | 2001-11-24 19:26 | 2018-06-07 | 2017-12-26 | Ice or snow/Equipment failure | Weather Related | Fuse holder/fuse cabinet failed |  | 2020-10-22 | 2.5699 | 18.4438
408 | TRUE | P212271 | Before | P212271 | 2010-01-21 15:59 | 2016-10-12 | 2016-06-27 | Ice or snow/Equipment failure | Weather Related | Pole broke/rotted/on fire |  | 2015-08-31 | 4.2219 | 16.7918
404 | TRUE | P112131 | After | P112131 | 2020-07-30 17:00 | 2016-06-02 | 2016-04-18 | Undetermined (weather related) | Weather Related | Fuse - overload/inadequate size/fatigue |  | 2018-03-26 | 4.5836 | 16.4301
412 | TRUE | P17990 | Before | P17990 | 2006-11-30 06:19 | 2016-10-26 | 2016-08-01 | Wind - wires slap/pole down | Weather Related |  | P17991 | 2018-07-05 | 4.1836 | 16.8301
412 | TRUE | P17991 | Before | P17991 | 2003-03-29 06:13 | 2016-10-26 | 2016-08-01 | Wind - wires slap/pole down | Weather Related |  | P17993 | 2018-07-05 | 4.1836 | 16.8301
412 | TRUE | P40811 | Before | P40811 | 2006-03-11 13:22 | 2016-10-18 | 2016-06-09 | Wind - wires slap/pole down | Weather Related |  | P40812 | 2017-02-11 | 4.2055 | 16.8082
412 | TRUE | P41619 | Before | P41619 | 2008-12-17 12:55 | 2018-05-29 | 2018-05-24 | Wind - wires slap/pole down | Weather Related |  | P41920 | 2018-04-25 | 2.5945 | 18.4192
412 | TRUE | P111379 | Before | P111379 | 2001-09-30 13:56 | 2017-05-26 | 2016-10-31 | Wind - wires slap/pole down | Weather Related |  |  | 2020-09-08 | 3.6027 | 17.411
412 | TRUE | P112501 | Before | P112501 | 2001-11-13 06:12 | 2020-10-08 | 2020-07-13 | Wind - wires slap/pole down | Weather Related |  |  | 2020-09-15 | 0.23014 | 20.7836
412 | TRUE | P115827 | Before | P518205 | 2005-07-23 04:53 | 2020-04-16 | 2019-03-28 | Wind - wires slap/pole down | Weather Related |  | P115827 | 2020-02-07 | 0.70959 | 20.3041
412 | TRUE | P211421 | Before | P211421 | 2006-03-12 08:48 | 2016-12-16 | 2016-08-12 | Wind - wires slap/pole down | Weather Related |  | P211422 | 2017-06-12 | 4.0438 | 16.9699
412 | TRUE | P215422 | Before | P215422 | 2006-04-05 01:16 | 2019-09-05 | 2018-01-17 | Wind - wires slap/pole down | Weather Related |  | P817974 | 2012-04-06 | 1.3233 | 19.6904
412 | TRUE | P216486 | Before | P216486 | 2004-11-21 11:35 | 2020-08-05 | 2020-05-04 | Wind - wires slap/pole down | Weather Related |  | P216487 | 2020-06-30 | 0.40548 | 20.6082
412 | TRUE | P710921 | Before | P710921 | 2001-10-01 10:32 | 2017-05-26 | 2016-10-31 | Wind - wires slap/pole down | Weather Related |  |  | 2016-04-26 | 3.6027 | 17.411
412 | TRUE | P41222 | Before | P41222 | 2007-10-21 20:16 | 2019-05-17 | 2019-02-11 | Wind - wires slap/pole down | Weather Related | Conductor contact/wire slap |  | 2019-05-09 | 1.6274 | 19.3863
412 | TRUE | P112248 | Before | P112248 | 2002-11-28 16:03 | 2017-07-26 | 2016-12-15 | Wind - wires slap/pole down | Weather Related | Conductor contact/wire slap |  | 2019-09-04 | 3.4356 | 17.5781
412 | TRUE | P112884 | Before | P112884 | 2002-11-28 20:39 | 2020-04-16 | 2019-03-28 | Wind - wires slap/pole down | Weather Related | Conductor contact/wire slap |  | 2020-02-07 | 0.70959 | 20.3041
412 | TRUE | P172716 | Before | P172716 | 2012-03-18 09:46 | 2016-03-23 | 2015-09-09 | Wind - wires slap/pole down | Weather Related | Conductor contact/wire slap |  | 2020-06-11 | 4.7781 | 16.2356
412 | TRUE | P175204 | Before | P175204 | 2002-02-10 22:10 | 2017-08-30 | 2017-02-04 | Wind - wires slap/pole down | Weather Related | Conductor contact/wire slap |  | 2018-03-13 | 3.3397 | 17.674
412 | TRUE | P212520 | Before | P212520 | 2017-01-22 13:57 | 2017-02-09 | 2016-12-04 | Wind - wires slap/pole down | Weather Related | Conductor contact/wire slap | P212527 | 2018-03-26 | 3.8932 | 17.1205
412 | TRUE | P412627 | Before | P412627 | 2012-04-01 03:23 | 2018-04-05 | 2016-10-14 | Wind - wires slap/pole down | Weather Related | Conductor contact/wire slap | P412634 | 2015-08-12 | 2.7425 | 18.2712
412 | TRUE | P413439 | Before | P413439 | 2008-12-18 14:22 | 2016-12-16 | 2016-08-12 | Wind - wires slap/pole down | Weather Related | Conductor contact/wire slap | P413443 | 2017-06-12 | 4.0438 | 16.9699
412 | TRUE | P673002 | Before | P673002 | 2004-04-01 21:05 | 2016-03-23 | 2015-09-09 | Wind - wires slap/pole down | Weather Related | Conductor contact/wire slap |  | 2020-06-11 | 4.7781 | 16.2356
412 | TRUE | P13233 | Before | P13233 | 2003-01-06 06:40 | 2017-06-29 | 2016-12-19 | Wind - wires slap/pole down | Weather Related | Conductor failure/wire down | P13234 | 2017-06-29 | 3.5096 | 17.5041
412 | TRUE | P13261 | Before | P13261 | 2010-01-19 19:56 | 2017-05-08 | 2016-10-17 | Wind - wires slap/pole down | Weather Related | Conductor failure/wire down | P214704 | 2018-03-26 | 3.6521 | 17.3616
412 | TRUE | P13893 | Before | P13893 | 2003-01-06 07:34 | 2019-12-23 | 2019-06-10 | Wind - wires slap/pole down | Weather Related | Conductor failure/wire down | P414176 | 2020-04-22 | 1.0247 | 19.989
412 | TRUE | P18004 | Before | P18004 | 2010-12-22 06:44 | 2016-10-26 | 2016-08-01 | Wind - wires slap/pole down | Weather Related | Conductor failure/wire down | P18005 | 2018-07-05 | 4.1836 | 16.8301
412 | TRUE | P19565 | Before | P19565 | 2002-09-10 11:50 | 2019-12-27 | 2019-06-25 | Wind - wires slap/pole down | Weather Related | Conductor failure/wire down | P19567 | 2015-08-24 | 1.0137 | 20
412 | TRUE | P41238 | Before | P41237 | 2011-02-20 03:52 | 2019-05-17 | 2019-02-11 | Wind - wires slap/pole down | Weather Related | Conductor failure/wire down | P41238 | 2019-05-09 | 1.6274 | 19.3863
412 | TRUE | P111580 | Before | P111581 | 2016-01-05 16:24 | 2018-03-01 | 2017-05-03 | Wind - wires slap/pole down | Weather Related | Conductor failure/wire down | P111580 | 2017-05-26 | 2.8384 | 18.1753
412 | TRUE | P111993 | Before | P111993 | 2010-01-19 14:05 | 2017-05-08 | 2015-08-17 | Wind - wires slap/pole down | Weather Related | Conductor failure/wire down | P111995 | 2020-07-28 | 3.6521 | 17.3616
412 | TRUE | P112093 | Before | P112093 | 2009-12-07 22:15 | 2016-10-18 | 2016-06-27 | Wind - wires slap/pole down | Weather Related | Conductor failure/wire down | P112094 | 2016-09-22 | 4.2055 | 16.8082
412 | TRUE | P112251 | Before | P112251 | 2007-10-22 02:06 | 2017-07-26 | 2016-12-15 | Wind - wires slap/pole down | Weather Related | Conductor failure/wire down | P112255 | 2019-09-04 | 3.4356 | 17.5781
412 | TRUE | P112741 | Before | P112741 | 2003-01-06 12:45 | 2018-03-01 | 2017-05-03 | Wind - wires slap/pole down | Weather Related | Conductor failure/wire down | P311523 | 2017-05-26 | 2.8384 | 18.1753
412 | TRUE | P113348 | Before | P213597 | 2008-01-07 07:38 | 2017-08-17 | 2016-12-01 | Wind - wires slap/pole down | Weather Related | Conductor failure/wire down | P113348 | 2018-06-28 | 3.3753 | 17.6384
412 | TRUE | P113838 | Before | P113838 | 2003-01-07 02:23 | 2019-12-23 | 2015-09-01 | Wind - wires slap/pole down | Weather Related | Conductor failure/wire down |  | 2019-12-13 | 1.0247 | 19.989
412 | TRUE | P114000 | Before | P114000 | 2010-01-19 14:26 | 2017-04-21 | 2016-10-31 | Wind - wires slap/pole down | Weather Related | Conductor failure/wire down | P115198 | 2018-07-09 | 3.6986 | 17.3151
412 | TRUE | P114732 | Before | P219574 | 2003-01-06 07:44 | 2018-03-01 | 2017-04-26 | Wind - wires slap/pole down | Weather Related | Conductor failure/wire down | P114732 | 2018-03-01 | 2.8384 | 18.1753
412 | TRUE | P117175 | Before | P117175 | 2017-01-20 13:03 | 2017-05-08 | 2016-11-23 | Wind - wires slap/pole down | Weather Related | Conductor failure/wire down | P117176 | 2018-06-14 | 3.6521 | 17.3616
412 | TRUE | P173171 | Before | P173171 | 2009-01-10 21:02 | 2015-11-21 | 2015-10-10 | Wind - wires slap/pole down | Weather Related | Conductor failure/wire down | P173172 | 2014-04-30 | 5.1151 | 15.8986
412 | TRUE | P211586 | Before | P211587 | 2008-03-10 18:50 | 2016-10-19 | 2016-04-18 | Wind - wires slap/pole down | Weather Related | Conductor failure/wire down | P211586 | 2020-08-13 | 4.2027 | 16.811
412 | TRUE | P213248 | Before | P213248 | 2003-01-07 02:28 | 2019-07-24 | 2019-02-26 | Wind - wires slap/pole down | Weather Related | Conductor failure/wire down |  | 2018-10-07 | 1.4411 | 19.5726
412 | TRUE | P213599 | Before | P213599 | 2004-12-16 21:40 | 2018-03-01 | 2016-11-22 | Wind - wires slap/pole down | Weather Related | Conductor failure/wire down | P213600 | 2017-10-17 | 2.8384 | 18.1753
412 | TRUE | P216471 | Before | P216471 | 2009-12-07 20:14 | 2020-08-05 | 2020-05-04 | Wind - wires slap/pole down | Weather Related | Conductor failure/wire down | P216472 | 2020-06-30 | 0.40548 | 20.6082
412 | TRUE | P217605 | Before | P217605 | 2004-12-17 00:48 | 2017-04-06 | 2017-01-14 | Wind - wires slap/pole down | Weather Related | Conductor failure/wire down | P101390 | 2020-07-14 | 3.7397 | 17.274
412 | TRUE | P273384 | Before | P273387 | 2017-01-20 15:21 | 2020-09-15 | 2020-03-10 | Wind - wires slap/pole down | Weather Related | Conductor failure/wire down | P273384 | 2020-07-25 | 0.29315 | 20.7205
412 | TRUE | P316588 | Before | P316588 | 2002-11-29 18:33 | 2019-01-10 | 2018-06-01 | Wind - wires slap/pole down | Weather Related | Conductor failure/wire down | P316589 | 2020-09-08 | 1.9753 | 19.0384
412 | TRUE | P316595 | Before | P316596 | 2005-02-19 09:23 | 2019-01-10 | 2018-01-08 | Wind - wires slap/pole down | Weather Related | Conductor failure/wire down | P316595 | 2020-12-29 | 1.9753 | 19.0384
412 | TRUE | P412625 | Before | P412625 | 2009-12-08 01:59 | 2018-04-05 | 2016-10-14 | Wind - wires slap/pole down | Weather Related | Conductor failure/wire down | P412626 | 2015-08-12 | 2.7425 | 18.2712
412 | TRUE | P612997 | Before | P612997 | 2017-01-22 15:04 | 2018-05-15 | 2017-12-11 | Wind - wires slap/pole down | Weather Related | Conductor failure/wire down | P110860 | 2018-05-08 | 2.6329 | 18.3808
412 | TRUE | P319081 | Before | P319081 | 2001-11-24 16:18 | 2017-03-21 | 2016-11-08 | Wind - wires slap/pole down | Weather Related | Flashover/vegetation |  | 2012-01-26 | 3.7836 | 17.2301
412 | TRUE | P612465 | Before | P612465 | 2005-01-04 13:00 | 2017-02-09 | 2016-11-14 | Wind - wires slap/pole down | Weather Related | Insulator/pin failure/wire floating | P613832 | 2018-03-26 | 3.8932 | 17.1205
412 | TRUE | P19514 | Before | P19514 | 2002-02-10 00:42 | 2019-12-27 | 2019-06-10 | Wind - wires slap/pole down | Weather Related | Pole broke/rotted/on fire |  | 2019-12-05 | 1.0137 | 20
412 | TRUE | P41776 | Before | P41776 | 2008-12-13 17:40 | 2019-12-12 | 2016-10-21 | Wind - wires slap/pole down | Weather Related | Pole broke/rotted/on fire |  | 2016-06-04 | 1.0548 | 19.9589
412 | TRUE | P318284 | Before | P318284 | 2002-02-10 11:18 | 2018-06-08 | 2018-03-19 | Wind - wires slap/pole down | Weather Related | Pole broke/rotted/on fire |  | 2020-08-26 | 2.5671 | 18.4466
412 | TRUE | P615327 | Before | P615327 | 2004-12-29 05:52 | 2016-04-09 | 2015-09-29 | Wind - wires slap/pole down | Weather Related | Pole broke/rotted/on fire | P615321 | 2018-07-26 | 4.7315 | 16.2822

## Summary
Project Id | Unhardened Faults | Unhardened years | Unhardned faults per operating year Average | Hardened Faults | Hardened years | Hardned faults per operating year Average | Number of Poles
0073-E | 2 | 16.9315 | 0.11812 | 1 | 4.0822 | 0.24497 | 28
0078-B | 1 | 15.2466 | 0.065588 | 0 | 5.7671 | 0 | 13
0078-C | 2 | 19.4521 | 0.10282 | 0 | 1.5616 | 0 | 24
0079-M | 1 | 16.2384 | 0.061583 | 1 | 4.7753 | 0.20941 | 22
0079-R | 1 | 16.4329 | 0.060854 | 1 | 4.5808 | 0.2183 | 22
0175-D | 1 | 17.1205 | 0.058409 | 1 | 3.8932 | 0.25686 | 15
0176-F | 0 | 18.6575 | 0 | 1 | 2.3562 | 0.42442 | 32
0217-C | 1 | 18.1753 | 0.05502 | 1 | 2.8384 | 0.35232 | 30
0220-B | 0 | 15.411 | 0 | 1 | 5.6027 | 0.17848 | 29
0221-F | 3 | 18.4192 | 0.16287 | 1 | 2.5945 | 0.38543 | 36
0221-L | 0 | 16.9699 | 0 | 1 | 4.0438 | 0.24729 | 27
0221-M | 0 | 16.7753 | 0 | 1 | 4.2384 | 0.23594 | 26
0222-AA | 1 | 17.5973 | 0.056827 | 1 | 3.4164 | 0.2927 | 20
0222-C | 6 | 16.2795 | 0.36856 | 1 | 4.7342 | 0.21123 | 42
0222-O | 0 | 15.796 | 0 | 0 | 5.2177 | 0 | 35
0222-U | 2 | 16.5753 | 0.12066 | 1 | 4.4384 | 0.22531 | 39
0222-Z | 2 | 17.3699 | 0.11514 | 1 | 3.6438 | 0.27444 | 30
0233-LONG SPAN EVAL | 1 | 14.9836 | 0.06674 | 1 | 7.6685 | 0.1304 | 3
0236-B | 2 | 16.811 | 0.11897 | 1 | 4.2027 | 0.23794 | 38
0237-C | 2 | 16.5479 | 0.12086 | 1 | 4.4658 | 0.22393 | 28
0237-D | 4 | 16.3945 | 0.24398 | 1 | 4.6192 | 0.21649 | 32
0237-I | 3 | 19.989 | 0.15008 | 1 | 1.0247 | 0.97594 | 26
0237-O | 1 | 16.4301 | 0.060864 | 1 | 4.5836 | 0.21817 | 39
0240-B | 3 | 16.3945 | 0.18299 | 1 | 4.6192 | 0.21649 | 33
0240-E | 1 | 16.5671 | 0.060361 | 1 | 4.4466 | 0.22489 | 27
0240-G | 2 | 18.7644 | 0.10658 | 1 | 2.2493 | 0.44458 | 30
0358-C | 2 | 16.4055 | 0.12191 | 1 | 4.6082 | 0.217 | 29
0442-D | 3 | 15.8986 | 0.1887 | 0 | 5.1151 | 0 | 16
0442-G | 2 | 15.9425 | 0.12545 | 1 | 5.0712 | 0.19719 | 6
0442-J | 1 | 16.2603 | 0.0615 | 1 | 4.7534 | 0.21037 | 7
0442-K | 0 | 16.2202 | 0 | 0 | 4.7935 | 0 | 30
0445-C | 1 | 18.5699 | 0.053851 | 1 | 2.4438 | 0.40919 | 39
0445-CALTRANS OH RFS | 0 | 12.9936 | 0 | 0 | 8.0201 | 0 | 2
0445-CFSP | 6 | 16.2877 | 0.36838 | 1 | 4.726 | 0.21159 | 44
0908-L (R-CODE) | 2 | 18.9836 | 0.10535 | 1 | 2.0301 | 0.49258 | 5
0971-L | 6 | 18.1753 | 0.33012 | 1 | 2.8384 | 0.35232 | 31
0971-M | 3 | 18.1753 | 0.16506 | 1 | 2.8384 | 0.35232 | 28
0972-C | 1 | 17.2082 | 0.058112 | 1 | 3.8055 | 0.26278 | 24
0972-D | 1 | 17.2301 | 0.058038 | 1 | 3.7836 | 0.2643 | 28
1030-C | 4 | 17.3616 | 0.23039 | 1 | 3.6521 | 0.27382 | 42
1030-F | 1 | 17.6411 | 0.056686 | 1 | 3.3726 | 0.29651 | 1
1030-G | 0 | 17.5781 | 0 | 0 | 3.4356 | 0 | 27
1030-T | 0 | 16.6438 | 0 | 1 | 4.3699 | 0.22884 | 6
1215-LONG SPAN | 0 | 14.7096 | 0 | 1 | 6.3041 | 0.15863 | 5
1215-ML CFSP | 2 | 16.2795 | 0.12285 | 1 | 4.7342 | 0.21123 | 15
0079-P | 1 | 15.9342 | 0.062758 | 1 | 5.0795 | 0.19687 | 43
0176-A | 3 | 17.274 | 0.17367 | 2 | 3.7397 | 0.5348 | 25
0220-G | 0 | 16.274 | 0 | 2 | 4.7397 | 0.42197 | 8
0221-A | 10 | 18.2712 | 0.54731 | 2 | 2.7425 | 0.72927 | 28
0221-ERI | 0 | 14.2274 | 0 | 2 | 6.7863 | 0.29471 | 13
0237-F | 0 | 16.0767 | 0 | 2 | 4.937 | 0.40511 | 24
0350-F | 3 | 19.7808 | 0.15166 | 2 | 1.2329 | 1.6222 | 44
0358-A | 0 | 16.4137 | 0 | 2 | 4.6 | 0.43478 | 12
0441-BL CFSP | 1 | 14.1233 | 0.070805 | 2 | 5.0767 | 0.39396 | 28
0441-PR | 1 | 14.8712 | 0.067244 | 2 | 6.1425 | 0.3256 | 23
1030-B | 1 | 16.5616 | 0.06038 | 1 | 4.4521 | 0.22462 | 18
0067-LS | 1 | 14.7041 | 0.068008 | 0 | 6.3096 | 0 | 13
0073-A | 1 | 15.2219 | 0.065695 | 0 | 5.7918 | 0 | 20
0073-B | 1 | 15.5288 | 0.064397 | 0 | 5.4849 | 0 | 37
0079-E | 1 | 19.3973 | 0.051554 | 0 | 1.6164 | 0 | 18
0079-K | 1 | 16.274 | 0.061448 | 0 | 4.7397 | 0 | 42
0157-U | 2 | 20.9014 | 0.095688 | 0 | 0.11233 | 0 | 32
0176-E | 1 | 17.3151 | 0.057753 | 0 | 3.6986 | 0 | 25
0212-G | 1 | 20.7041 | 0.0483 | 0 | 0.30959 | 0 | 2
0212-I | 1 | 20.4603 | 0.048875 | 0 | 0.55342 | 0 | 7
0212-P | 1 | 20.9534 | 0.047725 | 0 | 0.060274 | 0 | 63
0212-W | 1 | 20.3836 | 0.049059 | 0 | 0.63014 | 0 | 8
0212-W-FT-02 | 1 | 20.326 | 0.049198 | 0 | 0.68767 | 0 | 6
0215-C | 0 | 19.6904 | 0 | 0 | 1.3233 | 0 | 8
0215-E (ASD) | 0 | 18.4658 | 0 | 0 | 2.5479 | 0 | 1
0217-AD | 1 | 20.337 | 0.049171 | 0 | 0.67671 | 0 | 3
0217-F | 1 | 18.3808 | 0.054405 | 0 | 2.6329 | 0 | 25
0217-G | 1 | 18.6767 | 0.053543 | 0 | 2.337 | 0 | 18
0217-K | 1 | 19.2712 | 0.051891 | 0 | 1.7425 | 0 | 35
0217-Q | 1 | 19.463 | 0.05138 | 0 | 1.5507 | 0 | 32
0217-W (ASD) | 0 | 19.7425 | 0 | 0 | 1.2712 | 0 | 5
0217-Y (R-CODE) | 1 | 18.3808 | 0.054405 | 0 | 2.6329 | 0 | 1
0220-H | 1 | 16.8438 | 0.059369 | 0 | 4.1699 | 0 | 29
0220-I | 1 | 15.674 | 0.0638 | 0 | 5.3397 | 0 | 49
0220-L | 1 | 16.1808 | 0.061802 | 0 | 4.8329 | 0 | 32
0221-D-VOLCAN MTN | 1 | 20.7178 | 0.048268 | 0 | 0.29589 | 0 | 21
0221-H | 1 | 16.8082 | 0.059495 | 0 | 4.2055 | 0 | 24
0221-I | 1 | 17.389 | 0.057507 | 0 | 3.6247 | 0 | 26
0221-O | 1 | 18.3671 | 0.054445 | 0 | 2.6466 | 0 | 1
0221-PH | 1 | 15.8658 | 0.063029 | 0 | 5.1479 | 0 | 7
0221-T | 1 | 18.5781 | 0.053827 | 0 | 2.4356 | 0 | 30
0222-C222 FRM PRO P | 1 | 14.611 | 0.068442 | 0 | 6.4027 | 0 | 16
0222-F | 0 | 15.6109 | 0 | 0 | 5.4028 | 0 | 25
0222-HH | 1 | 20.3781 | 0.049072 | 0 | 0.63562 | 0 | 5
0222-J | 1 | 16.2986 | 0.061355 | 0 | 4.7151 | 0 | 18
0222-P | 2 | 18.111 | 0.11043 | 0 | 2.9027 | 0 | 23
0222-R1 | 1 | 15.1753 | 0.065896 | 0 | 5.8384 | 0 | 14
0222-RR (R-CODE) | 0 | 20.2027 | 0 | 0 | 0.81096 | 0 | 3
0222-S | 1 | 16.1781 | 0.061812 | 0 | 4.8356 | 0 | 16
0230-A | 1 | 18.2521 | 0.054788 | 0 | 2.7616 | 0 | 16
0237-A | 1 | 16.2027 | 0.061718 | 0 | 4.811 | 0 | 26
0237-B | 1 | 17.3616 | 0.057598 | 0 | 3.6521 | 0 | 19
0237-G | 1 | 18.1753 | 0.05502 | 0 | 2.8384 | 0 | 25
0237-M | 1 | 20.7315 | 0.048236 | 0 | 0.28219 | 0 | 34
0237-P | 1 | 16.3699 | 0.061088 | 0 | 4.6438 | 0 | 50
0240-D | 1 | 16.5616 | 0.06038 | 0 | 4.4521 | 0 | 21
0240-Z-FT | 1 | 20.5781 | 0.048595 | 0 | 0.43562 | 0 | 3
0350-E | 1 | 19.5945 | 0.051035 | 0 | 1.4192 | 0 | 30
0350-I | 1 | 18.6959 | 0.053488 | 0 | 2.3178 | 0 | 18
0350-J | 1 | 19.5726 | 0.051092 | 0 | 1.4411 | 0 | 33
0350-K | 1 | 19.074 | 0.052427 | 0 | 1.9397 | 0 | 36
0350-L | 0 | 19.7452 | 0 | 0 | 1.2685 | 0 | 3
0358-B | 1 | 16.3178 | 0.061283 | 0 | 4.6959 | 0 | 14
0441-CFSP | 1 | 16.8082 | 0.059495 | 0 | 4.2055 | 0 | 18
0442-E | 1 | 14.2822 | 0.070017 | 0 | 6.7315 | 0 | 5
0442-H | 1 | 20.1808 | 0.049552 | 0 | 0.83288 | 0 | 27
0444-BRANCH | 1 | 15.4082 | 0.0649 | 0 | 5.6055 | 0 | 18
0445-D | 1 | 18.7534 | 0.053324 | 0 | 2.2603 | 0 | 13
0445-G | 1 | 18.4329 | 0.054251 | 0 | 2.5808 | 0 | 5
0445-K | 0 | 19.3205 | 0 | 0 | 1.6932 | 0 | 39
0445-LONG SPAN | 1 | 15.1479 | 0.066016 | 0 | 5.8658 | 0 | 6
0520-B | 1 | 17.6603 | 0.056624 | 0 | 3.3534 | 0 | 37
0520-G | 1 | 17.5781 | 0.056889 | 0 | 3.4356 | 0 | 15
0908-C | 1 | 19.1178 | 0.052307 | 0 | 1.8959 | 0 | 33
0908-I | 0 | 20.4795 | 0 | 0 | 0.53425 | 0 | 2
0908-I-FT | 1 | 20.7096 | 0.048287 | 0 | 0.30411 | 0 | 9
0971-C | 1 | 17.7753 | 0.056258 | 0 | 3.2384 | 0 | 34
0971-G | 1 | 17.3041 | 0.05779 | 0 | 3.7096 | 0 | 22
0971-I | 1 | 17.5068 | 0.057121 | 0 | 3.5068 | 0 | 25
0971-O | 1 | 17.6384 | 0.056695 | 0 | 3.3753 | 0 | 38
0971-P | 1 | 17.7945 | 0.056197 | 0 | 3.2192 | 0 | 21
0972-A | 1 | 17.5041 | 0.057129 | 0 | 3.5096 | 0 | 33
1030-E | 1 | 17.8904 | 0.055896 | 0 | 3.1233 | 0 | 31
1030-I | 1 | 16.6384 | 0.060102 | 0 | 4.3753 | 0 | 29
1030-M | 1 | 17.0384 | 0.058691 | 0 | 3.9753 | 0 | 27
1030-N | 1 | 17.6301 | 0.056721 | 0 | 3.3836 | 0 | 40
1250-AERIAL | 1 | 13.7616 | 0.072666 | 0 | 7.2521 | 0 | 3
PE1-B | 1 | 15.411 | 0.064889 | 0 | 5.6027 | 0 | 26
PE1-C | 1 | 16.2301 | 0.061614 | 0 | 4.7836 | 0 | 9
0078-G | 2 | 17.6767 | 0.11314 | 0 | 3.337 | 0 | 31
0157-CC | 2 | 20.9671 | 0.095387 | 0 | 0.046575 | 0 | 8
0157-CFSP | 2 | 19.1315 | 0.10454 | 0 | 1.8822 | 0 | 2
0175-A | 2 | 17.063 | 0.11721 | 0 | 3.9507 | 0 | 38
0176-J | 2 | 17.3863 | 0.11503 | 0 | 3.6274 | 0 | 23
0212-C-PH-03 | 2 | 21.0055 | 0.095213 | 0 | 0.0082192 | 0 | 4
0217-A | 2 | 19.989 | 0.10005 | 0 | 1.0247 | 0 | 36
0217-P | 2 | 19.2712 | 0.10378 | 0 | 1.7425 | 0 | 31
0220-A | 2 | 15.411 | 0.12978 | 0 | 5.6027 | 0 | 34
0220-C | 1 | 16.2795 | 0.061427 | 0 | 4.7342 | 0 | 17
0220-K | 2 | 16.7918 | 0.11911 | 0 | 4.2219 | 0 | 26
0220-O | 2 | 16.3507 | 0.12232 | 0 | 4.663 | 0 | 13
0221-N | 2 | 16.9699 | 0.11786 | 0 | 4.0438 | 0 | 44
0222-A | 2 | 14.0521 | 0.14233 | 0 | 6.9616 | 0 | 21
0222-D | 2 | 15.0438 | 0.13294 | 0 | 5.9699 | 0 | 27
0222-MM | 2 | 20.7479 | 0.096395 | 0 | 0.26575 | 0 | 46
0222-R2 | 2 | 14.1863 | 0.14098 | 0 | 6.8274 | 0 | 7
0222-T | 0 | 15.5044 | 0 | 0 | 5.5093 | 0 | 25
0222-W | 2 | 16.4904 | 0.12128 | 0 | 4.5233 | 0 | 42
0230-E | 2 | 18.4438 | 0.10844 | 0 | 2.5699 | 0 | 20
0237-J | 2 | 16.0493 | 0.12462 | 0 | 4.9644 | 0 | 26
0237-Q | 2 | 16.4301 | 0.12173 | 0 | 4.5836 | 0 | 15
0237-R | 2 | 17.3726 | 0.11512 | 0 | 3.6411 | 0 | 12
0239-RR R | 2 | 15.5781 | 0.12839 | 0 | 5.4356 | 0 | 14
0240-C | 2 | 16.1589 | 0.12377 | 0 | 4.8548 | 0 | 23
0350-A | 2 | 18.3808 | 0.10881 | 0 | 2.6329 | 0 | 27
0350-D | 2 | 19.9781 | 0.10011 | 0 | 1.0356 | 0 | 28
0350-G | 2 | 18.7479 | 0.10668 | 0 | 2.2658 | 0 | 19
0350-N (ASD) | 2 | 19.9562 | 0.10022 | 0 | 1.0575 | 0 | 11
0350-N-FT | 2 | 19.937 | 0.10032 | 0 | 1.0767 | 0 | 7
0350-P (R-CODE) | 2 | 18.4466 | 0.10842 | 0 | 2.5671 | 0 | 7
0444-BRANCH LN | 0 | 14.9116 | 0 | 0 | 6.1021 | 0 | 22
0444-RECONDUCTOR | 1 | 13.7397 | 0.072782 | 0 | 7.274 | 0 | 15
0445-E | 2 | 20.3781 | 0.098145 | 0 | 0.63562 | 0 | 52
0445-F | 2 | 18.4192 | 0.10858 | 0 | 2.5945 | 0 | 8
0445-M | 1 | 20.3205 | 0.049211 | 0 | 0.69315 | 0 | 15
0445-N | 2 | 19.3863 | 0.10317 | 0 | 1.6274 | 0 | 25
0445-V-FT | 0 | 20.7068 | 0 | 0 | 0.30685 | 0 | 4
0520-H | 2 | 18.137 | 0.11027 | 0 | 2.8767 | 0 | 21
0908-E | 2 | 19.7096 | 0.10147 | 0 | 1.3041 | 0 | 4
0908-H | 2 | 20.3068 | 0.098489 | 0 | 0.70685 | 0 | 12
0971-D | 2 | 17.7753 | 0.11252 | 0 | 3.2384 | 0 | 32
0973-A | 2 | 15.5288 | 0.12879 | 0 | 5.4849 | 0 | 17
0974-D | 2 | 17.8301 | 0.11217 | 0 | 3.1836 | 0 | 37
1030-R | 2 | 17.6301 | 0.11344 | 0 | 3.3836 | 0 | 32
0073-C | 3 | 14.9863 | 0.20018 | 0 | 6.0274 | 0 | 40
0078-E | 3 | 16.2356 | 0.18478 | 0 | 4.7781 | 0 | 28
0079-G | 3 | 16.1151 | 0.18616 | 0 | 4.8986 | 0 | 17
0157-M | 2 | 20.1096 | 0.099455 | 0 | 0.90411 | 0 | 37
0217-E | 3 | 19.9781 | 0.15016 | 0 | 1.0356 | 0 | 28
0217-H | 3 | 19.2712 | 0.15567 | 0 | 1.7425 | 0 | 29
0217-N | 3 | 19.1068 | 0.15701 | 0 | 1.9068 | 0 | 35
0220-N | 3 | 16.8301 | 0.17825 | 0 | 4.1836 | 0 | 22
0221-S | 3 | 18.6795 | 0.1606 | 0 | 2.3342 | 0 | 28
0222-EE | 3 | 20.8521 | 0.14387 | 0 | 0.16164 | 0 | 26
0222-FIRE RISK MITIG | 3 | 15.1288 | 0.1983 | 0 | 5.8849 | 0 | 73
0222-I | 3 | 16.1808 | 0.1854 | 0 | 4.8329 | 0 | 25
0222-K | 3 | 16.5479 | 0.18129 | 0 | 4.4658 | 0 | 28
0222-R | 3 | 16.2822 | 0.18425 | 0 | 4.7315 | 0 | 37
0230-D | 3 | 19.0795 | 0.15724 | 0 | 1.9342 | 0 | 38
0237-N | 3 | 16.6521 | 0.18016 | 0 | 4.3616 | 0 | 27
0442-B | 2 | 16.3562 | 0.12228 | 0 | 4.6575 | 0 | 25
0444-MCCAIN REBUILD: | 5 | 15.2438 | 0.328 | 0 | 5.7699 | 0 | 1
0445-J | 2 | 20.4219 | 0.097934 | 0 | 0.59178 | 0 | 29
0520-C | 3 | 17.6384 | 0.17008 | 0 | 3.3753 | 0 | 18
0971-E | 3 | 17.1973 | 0.17445 | 0 | 3.8164 | 0 | 17
1030-D | 1 | 19.7288 | 0.050687 | 0 | 1.2849 | 0 | 42
1030-K | 3 | 17.5781 | 0.17067 | 0 | 3.4356 | 0 | 29
1030-U | 3 | 17.8904 | 0.16769 | 0 | 3.1233 | 0 | 34
0157-K | 4 | 20.7205 | 0.19305 | 0 | 0.29315 | 0 | 39
0157-T | 4 | 19.9589 | 0.20041 | 0 | 1.0548 | 0 | 8
0175-B | 3 | 17.3096 | 0.17331 | 0 | 3.7041 | 0 | 28
0175-C | 4 | 17.2548 | 0.23182 | 0 | 3.7589 | 0 | 44
0176-C | 4 | 17.1205 | 0.23364 | 0 | 3.8932 | 0 | 23
0217-M | 4 | 19.1836 | 0.20851 | 0 | 1.8301 | 0 | 36
0220-Q | 3 | 17.3452 | 0.17296 | 0 | 3.6685 | 0 | 11
0230-2013 FIRE HARDN | 4 | 15.3288 | 0.26095 | 0 | 5.6849 | 0 | 2
0230-C | 4 | 19.0384 | 0.2101 | 0 | 1.9753 | 0 | 36
0230-G | 4 | 18.4438 | 0.21687 | 0 | 2.5699 | 0 | 16
0442-F | 4 | 16.789 | 0.23825 | 0 | 4.2247 | 0 | 45
0520-L | 4 | 18.4466 | 0.21684 | 0 | 2.5671 | 0 | 35
0971-A | 4 | 17.411 | 0.22974 | 0 | 3.6027 | 0 | 36
0971-F | 3 | 18.1753 | 0.16506 | 0 | 2.8384 | 0 | 37
0972-B | 4 | 17.3616 | 0.23039 | 0 | 3.6521 | 0 | 25
1030-J | 4 | 17.9014 | 0.22345 | 0 | 3.1123 | 0 | 37
1030-O | 4 | 17.3616 | 0.23039 | 0 | 3.6521 | 0 | 52
0079-FIRE RISK | 5 | 16.0959 | 0.31064 | 0 | 4.9178 | 0 | 73
0212-D | 5 | 20.7836 | 0.24057 | 0 | 0.23014 | 0 | 36
0212-E | 5 | 20.6082 | 0.24262 | 0 | 0.40548 | 0 | 64
0215-B | 5 | 18.4466 | 0.27105 | 0 | 2.5671 | 0 | 30
0445-O | 5 | 20.7068 | 0.24147 | 0 | 0.30685 | 0 | 27
0908-D | 5 | 19.8384 | 0.25204 | 0 | 1.1753 | 0 | 30
0908-F | 5 | 20.6685 | 0.24191 | 0 | 0.34521 | 0 | 39
0972-F-CC | 5 | 20.8658 | 0.23963 | 0 | 0.14795 | 0 | 22
0974-B | 5 | 17.937 | 0.27875 | 0 | 3.0767 | 0 | 22
0078-D | 6 | 17.674 | 0.33948 | 0 | 3.3397 | 0 | 29
0157-H | 5 | 20.8822 | 0.23944 | 0 | 0.13151 | 0 | 37
0215-A | 6 | 18.4959 | 0.3244 | 0 | 2.5178 | 0 | 27
0217-D | 6 | 19.9781 | 0.30033 | 0 | 1.0356 | 0 | 36
0217-R | 6 | 19.7123 | 0.30438 | 0 | 1.3014 | 0 | 28
0237-H | 7 | 16.1221 | 0.43419 | 0 | 4.8916 | 0 | 28
PE1-A | 6 | 16.2301 | 0.36968 | 0 | 4.7836 | 0 | 57
0217-J | 7 | 19.463 | 0.35966 | 0 | 1.5507 | 0 | 28
0520-F | 7 | 18.5753 | 0.37684 | 0 | 2.4384 | 0 | 44
0157-W | 9 | 20.2959 | 0.44344 | 0 | 0.71781 | 0 | 37
0230-B | 9 | 19.0384 | 0.47273 | 0 | 1.9753 | 0 | 46
0212-A | 8 | 20 | 0.4 | 0 | 1.0137 | 0 | 24
0444-CFSP | 11 | 19.9589 | 0.55113 | 0 | 1.0548 | 0 | 46
0908-G | 12 | 20.3041 | 0.59101 | 0 | 0.70959 | 0 | 42
0212-B | 22 | 20 | 1.1 | 0 | 1.0137 | 0 | 36
0217-V | 0 | 19.9808 | 0 | 0 | 1.0329 | 0 | 6
0222-CC | 0 | 20.6082 | 0 | 0 | 0.40548 | 0 | 6
0222-N | 0 | 16.6521 | 0 | 0 | 4.3616 | 0 | 28
1458-A | 0 | 13.6904 | 0 | 0 | 7.3233 | 0 | 2
0908-FAIRFIELD | 0 | 13.9753 | 0 | 0 | 7.0384 | 0 | 7
0222-1C | 0 | 14.0451 | 0 | 0 | 6.9686 | 0 | 19
0233-MN | 0 | 14.0701 | 0 | 0 | 6.9436 | 0 | 44
0441-CFSP MINE LINE | 0 | 14.074 | 0 | 0 | 6.9397 | 0 | 1
C441 4 SINGLE POLE R | 0 | 14.074 | 0 | 0 | 6.9397 | 0 | 3
0222-FH | 0 | 14.1863 | 0 | 0 | 6.8274 | 0 | 1
0441-REBUILD | 0 | 14.4 | 0 | 0 | 6.6137 | 0 | 10
0350-LONG SPAN | 0 | 14.5501 | 0 | 0 | 6.4636 | 0 | 5
0354-FH | 0 | 14.6301 | 0 | 0 | 6.3836 | 0 | 1
0357-CFSP | 0 | 14.6757 | 0 | 0 | 6.338 | 0 | 14
C0236-LS-D | 0 | 14.7616 | 0 | 0 | 6.2521 | 0 | 1
0973-FTZ WILDCAT CAN | 0 | 14.7808 | 0 | 0 | 6.2329 | 0 | 6
0239-R5 | 0 | 14.8137 | 0 | 0 | 6.2 | 0 | 2
0220-J | 0 | 14.8163 | 0 | 0 | 6.1974 | 0 | 24
0217-LS | 0 | 14.8356 | 0 | 0 | 6.1781 | 0 | 2
0073-LONG SPAN | 0 | 14.9306 | 0 | 0 | 6.0831 | 0 | 3
0073-D | 0 | 14.937 | 0 | 0 | 6.0767 | 0 | 4
0220-D | 0 | 15.0274 | 0 | 0 | 5.9863 | 0 | 14
0220-E | 0 | 15.0274 | 0 | 0 | 5.9863 | 0 | 3
1233-PA | 0 | 15.0301 | 0 | 0 | 5.9836 | 0 | 6
0220-F | 0 | 15.0438 | 0 | 0 | 5.9699 | 0 | 14
0222-PH4 SEC2 | 0 | 15.0443 | 0 | 0 | 5.9694 | 0 | 18
0441-A | 0 | 15.0524 | 0 | 0 | 5.9613 | 0 | 8
0521-LONG SPAN | 0 | 15.1425 | 0 | 0 | 5.8712 | 0 | 4
0236-Q | 0 | 15.1562 | 0 | 0 | 5.8575 | 0 | 1
0073-F | 0 | 15.2 | 0 | 0 | 5.8137 | 0 | 7
0237-L | 0 | 15.2929 | 0 | 0 | 5.7208 | 0 | 24
0221-B | 0 | 15.3035 | 0 | 0 | 5.7102 | 0 | 19
0221-C | 0 | 15.3123 | 0 | 0 | 5.7014 | 0 | 15
0079-I | 0 | 15.3315 | 0 | 0 | 5.6822 | 0 | 24
0222-M | 0 | 15.5776 | 0 | 0 | 5.4361 | 0 | 17
0222-H | 0 | 15.6022 | 0 | 0 | 5.4115 | 0 | 10
0079-H | 0 | 15.8022 | 0 | 0 | 5.2115 | 0 | 26
0222-Q | 0 | 15.8133 | 0 | 0 | 5.2004 | 0 | 15
0358-D | 0 | 15.8603 | 0 | 0 | 5.1534 | 0 | 14
0442-C | 0 | 15.8712 | 0 | 0 | 5.1425 | 0 | 8
0073-I | 0 | 15.8986 | 0 | 0 | 5.1151 | 0 | 5
0078-A | 0 | 15.9219 | 0 | 0 | 5.0918 | 0 | 8
0079-O | 0 | 15.9674 | 0 | 0 | 5.0463 | 0 | 12
0079-J | 0 | 16.0192 | 0 | 0 | 4.9945 | 0 | 8
0220-M | 0 | 16.068 | 0 | 0 | 4.9457 | 0 | 57
CPE1-D | 0 | 16.0795 | 0 | 0 | 4.9342 | 0 | 26
0079-L | 0 | 16.137 | 0 | 0 | 4.8767 | 0 | 16
0079-N | 0 | 16.137 | 0 | 0 | 4.8767 | 0 | 7
0442-I | 0 | 16.1589 | 0 | 0 | 4.8548 | 0 | 13
0221-E | 0 | 16.1808 | 0 | 0 | 4.8329 | 0 | 5
0222-BB | 0 | 16.2466 | 0 | 0 | 4.7671 | 0 | 17
0079-F | 0 | 16.2603 | 0 | 0 | 4.7534 | 0 | 14
0240-H | 0 | 16.2603 | 0 | 0 | 4.7534 | 0 | 6
0240-A | 0 | 16.3288 | 0 | 0 | 4.6849 | 0 | 34
0222-V | 0 | 16.3738 | 0 | 0 | 4.6399 | 0 | 33
0237-E | 0 | 16.3842 | 0 | 0 | 4.6295 | 0 | 18
0445-A | 0 | 16.3945 | 0 | 0 | 4.6192 | 0 | 1
0073-J | 0 | 16.411 | 0 | 0 | 4.6027 | 0 | 6
0078-F | 0 | 16.411 | 0 | 0 | 4.6027 | 0 | 10
0222-L | 0 | 16.4881 | 0 | 0 | 4.5256 | 0 | 6
0221-K | 0 | 16.6164 | 0 | 0 | 4.3973 | 0 | 25
1030-S | 0 | 16.6164 | 0 | 0 | 4.3973 | 0 | 13
1215-A | 0 | 16.6548 | 0 | 0 | 4.3589 | 0 | 14
0237-S | 0 | 16.6822 | 0 | 0 | 4.3315 | 0 | 36
1030-H | 0 | 16.7918 | 0 | 0 | 4.2219 | 0 | 28
0973-B | 0 | 16.7973 | 0 | 0 | 4.2164 | 0 | 26
0175-E | 0 | 16.8301 | 0 | 0 | 4.1836 | 0 | 12
0220-P | 0 | 16.8301 | 0 | 0 | 4.1836 | 0 | 13
0222-X | 0 | 16.8466 | 0 | 0 | 4.1671 | 0 | 26
0222-Y | 0 | 16.8959 | 0 | 0 | 4.1178 | 0 | 21
0221-V | 0 | 16.926 | 0 | 0 | 4.0877 | 0 | 20
0221-J | 0 | 17.0082 | 0 | 0 | 4.0055 | 0 | 12
0176-G | 0 | 17.0438 | 0 | 0 | 3.9699 | 0 | 18
1030-L | 0 | 17.2356 | 0 | 0 | 3.7781 | 0 | 23
0073-H | 0 | 17.2548 | 0 | 0 | 3.7589 | 0 | 1
0176-B | 0 | 17.3534 | 0 | 0 | 3.6603 | 0 | 21
1458-B | 0 | 17.3918 | 0 | 0 | 3.6219 | 0 | 34
0972-E | 0 | 17.4 | 0 | 0 | 3.6137 | 0 | 31
1030-Q | 0 | 17.463 | 0 | 0 | 3.5507 | 0 | 29
0520-D | 0 | 17.4822 | 0 | 0 | 3.5315 | 0 | 21
0971-K | 0 | 17.5068 | 0 | 0 | 3.5068 | 0 | 19
0222-RR | 0 | 17.5726 | 0 | 0 | 3.4411 | 0 | 1
1030-P | 0 | 17.5781 | 0 | 0 | 3.4356 | 0 | 33
0520-A | 0 | 17.6384 | 0 | 0 | 3.3753 | 0 | 27
0974-C | 0 | 17.7863 | 0 | 0 | 3.2274 | 0 | 1
0974-F | 0 | 17.8712 | 0 | 0 | 3.1425 | 0 | 3
0974-A | 0 | 17.9562 | 0 | 0 | 3.0575 | 0 | 6
0221-G | 0 | 18.0932 | 0 | 0 | 2.9205 | 0 | 18
0075-A | 0 | 18.1041 | 0 | 0 | 2.9096 | 0 | 20
0221-Q | 0 | 18.137 | 0 | 0 | 2.8767 | 0 | 11
0520-J | 0 | 18.137 | 0 | 0 | 2.8767 | 0 | 12
0520-I | 0 | 18.137 | 0 | 0 | 2.8767 | 0 | 1
0221-P | 0 | 18.137 | 0 | 0 | 2.8767 | 0 | 7
0520-M | 0 | 18.2329 | 0 | 0 | 2.7808 | 0 | 18
0350-B | 0 | 18.3808 | 0 | 0 | 2.6329 | 0 | 26
0520-E | 0 | 18.4438 | 0 | 0 | 2.5699 | 0 | 23
0520-K | 0 | 18.4849 | 0 | 0 | 2.5288 | 0 | 37
0221-BB | 0 | 18.5178 | 0 | 0 | 2.4959 | 0 | 2
0221-U | 0 | 18.5315 | 0 | 0 | 2.4822 | 0 | 6
0221-Y-PH1-SLAUGHTER | 0 | 18.5753 | 0 | 0 | 2.4384 | 0 | 4
0217-B | 0 | 18.6493 | 0 | 0 | 2.3644 | 0 | 15
0217-I | 0 | 18.6493 | 0 | 0 | 2.3644 | 0 | 10
0221-W | 0 | 18.6575 | 0 | 0 | 2.3562 | 0 | 1
0217-O | 0 | 18.6767 | 0 | 0 | 2.337 | 0 | 17
0350-H | 0 | 18.7836 | 0 | 0 | 2.2301 | 0 | 39
0908-A | 0 | 18.9836 | 0 | 0 | 2.0301 | 0 | 4
0176-D | 0 | 19.0384 | 0 | 0 | 1.9753 | 0 | 1
0176-H | 0 | 19.0384 | 0 | 0 | 1.9753 | 0 | 7
0217-S | 0 | 19.0795 | 0 | 0 | 1.9342 | 0 | 16
0217-L | 0 | 19.2712 | 0 | 0 | 1.7425 | 0 | 20
0972-FH | 0 | 19.4356 | 0 | 0 | 1.5781 | 0 | 1
0445-U | 0 | 19.7096 | 0 | 0 | 1.3041 | 0 | 22
0908-K | 0 | 19.7096 | 0 | 0 | 1.3041 | 0 | 10
0217-U | 0 | 19.7425 | 0 | 0 | 1.2712 | 0 | 4
0350-M | 0 | 19.7452 | 0 | 0 | 1.2685 | 0 | 7
0222-QQ-FT | 0 | 19.8055 | 0 | 0 | 1.2082 | 0 | 2
0908-B | 0 | 19.8384 | 0 | 0 | 1.1753 | 0 | 25
0222-G | 0 | 19.9096 | 0 | 0 | 1.1041 | 0 | 7
0217-X (ASD) | 0 | 19.9397 | 0 | 0 | 1.074 | 0 | 6
0350-O (ASD) | 0 | 19.9562 | 0 | 0 | 1.0575 | 0 | 3
0442-L | 0 | 19.9589 | 0 | 0 | 1.0548 | 0 | 14
0217-T | 0 | 19.9781 | 0 | 0 | 1.0356 | 0 | 2
0230-H (ASD) | 0 | 19.9808 | 0 | 0 | 1.0329 | 0 | 5
0222-UU-FT | 0 | 19.9973 | 0 | 0 | 1.0164 | 0 | 1
0448-C-FT | 0 | 20.011 | 0 | 0 | 1.0027 | 0 | 1
0212-U-FT | 0 | 20.1726 | 0 | 0 | 0.8411 | 0 | 1
0157-X-FT | 0 | 20.1836 | 0 | 0 | 0.83014 | 0 | 1
0211-FTZAP | 0 | 20.211 | 0 | 0 | 0.80274 | 0 | 1
0157-Q | 0 | 20.2959 | 0 | 0 | 0.71781 | 0 | 21
0222-GG | 0 | 20.3342 | 0 | 0 | 0.67945 | 0 | 16
0212-V | 0 | 20.3836 | 0 | 0 | 0.63014 | 0 | 2
0520-O-FT | 0 | 20.3973 | 0 | 0 | 0.61644 | 0 | 1
0448-O-FT | 0 | 20.4137 | 0 | 0 | 0.6 | 0 | 1
0908-J | 0 | 20.4521 | 0 | 0 | 0.56164 | 0 | 16
0212-O-FT | 0 | 20.663 | 0 | 0 | 0.35068 | 0 | 1
0157-I | 0 | 20.6849 | 0 | 0 | 0.32877 | 0 | 6
PE1-D | 0 | 20.7014 | 0 | 0 | 0.31233 | 0 | 1
0212-F | 0 | 20.7041 | 0 | 0 | 0.30959 | 0 | 2
0211-FTZAP-FT | 0 | 20.7068 | 0 | 0 | 0.30685 | 0 | 1
0445-P-FT | 0 | 20.7178 | 0 | 0 | 0.29589 | 0 | 1
0212-H | 0 | 20.7178 | 0 | 0 | 0.29589 | 0 | 19
0448-F-FT | 0 | 20.7233 | 0 | 0 | 0.29041 | 0 | 1
0157-H-FT | 0 | 20.7781 | 0 | 0 | 0.23562 | 0 | 1
0222-JJ | 0 | 20.8055 | 0 | 0 | 0.20822 | 0 | 2
0357-OH-RFS | 0 | 20.8466 | 0 | 0 | 0.16712 | 0 | 2
0176-K-FT | 0 | 20.874 | 0 | 0 | 0.13973 | 0 | 1
0357-G-FT | 0 | 20.9288 | 0 | 0 | 0.084932 | 0 | 1
0073-FTZAP-FT | 0 | 20.937 | 0 | 0 | 0.076712 | 0 | 6
0230-FUSING-FT | 0 | 20.9534 | 0 | 0 | 0.060274 | 0 | 2
0444-B-FT | 0 | 20.9699 | 0 | 0 | 0.043836 | 0 | 1
Average | 1.4112 | 17.6882 | 0.078298 | 0.14721 | 3.325 | 0.041544 | 20.0152
| Unhardened Fault Rate | 9.2315
| Hardened Fault Rate | 5.1229
| Fault Rate Reduction | 44.51%

## Summary by Cause Category
Prim_Cause Description (group) | Avg. Hardened years | Avg. Unhardened years | Avg Hardened Faults | Avg Unardened Faults | No of poles | Avg Hardened rate | Avg Unhardened rate | Rate reduction
Equipment failure | 3.33 | 17.69 | 0.071066 | 0.53553 | 20.02 | 2.4688 | 3.5021 | 0.29505
Foreign object | 3.32 | 17.69 | 0.038071 | 0.3198 | 20.02 | 1.3266 | 2.0913 | 0.36568
Miscellaneous | 3.32 | 17.69 | 0 | 0.015228 | 20.02 | 0 | 0.099587 | 1
SDGE Crew Contact | 3.32 | 17.69 | 0 | 0.038071 | 20.02 | 0 | 0.24897 | 1
Third PArty Contact | 3.32 | 17.69 | 0.022843 | 0.17259 | 20.02 | 0.79594 | 1.1287 | 0.29478
Undetermined | 3.32 | 17.69 | 0.0050761 | 0.022843 | 20.02 | 0.17688 | 0.14938 | -0.18407
Weather Related | 3.32 | 17.69 | 0.010152 | 0.30711 | 20.02 | 0.35375 | 2.0083 | 0.82386
[6 empty] | 5.122 | 9.2284 | 44.5%