## Lifecycle Cost HFTD Only
upstreamardfacilityid | conductor_style | hftd | miles | hftd_miles | hftd_oh_miles | oh_miles | if_ug_mit_miles | detailed_inspection | detailed_inspection_per_mile | patrol_inspection | patrol_inspection_per_mile | wood_pole_intrusive_inspection | wood_pole_intrusive_inspection_per_mile | drone_inspection | drone_inspection_per_mile | total_oh_inspection_cost | total_oh_inspection_cost_per_mile | cmp_pole_repair | cmp_pole_repair_per_mile | cmp_equipment_repair_(o&m) | cmp_equipment_repair_(o&m)_per_mile | cmp_equipment_repair_(capital) | cmp_equipment_repair_(capital)_per_mile | cmp_equipment_repair | cmp_equipment_repair_per_mile | total_oh_repair_cost | total_oh_repair_cost_per_mile | pole_replacement_cost | pole_replacement_cost_per_mile | total_oh_asset_cost | total_oh_asset_cost_per_mile | ug_subsurface_inspection | ug_subsurface_inspection_per_mile | ug_padmount_inspection | ug_padmount_inspection_per_mile | total_ug_inspection_cost | total_ug_inspection_cost_per_mile | ug_repair_and_replace_(capital) | ug_repair_and_replace_(capital)_per_mile | ug_repair_and_replace_(o&m) | ug_repair_and_replace_(o&m)_per_mile | total_ug_repair_cost | total_ug_repair_cost_per_mile | total_ug_asset_cost | total_ug_asset_cost_per_mile | veg_inspection | veg_inspection_per_mile | tree_trimming | tree_trimming_per_mile | tree_auditing | tree_auditing_per_mile | veg_pole_clearance_inspection | veg_pole_clearance_inspection_per_mile | veg_pole_clearance | veg_pole_clearance_per_mile | veg_pole_clearance_auditing | veg_pole_clearance_auditing_per_mile | fuels_management | fuels_management_per_mile | total_oh_veg_cost | total_oh_veg_cost_per_mile | psps_general_cost_oh | psps_general_cost_oh_per_mile | psps_general_cost_ug | psps_general_cost_ug_per_mile | psps_cc_activation_cost | psps_cc_activation_cost_per_mile | psps_ug_activation_cost | psps_ug_activation_cost_per_mile | total_cc_psps_cost | total_cc_psps_cost_per_mile | total_ug_psps_cost | total_ug_psps_cost_per_mile | efd | efd_per_mile | fcp | fcp_per_mile | total_oh_peds_cost | total_oh_peds_cost_per_mile | microgrid_cost | microgrid_cost_per_mile | total_if_cc_maintenance | total_if_cc_maintenance_per_mile | total_if_ug_maintenance | total_if_ug_maintenance_per_mile | total_if_cc_capital | total_if_ug_capital | if_cc_cost | if_ug_cost
1001-1820F | oh | 2 | 31.2983 | 30.4687 | 6.1076 | 6.5366 | 8.4934 | 26294.07 | 4022.6202 | 50374.5 | 7706.5848 | 47217.5 | 7223.6085 | 115429.2857 | 17659.0452 | 239315.3557 | 36611.8587 | 1986600 | 303921.6527 | 3632648.8687 | 555743.8075 | 1242707.224 | 190116.5979 | 4875356.0927 | 745860.4053 | 6861956.0927 | 1049782.0581 | 2225000 | 340393.4749 | 9326271.4485 | 1426787.3916 | 88673.31 | 13565.7601 | 167879.25 | 25683.1466 | 256552.56 | 39248.9067 | 1587598 | 242880 | 28760.8333 | 4400 | 1616358.8333 | 247280 | 1872911.3933 | 286528.9067 | 1354320 | 207191.7712 | 8156016 | 1247754.8889 | 413820 | 63308.5968 | 10395 | 1590.2877 | 116270 | 17787.6626 | 9240 | 1413.5891 | 228900 | 35018.4568 | 10288961 | 1574065.2531 | 1667288.7833 | 255071.5607 | 833745.1667 | 127551.1975 | 104443.8818 | 15978.4341 | 45810.2323 | 7008.3165 | 1771732.6652 | 271049.9948 | 879555.399 | 134559.514 | 2966.8761 | 453.89 | 9900 | 1514.5597 | 12866.8761 | 1968.4497 | 0 | 0 | 21399831.9897 | 3273871.0893 | 2752466.7923 | 421088.4207 | 6536553.0303 | 16986791.3477 | 27936385.02 | 19739258.14
1021-1748F | oh | 3 | 26.1833 | 26.1833 | 17.8345 | 17.8345 | 22.7252 | 86016.26 | 4823.0344 | 164791 | 9240.028 | 156145 | 8755.2365 | 412806.4286 | 23146.5491 | 819758.6886 | 45964.848 | 6498800 | 364395.4718 | 11883549.0125 | 666324.7752 | 4065290.2987 | 227945.6787 | 15948839.3112 | 894270.4539 | 22447639.3112 | 1258665.9257 | 8775000 | 492024.7223 | 32042397.9997 | 1796655.496 | 290078.58 | 16265.0522 | 135481.5 | 7596.6094 | 425560.08 | 23861.6616 | 4331636 | 242880 | 78471.6667 | 4400 | 4410107.6667 | 247280 | 4835667.7467 | 271141.6616 | 1357290 | 76104.8701 | 8173902 | 458320.4401 | 414727.5 | 23254.2659 | 76230 | 4274.3071 | 852646.6667 | 47808.9162 | 67760 | 3799.3841 | 1678600 | 94121.1053 | 12621156.1667 | 707683.2887 | 4868578.3792 | 272987 | 2434583.4583 | 136510 | 300746.1937 | 16863.198 | 133015.7527 | 7458.352 | 5169324.5729 | 289850.198 | 2567599.2111 | 143968.352 | 8094.8875 | 453.89 | 9900 | 555.1048 | 17994.8875 | 1008.9948 | 0 | 0 | 49850873.6267 | 2795197.9775 | 7403266.9577 | 415110.0136 | 17834469.697 | 45450452.0327 | 67685343.3237 | 52853718.9905
1021-1760R | oh | 3 | 5.3744 | 5.3744 | 2.9629 | 2.9629 | 3.8132 | 14675.76 | 4953.2097 | 28116 | 9489.4196 | 23842.5 | 8047.0724 | 70431.4286 | 23771.2825 | 137065.6886 | 46260.9841 | 1108800 | 374230.6316 | 2027524.95 | 684309.1112 | 693604.032 | 234098.0113 | 2721128.982 | 918407.1225 | 3829928.982 | 1292637.7541 | 1100000 | 371260.5472 | 5066994.6706 | 1710159.2854 | 49492.08 | 16704.0515 | 30630.6 | 10338.1212 | 80122.68 | 27042.1727 | 719624 | 242880 | 13036.6667 | 4400 | 732660.6667 | 247280 | 812783.3467 | 274322.1727 | 231660 | 78187.4712 | 1395108 | 470862.3268 | 70785 | 23890.6162 | 16830 | 5680.2864 | 188246.6667 | 63535.055 | 14960 | 5049.1434 | 370600 | 125081.0534 | 2288189.6667 | 772285.9524 | 808827.3917 | 272987 | 404462.5833 | 136510 | 50030.392 | 16885.737 | 22109.9911 | 7462.334 | 858857.7836 | 289872.737 | 426572.5744 | 143972.334 | 1344.8211 | 453.89 | 9900 | 3341.3449 | 11244.8211 | 3795.2349 | 0 | 0 | 8225286.9419 | 2776113.2098 | 1239355.9211 | 418294.5067 | 2962878.7879 | 7626300.2925 | 11188165.7298 | 8865656.2136
1021-25R | oh | 3 | 7.7464 | 7.7464 | 6.9741 | 6.9741 | 9.007 | 28740.03 | 4120.9939 | 55060.5 | 7895.0504 | 43945 | 6301.2139 | 137928.2143 | 19777.3395 | 265673.7443 | 38094.5977 | 2171400 | 311354.0993 | 3970569.6938 | 569334.6002 | 1358307.896 | 194765.9259 | 5328877.5898 | 764100.5261 | 7500277.5898 | 1075454.6255 | 1950000 | 279607.8538 | 9715951.334 | 1393157.0769 | 96921.99 | 13897.5126 | 36521.1 | 5236.711 | 133443.09 | 19134.2236 | 1693858 | 242880 | 30685.8333 | 4400 | 1724543.8333 | 247280 | 1857986.9233 | 266414.2236 | 626670 | 89857.3609 | 3773946 | 541140.9956 | 191482.5 | 27456.4158 | 26235 | 3761.801 | 293443.3333 | 42076.4414 | 23320 | 3343.8232 | 577700 | 82835.619 | 5512796.8333 | 790472.4569 | 1903825.8146 | 272987 | 952027.9792 | 136510 | 117802.7607 | 16891.578 | 52050.7681 | 7463.489 | 2021628.5753 | 289878.578 | 1004078.7472 | 143973.489 | 3165.4529 | 453.89 | 9900 | 1419.5476 | 13065.4529 | 1873.4376 | 0 | 0 | 17263442.1956 | 2475381.5494 | 2862065.6706 | 410387.7126 | 6974053.0303 | 18014060.7545 | 24237495.2259 | 20876126.4251
1021-855 | oh | 3 | 3.7047 | 3.7047 | 2.9134 | 2.9134 | 3.5242 | 12637.46 | 4337.6317 | 24211 | 8310.0878 | 21505 | 7381.291 | 60649.2857 | 20817.0206 | 119002.7457 | 40846.0312 | 954800 | 327721.7708 | 1745924.2625 | 599264.1296 | 597270.1387 | 205004.6371 | 2343194.4012 | 804268.7667 | 3297994.4012 | 1131990.5375 | 1175000 | 403302.3467 | 4591997.1469 | 1576138.9154 | 42618.18 | 14628.0953 | 17082.45 | 5863.3125 | 59700.63 | 20491.4078 | 707618 | 242880 | 12819.1667 | 4400 | 720437.1667 | 247280 | 780137.7967 | 267771.4078 | 266310 | 91407.1898 | 1603778 | 550474.4094 | 81372.5 | 27929.9746 | 8910 | 3058.2331 | 99660 | 34206.9037 | 7920 | 2718.4294 | 196200 | 67342.911 | 2264150.5 | 777138.0511 | 795333.1479 | 272987 | 397714.6458 | 136510 | 49227.0101 | 16896.484 | 21747.3637 | 7464.479 | 844560.158 | 289883.484 | 419462.0096 | 143974.479 | 1322.3844 | 453.89 | 9900 | 3398.0368 | 11222.3844 | 3851.9268 | 0 | 0 | 7711930.1894 | 2647012.3773 | 1199599.8062 | 411745.8868 | 2913446.9697 | 7048337.6821 | 10625377.159 | 8247937.4883
1022-17F | oh | 3 | 4.7534 | 4.7534 | 4.5506 | 4.5506 | 5.8703 | 21809.81 | 4792.7663 | 41783.5 | 9182.0402 | 34127.5 | 7499.6129 | 104668.9286 | 23001.2878 | 202389.7386 | 44475.7073 | 1647800 | 362108.6278 | 3013127.3563 | 662143.1074 | 1030772.6587 | 226515.1554 | 4043900.0149 | 888658.2627 | 5691700.0149 | 1250766.8905 | 1700000 | 373579.7228 | 7594089.7535 | 1668822.3207 | 73550.73 | 16162.9773 | 24740.1 | 5436.7057 | 98290.83 | 21599.683 | 1105242 | 242880 | 20022.5 | 4400 | 1125264.5 | 247280 | 1223555.33 | 268879.683 | 387090 | 85064.1029 | 2331142 | 512274.9307 | 118277.5 | 25991.8092 | 24255 | 5330.1036 | 271296.6667 | 59618.1962 | 21560 | 4737.8699 | 534100 | 117369.9588 | 3687721.1667 | 810386.9713 | 1242245.9562 | 272987 | 621198.0625 | 136510 | 75956.3549 | 16691.62 | 33807.5407 | 7429.301 | 1318202.3111 | 289678.62 | 655005.6032 | 143939.301 | 2065.4574 | 453.89 | 9900 | 2175.5525 | 11965.4574 | 2629.4425 | 0 | 0 | 12611978.6887 | 2771517.3545 | 1878560.9332 | 412818.984 | 4550568.1818 | 11740632.4204 | 17162546.8705 | 13619193.3536
1022-322R | oh | 3 | 4.122 | 4.122 | 3.6661 | 3.6661 | 4.9918 | 15694.91 | 4281.0934 | 30068.5 | 8201.7709 | 27582.5 | 7523.6659 | 75322.5 | 20545.6837 | 148668.41 | 40552.2139 | 1185800 | 323450.1214 | 2168325.2938 | 591453.0945 | 741770.9787 | 202332.5292 | 2910096.2724 | 793785.6237 | 4095896.2724 | 1117235.7451 | 1400000 | 381877.357 | 5644564.6824 | 1539665.3161 | 52929.03 | 14437.4272 | 22972.95 | 6266.321 | 75901.98 | 20703.7482 | 890422 | 242880 | 16130.8333 | 4400 | 906552.8333 | 247280 | 982454.8133 | 267983.7482 | 218790 | 59679.2478 | 1317602 | 359401.6924 | 66852.5 | 18235.3257 | 20295 | 5535.8578 | 227003.3333 | 61919.595 | 18040 | 4920.7625 | 446900 | 121900.7078 | 2315482.8333 | 631593.189 | 1000797.2271 | 272987 | 500459.1042 | 136510 | 61242.5235 | 16705.095 | 27244.05 | 7431.347 | 1062039.7506 | 289692.095 | 527703.1541 | 143941.347 | 1664.0054 | 453.89 | 9900 | 2700.4185 | 11564.0054 | 3154.3085 | 0 | 0 | 9033651.2717 | 2464104.9086 | 1510157.9675 | 411925.0952 | 3666098.4848 | 9983625.5896 | 12699749.7566 | 11493783.5571
1023-200R | oh | 2 | 4.6284 | 4.6284 | 3.7112 | 3.7112 | 4.4861 | 15083.42 | 4064.3255 | 28897 | 7786.4843 | 14025 | 3779.1273 | 72387.8571 | 19505.3782 | 130393.2771 | 35135.3153 | 1139600 | 307072.6206 | 2083845.0875 | 561505.5913 | 712870.8107 | 192087.6693 | 2796715.8982 | 753593.2606 | 3936315.8982 | 1060665.8812 | 650000 | 175146.7211 | 4716709.1753 | 1270947.9176 | 50866.86 | 13706.4058 | 18849.6 | 5079.1471 | 69716.46 | 18785.5529 | 901370 | 242880 | 16329.1667 | 4400 | 917699.1667 | 247280 | 987415.6267 | 266065.5529 | 206910 | 55753.2432 | 1246058 | 335758.42 | 63222.5 | 17035.7132 | 11385 | 3067.7622 | 127343.3333 | 34313.4881 | 10120 | 2726.8997 | 250700 | 67552.743 | 1915738.8333 | 516208.2695 | 1013102.3229 | 272987 | 506612.3958 | 136510 | 59373.0949 | 15998.466 | 27115.9284 | 7306.563 | 1072475.4179 | 288985.466 | 533728.3242 | 143816.563 | 1684.4649 | 453.89 | 9900 | 2667.6193 | 11584.4649 | 3121.5093 | 0 | 0 | 7716507.8914 | 2079263.1624 | 1521143.9509 | 409882.1159 | 3711174.2424 | 8972257.6113 | 11427682.1338 | 10493401.5622
1023-46AE | oh | 2 | 29.0945 | 29.0945 | 17.1742 | 17.1742 | 21.5326 | 76843.91 | 4474.3697 | 147218.5 | 8572.0521 | 133237.5 | 7757.9841 | 368786.7857 | 21473.2491 | 726086.6957 | 42277.655 | 5805800 | 338052.7569 | 10616345.9187 | 618155.1219 | 3631787.7787 | 211467.1314 | 14248133.6974 | 829622.2532 | 20053933.6974 | 1167675.0102 | 6225000 | 362461.4027 | 27005020.3931 | 1572414.0679 | 259146.03 | 15089.2263 | 154331.1 | 8986.1955 | 413477.13 | 24075.4218 | 4171280 | 242880 | 75566.6667 | 4400 | 4246846.6667 | 247280 | 4660323.7967 | 271355.4218 | 1599840 | 93153.4539 | 9634592 | 560990.8002 | 488840 | 28463.5554 | 51975 | 3026.3344 | 581350 | 33850.1103 | 46200 | 2690.075 | 1144500 | 66640.494 | 13547297 | 788814.8231 | 4688344.9167 | 272987 | 2344455.8333 | 136510 | 274175.1362 | 15964.322 | 125381.1579 | 7300.535 | 4962520.0528 | 288951.322 | 2469836.9912 | 143810.535 | 7795.2169 | 453.89 | 9900 | 576.4446 | 17695.2169 | 1030.3346 | 0 | 0 | 45532532.6629 | 2651210.5476 | 7130160.7879 | 415165.9568 | 17174242.4242 | 43065160.2637 | 62706775.0871 | 50195321.0516
1023-48R | oh | 2 | 16.6492 | 16.6492 | 14.9381 | 14.9381 | 19.7764 | 59314.53 | 3970.6962 | 113635.5 | 7607.1081 | 114537.5 | 7667.4908 | 284660.3571 | 19056.0355 | 572147.8871 | 38301.3305 | 4481400 | 299998.6307 | 8194580.0062 | 548570.264 | 2803316.296 | 187662.572 | 10997896.3022 | 736232.836 | 15479296.3022 | 1036231.4667 | 5575000 | 373207.5615 | 21626444.1894 | 1447740.3588 | 200030.49 | 13390.6532 | 88946.55 | 5954.3543 | 288977.04 | 19345.0074 | 3628158 | 242880 | 65727.5 | 4400 | 3693885.5 | 247280 | 3982862.54 | 266625.0074 | 1075140 | 71973.1619 | 6474732 | 433438.3751 | 328515 | 21991.7995 | 45540 | 3048.587 | 509373.3333 | 34099.0098 | 40480 | 2709.8551 | 1002800 | 67130.5009 | 9476580.3333 | 634391.2893 | 4077898.4187 | 272987 | 2039195.6875 | 136510 | 238598.3837 | 15972.506 | 109079.8801 | 7302.141 | 4316496.8024 | 288959.506 | 2148275.5676 | 143812.141 | 6780.2398 | 453.89 | 9900 | 662.7363 | 16680.2398 | 1116.6263 | 0 | 0 | 35436201.5649 | 2372207.7804 | 6131138.1076 | 410437.1484 | 14938068.1818 | 39552707.144 | 50374269.7467 | 45683845.2517
1023-89R | oh | 2 | 9.8199 | 9.557 | 3.3587 | 3.6216 | 4.8944 | 17529.38 | 4840.243 | 33583 | 9272.9965 | 33660 | 9294.2579 | 84126.4286 | 23229.1362 | 168898.8086 | 46636.6337 | 1324400 | 365695.6385 | 2421765.9125 | 668702.2287 | 828471.4827 | 228758.9911 | 3250237.3952 | 897461.2199 | 4574637.3952 | 1263156.8584 | 1725000 | 476310.0094 | 6468536.2037 | 1786103.5015 | 59115.54 | 16323.086 | 58315.95 | 16102.3019 | 117431.49 | 32425.3879 | 879612 | 242880 | 15935 | 4400 | 895547 | 247280 | 1012978.49 | 279705.3879 | 170280 | 47018.0107 | 1025464 | 283152.9087 | 52030 | 14366.6144 | 14850 | 4100.4079 | 166100 | 45863.8218 | 13200 | 3644.807 | 327000 | 90291.8105 | 1768924 | 488438.3809 | 916884.7458 | 253171.8156 | 458497.7917 | 126601.2101 | 53649.5988 | 14813.8208 | 24525.7525 | 6772.0936 | 970534.3446 | 267985.6364 | 483023.5442 | 133373.3037 | 1643.8039 | 453.89 | 9900 | 2733.6053 | 11543.8039 | 3187.4953 | 0 | 0 | 9219538.3522 | 2545715.0141 | 1496002.0342 | 413078.6916 | 3621590.9091 | 9788870.3749 | 12841129.2613 | 11284872.4091
1030-1728R | oh | 3 | 2.6777 | 2.6777 | 2.6777 | 2.6777 | 1.1506 | 12433.63 | 4643.4833 | 23820.5 | 8896.0419 | 22440 | 8380.4781 | 59671.0714 | 22284.8534 | 118365.2014 | 44204.8567 | 939400 | 350829.8203 | 1717764.1938 | 641518.952 | 587636.7493 | 219459.7564 | 2305400.9431 | 860978.7084 | 3244800.9431 | 1211808.5288 | 650000 | 242750.0354 | 4013166.1445 | 1498763.4208 | 41930.79 | 15659.5396 | 14137.2 | 5279.7012 | 56067.99 | 20939.2409 | 650348 | 242880 | 11781.6667 | 4400 | 662129.6667 | 247280 | 718197.6567 | 268219.2409 | 102960 | 38451.6056 | 620048 | 231564.1137 | 31460 | 11749.1017 | 16335 | 6100.4951 | 182710 | 68235.1676 | 14520 | 5422.6623 | 359700 | 134334.135 | 1327733 | 495857.2811 | 730964.0542 | 272987 | 365526.2083 | 136510 | 56015.7869 | 20919.745 | 21881.1764 | 8171.779 | 786979.8411 | 293906.745 | 387407.3848 | 144681.779 | 1215.3592 | 453.89 | 9900 | 3697.2698 | 11115.3592 | 4151.1598 | 0 | 0 | 6138994.3448 | 2292678.6066 | 1105605.0414 | 412901.0199 | 2677651.5152 | 2301242.0455 | 8816645.86 | 3406847.0869
1030-1777 | oh | 3 | 6.2943 | 6.2943 | 5.7576 | 5.7576 | 1.6578 | 29147.69 | 5062.4935 | 55841.5 | 9698.7868 | 40205 | 6982.9737 | 139884.6429 | 24295.7538 | 265078.8329 | 46040.0078 | 2202200 | 382487.3684 | 4026889.8312 | 699407.1812 | 1377574.6747 | 239262.9698 | 5404464.5059 | 938670.151 | 7606664.5059 | 1321157.5194 | 1275000 | 221447.3684 | 9146743.3388 | 1588644.8957 | 98296.77 | 17072.5969 | 32986.8 | 5729.2863 | 131283.57 | 22801.8832 | 1398400 | 242880 | 25333.3333 | 4400 | 1423733.3333 | 247280 | 1555016.9033 | 270081.8832 | 266310 | 46253.8421 | 1603778 | 278550.9158 | 81372.5 | 14133.1184 | 38115 | 6619.9737 | 426323.3333 | 74045.6316 | 33880 | 5884.4211 | 839300 | 145773.1579 | 3289078.8333 | 571261.0605 | 1571743.3333 | 272987 | 785966.6667 | 136510 | 120175.57 | 20872.599 | 46997.64 | 8162.748 | 1691918.9033 | 293859.599 | 832964.3067 | 144672.748 | 2613.3061 | 453.89 | 9900 | 1719.4737 | 12513.3061 | 2173.3637 | 0 | 0 | 14140254.3815 | 2455938.9189 | 2387981.21 | 414754.6312 | 5757575.7576 | 3315693.1818 | 19897830.1391 | 5703674.3918
1030-18R | oh | 3 | 3.5042 | 3.5042 | 3.4777 | 3.4777 | 4.5033 | 14879.59 | 4278.6317 | 28506.5 | 8197.0548 | 14960 | 4301.7536 | 71409.6429 | 20533.8696 | 129755.7329 | 37311.3097 | 1124200 | 323264.1324 | 2055685.0188 | 591112.9996 | 703237.4213 | 202216.1848 | 2758922.4401 | 793329.1844 | 3883122.4401 | 1116593.3168 | 375000 | 107831.3909 | 4387878.1729 | 1261736.0175 | 50179.47 | 14429.1255 | 15315.3 | 4403.9203 | 65494.77 | 18833.0457 | 844652 | 242880 | 15301.6667 | 4400 | 859953.6667 | 247280 | 925448.4367 | 266113.0457 | 204930 | 58927.6985 | 1234134 | 354875.6955 | 62617.5 | 18005.6857 | 18315 | 5266.4851 | 204856.6667 | 58906.6115 | 16280 | 4681.3201 | 403300 | 115969.0666 | 2144433.1667 | 616632.5629 | 949353.6542 | 272987 | 474734.2083 | 136510 | 72671.4404 | 20896.7 | 28405.6697 | 8168.061 | 1022025.0946 | 293883.7 | 503139.878 | 144678.061 | 1578.4712 | 453.89 | 9900 | 2846.7487 | 11478.4712 | 3300.6387 | 0 | 0 | 7565814.9054 | 2175552.9191 | 1428588.3147 | 410791.1067 | 3477651.5152 | 9006680.4468 | 11043466.4206 | 10435268.7615
1030-20R | oh | 3 | 16.2256 | 16.2256 | 15.7169 | 15.7169 | 2.3083 | 66040.92 | 4201.9167 | 126522 | 8050.0833 | 39270 | 2498.5913 | 316941.4286 | 20165.7015 | 548774.3486 | 34916.2928 | 4989600 | 317468.0725 | 9123862.275 | 580514.4642 | 3121218.144 | 198590.4899 | 12245080.419 | 779104.9541 | 17234680.419 | 1096573.0266 | 1025000 | 65216.6054 | 18808454.7676 | 1196705.9248 | 222714.36 | 14170.4142 | 59494.05 | 3785.3658 | 282208.41 | 17955.78 | 3817310 | 242880 | 69154.1667 | 4400 | 3886464.1667 | 247280 | 4168672.5767 | 265235.78 | 1443420 | 91838.9781 | 8692596 | 553074.735 | 441045 | 28061.91 | 65340 | 4157.32 | 730840 | 46500.394 | 58080 | 3695.3956 | 1438800 | 91545.0262 | 12870121 | 818873.7589 | 4290497.3854 | 272987 | 2145508.0208 | 136510 | 327195.8513 | 20818.149 | 128157.0203 | 8154.113 | 4617693.2367 | 293805.149 | 2273665.0412 | 144664.113 | 7133.7238 | 453.89 | 9900 | 629.897 | 17033.7238 | 1083.787 | 0 | 0 | 36313302.7281 | 2310468.6197 | 6442337.6178 | 409899.893 | 15716856.0606 | 4616574.8232 | 52030158.7887 | 11058912.441
1030-42R | oh | 3 | 18.5081 | 18.5081 | 16.74 | 16.74 | 4.2328 | 76843.91 | 4590.4471 | 147218.5 | 8794.4345 | 93967.5 | 5613.364 | 368786.7857 | 22030.3238 | 686816.6957 | 41028.5693 | 5805800 | 346822.7681 | 10616345.9187 | 634191.7528 | 3631787.7787 | 216953.1659 | 14248133.6974 | 851144.9186 | 20053933.6974 | 1197967.6867 | 3700000 | 221027.9792 | 24440750.3931 | 1460024.2352 | 259146.03 | 15480.682 | 88946.55 | 5313.426 | 348092.58 | 20794.108 | 4065802 | 242880 | 73655.8333 | 4400 | 4139457.8333 | 247280 | 4487550.4133 | 268074.108 | 1493910 | 89242.1374 | 8996658 | 537435.9831 | 456472.5 | 27268.4309 | 83160 | 4967.7532 | 930160 | 55565.2392 | 73920 | 4415.7806 | 1831200 | 109390.9285 | 13865480.5 | 828286.253 | 4569792.0396 | 272987 | 2285172.2292 | 136510 | 346134.5404 | 20677.14 | 136082.4666 | 8129.198 | 4915926.58 | 293664.14 | 2421254.6958 | 144639.198 | 7598.1014 | 453.89 | 9900 | 591.3992 | 17498.1014 | 1045.2892 | 0 | 0 | 43239655.5745 | 2583019.9173 | 6908805.1091 | 412713.306 | 16739962.1212 | 8465604.809 | 59979617.6957 | 15374409.9181
1030-989R | oh | 3 | 20.4036 | 20.4036 | 19.582 | 19.582 | 1.9348 | 76028.59 | 3882.5738 | 145656.5 | 7438.2823 | 88825 | 4536.0518 | 364873.9286 | 18633.1216 | 675384.0186 | 34490.0295 | 5744200 | 293340.7097 | 10503705.6438 | 536395.7502 | 3593254.2213 | 183497.7444 | 14096959.8651 | 719893.4946 | 19841159.8651 | 1013234.2043 | 2500000 | 127668.2174 | 23016543.8837 | 1175392.4512 | 256396.47 | 13093.4721 | 68918.85 | 3519.4987 | 325315.32 | 16612.9708 | 4756078 | 242880 | 86160.8333 | 4400 | 4842238.8333 | 247280 | 5167554.1533 | 263892.9708 | 1219680 | 62285.7486 | 7345184 | 375098.6191 | 372680 | 19031.7565 | 70785 | 3614.7979 | 791743.3333 | 40432.184 | 62920 | 3213.1537 | 1558700 | 79598.5802 | 11421692.3333 | 583274.8399 | 5345633.5021 | 272987 | 2673139.8542 | 136510 | 406893.243 | 20778.934 | 159541.2149 | 8147.337 | 5752526.7451 | 293765.934 | 2832681.069 | 144657.337 | 8888.0774 | 453.89 | 9900 | 505.5661 | 18788.0774 | 959.4561 | 0 | 0 | 40209551.0395 | 2053392.6812 | 8000235.2224 | 408550.3078 | 19582007.5758 | 3869663.6364 | 59791558.6153 | 11869898.8587
1039-13 | oh | 2 | 26.6966 | 26.6866 | 13.3375 | 13.3375 | 16.4646 | 69506.03 | 5211.3237 | 133160.5 | 9983.9175 | 135575 | 10164.9485 | 333571.0714 | 25010.0147 | 671812.6014 | 50370.2044 | 5251400 | 393731.9588 | 9602583.4437 | 719968.768 | 3284985.7627 | 246296.9644 | 12887569.2064 | 966265.7324 | 18138969.2064 | 1359997.6912 | 5850000 | 438612.9335 | 24660781.8078 | 1848980.8291 | 234399.99 | 17574.5072 | 173769.75 | 13028.6598 | 408169.74 | 30603.167 | 3239412 | 242880 | 58685 | 4400 | 3298097 | 247280 | 3706266.74 | 277883.167 | 1685970 | 126408.2474 | 10153286 | 761258.5567 | 515157.5 | 38624.7423 | 43560 | 3265.9794 | 487226.6667 | 36530.5842 | 38720 | 2903.0928 | 959200 | 71917.5258 | 13883120.1667 | 1040908.7285 | 3640964.1125 | 272987 | 1820702.125 | 136510 | 214137.6038 | 16055.303 | 97597.5564 | 7317.53 | 3855101.7163 | 289042.303 | 1918299.6814 | 143827.53 | 6053.7579 | 453.89 | 9900 | 742.268 | 15953.7579 | 1196.158 | 0 | 0 | 42414957.4486 | 3180128.0186 | 5624566.4214 | 421710.697 | 13337500 | 32929108.6459 | 55752457.4486 | 38553675.0673
1090-1734 | oh | 3 | 7.9937 | 7.9937 | 2.0241 | 2.0241 | 2.6405 | 7949.37 | 3927.4514 | 15229.5 | 7524.2594 | 11220 | 5543.333 | 38150.3571 | 18848.4968 | 72549.2271 | 35843.5407 | 600600 | 296731.3559 | 1098242.6812 | 542595.804 | 375702.184 | 185618.7453 | 1473944.8653 | 728214.5493 | 2074544.8653 | 1024945.9052 | 500000 | 247029.1008 | 2647094.0924 | 1307818.5466 | 26808.21 | 13244.816 | 34164.9 | 16879.4491 | 60973.11 | 30124.2651 | 491602 | 242880 | 8905.8333 | 4400 | 500507.8333 | 247280 | 561480.9433 | 277404.2651 | 18810 | 9293.2348 | 113278 | 55965.925 | 5747.5 | 2839.5995 | 6930 | 3423.8233 | 77513.3333 | 38296.0981 | 6160 | 3043.3985 | 152600 | 75393.2816 | 381038.8333 | 188255.3607 | 552540.1646 | 272987 | 276303.4792 | 136510 | 28384.8724 | 14023.779 | 14084.4196 | 6958.523 | 580925.037 | 287010.779 | 290387.8987 | 143468.523 | 918.6974 | 453.89 | 9900 | 4891.1762 | 10818.6974 | 5345.0662 | 0 | 0 | 3619876.6601 | 1788429.7525 | 851868.8421 | 420872.7881 | 2024053.0303 | 5280933.2522 | 5643929.6904 | 6132802.0943
1090-636R | oh | 3 | 8.3888 | 8.3888 | 8.0809 | 8.0809 | 11.5889 | 24051.94 | 2976.4043 | 46079 | 5702.2317 | 22907.5 | 2834.781 | 115429.2857 | 14284.2625 | 208467.7257 | 25797.6795 | 1817200 | 224876.7432 | 3322888.1125 | 411204.1914 | 1136739.9413 | 140670.4688 | 4459628.0538 | 551874.6601 | 6276828.0538 | 776751.4033 | 950000 | 117561.5816 | 7435295.7795 | 920110.6644 | 81112.02 | 10037.5341 | 11781 | 1457.8874 | 92893.02 | 11495.4214 | 1962682 | 242880 | 35555.8333 | 4400 | 1998237.8333 | 247280 | 2091130.8533 | 258775.4214 | 185130 | 22909.6585 | 1114894 | 137967.0546 | 56567.5 | 7000.1734 | 13860 | 1715.1616 | 155026.6667 | 19184.4001 | 12320 | 1524.5881 | 305200 | 37768.2049 | 1842998.1667 | 228069.2413 | 2205972.7896 | 272987 | 1103119.7292 | 136510 | 200730.9015 | 24840.255 | 71618.4262 | 8862.711 | 2406703.6911 | 297827.255 | 1174738.1553 | 145372.711 | 3667.8266 | 453.89 | 9900 | 1225.1154 | 13567.8266 | 1679.0054 | 0 | 0 | 11698565.464 | 1447686.1661 | 3265869.0087 | 404148.1324 | 8080871.2121 | 23177742.4109 | 19779436.6761 | 26443611.4196
1090-639R | oh | 3 | 4.3254 | 4.3254 | 4.261 | 4.261 | 6.3665 | 14879.59 | 3492.0542 | 28506.5 | 6690.12 | 7012.5 | 1645.7463 | 71409.6429 | 16758.9525 | 121808.2329 | 28586.873 | 1124200 | 263835.7187 | 2055685.0188 | 482443.6349 | 703237.4213 | 165041.0519 | 2758922.4401 | 647484.6868 | 3883122.4401 | 911320.4055 | 250000 | 58671.8819 | 4254930.6729 | 998579.1605 | 50179.47 | 11776.4958 | 5301.45 | 1244.1842 | 55480.92 | 13020.68 | 1034908 | 242880 | 18748.3333 | 4400 | 1053656.3333 | 247280 | 1109137.2533 | 260300.68 | 0 | 0 | 0 | 0 | 0 | 0 | 4950 | 1161.7033 | 55366.6667 | 12993.8661 | 4400 | 1032.6251 | 109000 | 25580.9405 | 173716.6667 | 40769.135 | 1163193.4708 | 272987 | 581667.0417 | 136510 | 105586.4418 | 24779.821 | 37718.5532 | 8852.074 | 1268779.9127 | 297766.821 | 619385.5949 | 145362.074 | 1934.0184 | 453.89 | 9900 | 2323.4065 | 11834.0184 | 2777.2965 | 0 | 0 | 5709261.2707 | 1339892.4131 | 1728522.8482 | 405662.754 | 4260984.8485 | 12732978.1005 | 9970246.1192 | 14461500.9487
1090-73F | oh | 3 | 14.5956 | 14.5956 | 8.9759 | 8.9759 | 11.6074 | 44027.28 | 4905.029 | 84348 | 9397.1143 | 82747.5 | 9218.8045 | 211294.2857 | 23540.055 | 422417.0657 | 47061.0028 | 3326400 | 370590.4247 | 6082574.85 | 677652.7168 | 2080812.096 | 231820.899 | 8163386.946 | 909473.6158 | 11489786.946 | 1280064.0406 | 4125000 | 459561.5386 | 16037204.0117 | 1786686.582 | 148476.24 | 16541.5683 | 78343.65 | 8728.1766 | 226819.89 | 25269.7449 | 2180078 | 242880 | 39494.1667 | 4400 | 2219572.1667 | 247280 | 2446392.0567 | 272549.7449 | 529650 | 59007.7016 | 3189670 | 355357.4916 | 161837.5 | 18030.131 | 47025 | 5239.0015 | 525983.3333 | 58599.2024 | 41800 | 4656.8903 | 1035500 | 115363.8723 | 5531465.8333 | 616254.2907 | 2450316.8354 | 272987 | 1225306.5208 | 136510 | 125878.6713 | 14023.999 | 62460.3208 | 6958.633 | 2576195.5067 | 287010.999 | 1287766.8416 | 143468.633 | 4074.0926 | 453.89 | 9900 | 1102.9477 | 13974.0926 | 1556.8377 | 0 | 0 | 24158839.4444 | 2691508.7094 | 3734158.8983 | 416018.3779 | 8975946.9697 | 23214853.8269 | 33134786.4141 | 26949012.7252
1090-74F | oh | 3 | 10.4066 | 10.4066 | 8.54 | 8.54 | 9.7826 | 45861.75 | 5370.2522 | 87862.5 | 10288.3946 | 90695 | 10620.0705 | 220098.2143 | 25772.7389 | 444517.4643 | 52051.4562 | 3465000 | 405739.5046 | 6336015.4688 | 741925.4768 | 2167512.6 | 253808.2218 | 8503528.0687 | 995733.6986 | 11968528.0687 | 1401473.2031 | 4625000 | 541571.4888 | 17038045.533 | 1995096.1481 | 154662.75 | 18110.4726 | 75398.4 | 8828.8916 | 230061.15 | 26939.3642 | 2074186 | 242880 | 37575.8333 | 4400 | 2111761.8333 | 247280 | 2341822.9833 | 274219.3642 | 605880 | 70946.4505 | 3648744 | 427255.2909 | 185130 | 21678.0821 | 38610 | 4521.0973 | 431860 | 50569.3109 | 34320 | 4018.7532 | 850200 | 99555.4767 | 5794744 | 678544.4616 | 2331298.6396 | 272987 | 1165790.2292 | 136510 | 119763.3869 | 14023.878 | 59426.4622 | 6958.633 | 2451062.0265 | 287010.878 | 1225216.6914 | 143468.633 | 3876.2034 | 453.89 | 9900 | 1159.2557 | 13776.2034 | 1613.1457 | 0 | 0 | 25297627.7629 | 2962264.6335 | 3567039.6747 | 417687.9972 | 8539962.1212 | 19565113.3593 | 33837589.8842 | 23132153.034
1094-35F | oh | 2 | 15.2752 | 15.2752 | 5.1366 | 5.1366 | 6.1219 | 28536.2 | 5555.5155 | 54670 | 10643.3244 | 57970 | 11285.7785 | 136950 | 26661.8488 | 278126.2 | 54146.4672 | 2156000 | 419736.7354 | 3942409.625 | 767520.4756 | 1348674.5067 | 262564.1162 | 5291084.1317 | 1030084.5918 | 7447084.1317 | 1449821.3272 | 1875000 | 365030.788 | 9600210.3317 | 1868998.5823 | 96234.6 | 18735.249 | 64206.45 | 12499.9099 | 160441.05 | 31235.1589 | 1247566 | 242880 | 22600.8333 | 4400 | 1270166.8333 | 247280 | 1430607.8833 | 278515.1589 | 343530 | 66879.4808 | 2068814 | 402763.0958 | 104967.5 | 20435.3969 | 15345 | 2987.412 | 171636.6667 | 33414.7561 | 13640 | 2655.4773 | 337900 | 65783.4151 | 3055833.1667 | 594919.034 | 1402212.2021 | 272987 | 701190.8542 | 136510 |  |  |  |  | 1402212.2021 | 272987 | 701190.8542 | 136510 | 2331.4301 | 453.89 | 9900 | 1927.3626 | 12231.4301 | 2381.2526 | 0 | 0 | 14070487.1305 | 2739285.8688 | 2131798.7375 | 415025.1589 | 5136553.0303 | 12243858.838 | 19207040.1608 | 14375657.5755
1094-7 | oh | 2 | 22.333 | 11.7572 | 1.1278 | 1.703 | 2.3145 | 10191.5 | 5984.3327 | 19525 | 11464.8577 | 21972.5 | 12902.0018 | 33259.2857 | 19529.4738 | 84948.2857 | 49880.666 | 770000 | 452135.2313 | 1408003.4375 | 826763.5843 | 481669.4667 | 282830.8256 | 1889672.9042 | 1109594.4099 | 2659672.9042 | 1561729.6412 | 775000 | 455071.1744 | 3519621.1899 | 2066681.4816 | 34369.5 | 20181.379 | 96604.2 | 56724.8861 | 130973.7 | 76906.2651 | 413632 | 242880 | 7493.3333 | 4400 | 421125.3333 | 247280 | 552099.0333 | 324186.2651 | 164340 | 96498.5765 | 989692 | 581135.8719 | 50215 | 29485.6762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1204247 | 707120.1246 | 307885.9062 | 180787.098 | 153961.5625 | 90404.4762 |  |  |  |  | 307885.9062 | 180787.098 | 153961.5625 | 90404.4762 | 772.9884 | 453.89 | 9900 | 5813.1673 | 10672.9884 | 6267.0573 | 0 | 0 | 5042427.0846 | 2960855.7614 | 706060.5958 | 414590.7413 | 1703030.303 | 4628903.7757 | 6745457.3876 | 5334964.3715
1100-1172R | oh | 2 | 2.5523 | 2.5523 | 2.2354 | 2.2354 | 3.2012 | 6930.22 | 3100.1916 | 13277 | 5939.3849 | 9350 | 4182.6654 | 33259.2857 | 14878.3384 | 62816.5057 | 28100.5804 | 523600 | 234229.2637 | 957442.3375 | 428305.9851 | 327535.2373 | 146520.889 | 1284977.5748 | 574826.8741 | 1808577.5748 | 809056.1379 | 300000 | 134203.1687 | 2171394.0805 | 971359.8869 | 23371.26 | 10454.9905 | 4712.4 | 2108.0634 | 28083.66 | 12563.0539 | 542938 | 242880 | 9835.8333 | 4400 | 552773.8333 | 247280 | 580857.4933 | 259843.0539 | 47520 | 21257.7819 | 286176 | 128019.0867 | 14520 | 6495.4334 | 2475 | 1107.1761 | 27683.3333 | 12383.9702 | 2200 | 984.1566 | 54500 | 24380.2423 | 435074.3333 | 194627.8472 | 610239.6896 | 272987 | 305156.7292 | 136510 | 35873.03 | 16047.581 | 16354.4581 | 7316.067 | 646112.7196 | 289034.581 | 321511.1873 | 143826.067 | 1014.6333 | 453.89 | 9900 | 4428.7046 | 10914.6333 | 4882.5946 | 0 | 0 | 3263495.7668 | 1459904.9096 | 902368.6806 | 403669.1209 | 2235416.6667 | 6402304.7248 | 5498912.4334 | 7304673.4054
1105-1479 | oh | 2 | 3.4843 | 3.4843 | 3.4339 | 3.4339 | 4.7597 | 10599.16 | 3086.6232 | 20306 | 5913.3903 | 2805 | 816.8551 | 50867.1429 | 14813.2212 | 84577.3029 | 24630.0899 | 800800 | 233204.1255 | 1464323.575 | 426431.4421 | 500936.2453 | 145879.6192 | 1965259.8203 | 572311.0612 | 2766059.8203 | 805515.1868 | 50000 | 14560.6971 | 2900637.1232 | 844705.9738 | 35744.28 | 10409.2327 | 2945.25 | 857.6979 | 38689.53 | 11266.9306 | 834026 | 242880 | 15109.1667 | 4400 | 849135.1667 | 247280 | 887824.6967 | 258546.9306 | 111870 | 32578.1038 | 673706 | 196192.5807 | 34182.5 | 9954.4206 | 3465 | 1009.0563 | 38756.6667 | 11286.4817 | 3080 | 896.9389 | 76300 | 22219.6238 | 941360.1667 | 274137.2059 | 937410.4729 | 272987 | 468761.8958 | 136510 | 57513.8739 | 16748.842 | 25543.6705 | 7438.673 | 994924.3468 | 289735.842 | 494305.5663 | 143948.673 | 1558.6136 | 453.89 | 9900 | 2883.018 | 11458.6136 | 3336.908 | 0 | 0 | 4848380.2503 | 1411915.9297 | 1382130.263 | 402495.6036 | 3433901.5152 | 9519317.9577 | 8282281.7654 | 10901448.2207
1138-6R | oh | 2 | 15.0831 | 14.7426 | 13.425 | 13.7655 | 16.4147 | 83366.47 | 6056.1757 | 159714.5 | 11602.4953 | 168767.5 | 12260.1524 | 389329.2857 | 28282.9123 | 801177.7557 | 58201.7356 | 6298600 | 457563.1931 | 11517468.1188 | 836689.0243 | 3940056.2373 | 286226.2587 | 15457524.3561 | 1122915.283 | 21756124.3561 | 1580478.4761 | 8200000 | 595690.8175 | 30757302.1118 | 2234371.0293 | 281142.51 | 20423.66 | 138426.75 | 10056.0419 | 419569.26 | 30479.7019 | 3343372 | 242880 | 60568.3333 | 4400 | 3403940.3333 | 247280 | 3823509.5933 | 277759.7019 | 1564200 | 113631.6557 | 9419960 | 684315.0821 | 477950 | 34720.7837 | 61875 | 4494.9231 | 692083.3333 | 50276.5472 | 55000 | 3995.4872 | 1362500 | 98979.1145 | 13633568.3333 | 990413.5935 | 3664850.475 | 266233.8751 | 1832646.75 | 133133.0294 | 229111.2648 | 16643.8386 | 100617.7705 | 7309.4002 | 3893961.7398 | 282877.7137 | 1933264.5205 | 140442.4296 | 6248.0365 | 453.89 | 9900 | 719.1877 | 16148.0365 | 1173.0777 | 0 | 0 | 48300980.2215 | 3508835.4141 | 5756774.1139 | 418202.1315 | 13765530.303 | 32829398.3481 | 62066510.5245 | 38586172.4619
1162-324R | oh | 2 | 5.1752 | 5.1752 | 2.7439 | 2.7439 | 3.2888 | 11618.31 | 4234.1715 | 22258.5 | 8111.8774 | 2805 | 1022.2529 | 55758.2143 | 20320.4978 | 92440.0243 | 33688.7996 | 877800 | 319905.0248 | 1605123.9187 | 584970.6164 | 549103.192 | 200114.9126 | 2154227.1107 | 785085.529 | 3032027.1107 | 1104990.5539 | 100000 | 36443.9536 | 3224467.135 | 1175123.3071 | 39181.23 | 14279.1893 | 14726.25 | 5366.8277 | 53907.48 | 19646.017 | 666448 | 242880 | 12073.3333 | 4400 | 678521.3333 | 247280 | 732428.8133 | 266926.017 | 9900 | 3607.9514 | 59620 | 21727.8851 | 3025 | 1102.4296 | 7920 | 2886.3611 | 88586.6667 | 32284.4837 | 7040 | 2565.6543 | 174400 | 63558.2551 | 350491.6667 | 127733.0204 | 749059.7833 | 272987 | 374575.1667 | 136510 | 42985.6847 | 15665.683 | 19886.7419 | 7247.515 | 792045.468 | 288652.683 | 394461.9086 | 143757.515 | 1245.4467 | 453.89 | 9900 | 3607.9514 | 11145.4467 | 4061.8414 | 0 | 0 | 4378149.7164 | 1595570.8519 | 1126890.7219 | 410683.532 | 2743939.3939 | 6577696.4658 | 7122089.1103 | 7704587.1878
1162-329R | oh | 2 | 3.5167 | 3.5167 | 3.3758 | 3.3758 | 5.0725 | 9580.01 | 2837.8845 | 18353.5 | 5436.8537 | 14960 | 4431.5978 | 45976.0714 | 13619.4826 | 88869.5814 | 26325.8186 | 723800 | 214411.1311 | 1323523.2312 | 392067.0254 | 452769.2987 | 134123.7599 | 1776292.5299 | 526190.7853 | 2500092.5299 | 740601.9164 | 775000 | 229578.0969 | 3363962.1113 | 996505.8319 | 32307.33 | 9570.394 | 7657.65 | 2268.4241 | 39964.98 | 11838.8181 | 819904 | 242880 | 14853.3333 | 4400 | 834757.3333 | 247280 | 874722.3133 | 259118.8181 | 22770 | 6745.1526 | 137126 | 40620.8079 | 6957.5 | 2061.0189 | 3960 | 1173.07 | 44293.3333 | 13121.0054 | 3520 | 1042.7289 | 87200 | 25831.2388 | 305826.8333 | 90595.0224 | 921537.9333 | 272987 | 460824.6667 | 136510 | 52890.7148 | 15667.806 | 24467.4504 | 7247.988 | 974428.6481 | 288654.806 | 485292.1171 | 143757.988 | 1532.2226 | 453.89 | 9900 | 2932.675 | 11432.2226 | 3386.565 | 0 | 0 | 4655649.8154 | 1379142.2254 | 1360014.4304 | 402876.8061 | 3375757.5758 | 10144926.354 | 8031407.3912 | 11504940.7844
1162-363 | oh | 2 | 2.0172 | 2.0172 | 1.6146 | 1.6146 | 2.4144 | 7134.05 | 4418.5084 | 13667.5 | 8465.0323 | 8415 | 5211.871 | 34237.5 | 21205.1613 | 63454.05 | 39300.5729 | 539000 | 333832.2581 | 985602.4062 | 610437.6194 | 337168.6267 | 208827.0204 | 1322771.0329 | 819264.6397 | 1861771.0329 | 1153096.8978 | 450000 | 278709.6774 | 2375225.0829 | 1471107.1481 | 24058.65 | 14900.8413 | 4712.4 | 2918.6477 | 28771.05 | 17819.489 | 392150 | 242880 | 7104.1667 | 4400 | 399254.1667 | 247280 | 428025.2167 | 265099.489 | 9900 | 6131.6129 | 59620 | 36925.9355 | 3025 | 1873.5484 | 3960 | 2452.6452 | 44293.3333 | 27433.2903 | 3520 | 2180.129 | 87200 | 54007.7419 | 211518.3333 | 131004.9032 | 440760.2604 | 272987 | 220406.7708 | 136510 | 25302.0402 | 15670.941 | 11703.3509 | 7248.527 | 466062.3006 | 288657.941 | 232110.1217 | 143758.527 | 732.8432 | 453.89 | 9900 | 6131.6129 | 10632.8432 | 6585.5029 | 0 | 0 | 3063438.5601 | 1897355.4953 | 660135.3384 | 408858.016 | 1614583.3333 | 4828815.5762 | 4678021.8934 | 5488950.9146
1166-15R | oh | 3 | 6.2937 | 6.2937 | 5.0748 | 5.0748 | 6.6961 | 20179.17 | 3976.3395 | 38659.5 | 7617.9198 | 35997.5 | 7093.3682 | 96843.2143 | 19083.1189 | 191679.3843 | 37770.7464 | 1524600 | 300425.0047 | 2787846.8062 | 549349.9211 | 953705.544 | 187929.288 | 3741552.3503 | 737279.2092 | 5266152.3503 | 1037704.2138 | 1975000 | 389177.0853 | 7432831.7345 | 1464652.0455 | 68051.61 | 13409.6847 | 21794.85 | 4294.712 | 89846.46 | 17704.3967 | 1232570 | 242880 | 22329.1667 | 4400 | 1254899.1667 | 247280 | 1344745.6267 | 264984.3967 | 147510 | 29067.0946 | 888338 | 175048.5031 | 45072.5 | 8881.6122 | 16335 | 3218.8393 | 182710 | 36003.3141 | 14520 | 2861.1905 | 359700 | 70879.4924 | 1654185.5 | 325960.0463 | 1385357.3229 | 272987 | 692762.3958 | 136510 | 97958.9473 | 19302.976 | 40024.6963 | 7886.934 | 1483316.2702 | 292289.976 | 732787.0921 | 144396.934 | 2303.4058 | 453.89 | 9900 | 1950.8117 | 12203.4058 | 2404.7017 | 0 | 0 | 10582536.9106 | 2085306.7695 | 2077532.7188 | 409381.3307 | 5074810.6061 | 13392255.827 | 15657347.5166 | 15469788.5458
1166-18R | oh | 3 | 7.661 | 7.661 | 7.5917 | 7.5917 | 11.3006 | 19771.51 | 2604.3701 | 37878.5 | 4989.4841 | 21505 | 2832.7113 | 94886.7857 | 12498.8082 | 174041.7957 | 22925.3737 | 1493800 | 196768.3864 | 2731526.6688 | 359805.9278 | 934438.7653 | 123087.4334 | 3665965.4341 | 482893.3612 | 5159765.4341 | 679661.7476 | 1050000 | 138309.5499 | 6383807.2298 | 840896.6713 | 66676.83 | 8782.8975 | 7657.65 | 1008.6915 | 74334.48 | 9791.589 | 1843864 | 242880 | 33403.3333 | 4400 | 1877267.3333 | 247280 | 1951601.8133 | 257071.589 | 224730 | 29602.1954 | 1353374 | 178270.9989 | 68667.5 | 9045.1153 | 9900 | 1304.0615 | 110733.3333 | 14586.169 | 8800 | 1159.1658 | 218000 | 28715.697 | 1994204.8333 | 262683.4029 | 2072426.3083 | 272987 | 1036338.4167 | 136510 | 146576.5824 | 19307.563 | 59883.6588 | 7888.078 | 2219002.8908 | 292294.563 | 1096222.0755 | 144398.078 | 3445.7816 | 453.89 | 9900 | 1304.0615 | 13345.7816 | 1757.9515 | 0 | 0 | 10610360.7355 | 1397632.5886 | 3047823.8888 | 401469.667 | 7591666.6667 | 22601268.7812 | 18202027.4022 | 25649092.67
1166-342R | oh | 3 | 12.329 | 12.329 | 11.5801 | 11.5801 | 16.8158 | 38320.04 | 3309.1247 | 73414 | 6339.6614 | 56100 | 4844.512 | 183904.2857 | 15881.0433 | 351738.3257 | 30374.3415 | 2895200 | 250014.8177 | 5294092.925 | 457171.0685 | 1811077.1947 | 156395.4596 | 7105170.1197 | 613566.5282 | 10000370.1197 | 863581.3459 | 2700000 | 233158.3337 | 13052108.4454 | 1127114.0211 | 129229.32 | 11159.59 | 41822.55 | 3611.5837 | 171051.87 | 14771.1737 | 2812578 | 242880 | 50952.5 | 4400 | 2863530.5 | 247280 | 3034582.37 | 262051.1737 | 464310 | 40095.4615 | 2796178 | 241463.779 | 141872.5 | 12251.391 | 47025 | 4060.841 | 525983.3333 | 45421.2584 | 41800 | 3609.6364 | 1035500 | 89420.5387 | 5052668.8333 | 436322.906 | 3161220.4812 | 272987 | 1580801.3125 | 136510 | 223195.7703 | 19274.057 | 91274.6525 | 7882.017 | 3384416.2515 | 292261.057 | 1672075.965 | 144392.017 | 5256.0978 | 453.89 | 9900 | 854.9139 | 15156.0978 | 1308.8039 | 0 | 0 | 21504349.628 | 1857006.788 | 4706658.335 | 406443.1907 | 11580113.6364 | 33631561.0373 | 33084463.2644 | 38338219.3723
1201-282F | oh | 2 | 7.9419 | 2.0657 | 1.5301 | 1.7013 | 2.6053 | 6114.9 | 3594.197 | 11715 | 6885.8065 | 13090 | 7693.9998 | 19564.2857 | 11499.4354 | 50484.1857 | 29673.4388 | 462000 | 271552.9333 | 844802.0625 | 496555.1475 | 289001.68 | 169868.515 | 1133803.7425 | 666423.6625 | 1595803.7425 | 937976.5958 | 425000 | 249805.1876 | 2071287.9282 | 1217455.2222 | 20621.7 | 12120.9591 | 30041.55 | 17657.7295 | 50663.25 | 29778.6886 | 413218 | 242880 | 7485.8333 | 4400 | 420703.8333 | 247280 | 471367.0833 | 277058.6886 | 8910 | 5237.0923 | 53658 | 31538.9335 | 2722.5 | 1600.2226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65290.5 | 38376.2485 | 417701.1312 | 245515.081 | 208875.8125 | 122772.3801 |  |  |  |  | 417701.1312 | 245515.081 | 208875.8125 | 122772.3801 | 772.2147 | 453.89 | 9900 | 5818.9914 | 10672.2147 | 6272.8814 | 0 | 0 | 2564951.7742 | 1507619.4331 | 680242.8958 | 399831.0687 | 1701325.7576 | 5210675.7672 | 4266277.5318 | 5890918.6631
1215-12R | oh | 3 | 8.7831 | 8.7831 | 8.3178 | 8.3178 | 7.2899 | 27720.88 | 3332.7166 | 53108 | 6384.8591 | 26180 | 3147.4657 | 133037.1429 | 15994.2646 | 240046.0229 | 28859.306 | 2094400 | 251797.2585 | 3829769.35 | 460430.3968 | 1310140.9493 | 157510.4561 | 5139910.2993 | 617940.853 | 7234310.2993 | 869738.1115 | 575000 | 69128.831 | 8049356.3222 | 967726.2485 | 93485.04 | 11239.1505 | 20616.75 | 2478.6293 | 114101.79 | 13717.7798 | 2020228 | 242880 | 36598.3333 | 4400 | 2056826.3333 | 247280 | 2170928.1233 | 260997.7798 | 84150 | 10116.8541 | 506770 | 60925.9438 | 25712.5 | 3091.261 | 24750 | 2975.5453 | 276833.3333 | 33282.0256 | 22000 | 2644.9292 | 545000 | 65522.1094 | 1485215.8333 | 178558.6684 | 2270652.0958 | 272987 | 1135463.2917 | 136510 | 284621.304 | 34218.327 | 87468.2782 | 10515.791 | 2555273.3998 | 307205.327 | 1222931.5699 | 147025.791 | 3775.3676 | 453.89 | 9900 | 1190.2181 | 13675.3676 | 1644.1081 | 0 | 0 | 12103520.923 | 1455134.3521 | 3393859.6932 | 408023.5708 | 8317803.0303 | 14579802.7554 | 20421323.9533 | 17973662.4486
1215-28R | oh | 3 | 3.4398 | 3.4398 | 3.06 | 3.06 | 2.961 | 11414.48 | 3730.176 | 21868 | 7146.3168 | 7947.5 | 2597.1901 | 54780 | 17901.7392 | 96009.98 | 31375.4221 | 862400 | 281826.5767 | 1576963.85 | 515341.2841 | 539469.8027 | 176295.1388 | 2116433.6527 | 691636.423 | 2978833.6527 | 973462.9997 | 375000 | 122547.5026 | 3449843.6327 | 1127385.9244 | 38493.84 | 12579.5306 | 11191.95 | 3657.4547 | 49685.79 | 16236.9853 | 743222 | 242880 | 13464.1667 | 4400 | 756686.1667 | 247280 | 806371.9567 | 263516.9853 | 53460 | 17470.372 | 321948 | 105210.4623 | 16335 | 5338.1692 | 8910 | 2911.7287 | 99660 | 32568.2243 | 7920 | 2588.2033 | 196200 | 64116.8534 | 704433 | 230204.0131 | 835350.5604 | 272987 | 417725.7708 | 136510 | 104587.8963 | 34178.628 | 32157.2098 | 10508.762 | 939938.4567 | 307165.628 | 449882.9806 | 147018.762 | 1388.9206 | 453.89 | 9900 | 3235.2541 | 11288.9206 | 3689.1441 | 0 | 0 | 5105504.01 | 1668444.7096 | 1256254.9373 | 410535.7473 | 3060037.8788 | 5922096.5289 | 8165541.8888 | 7178351.4662
1215-32R | oh | 3 | 12.2886 | 12.2886 | 12.1911 | 12.1911 | 3.1959 | 41988.98 | 3444.2327 | 80443 | 6598.503 | 70125 | 5752.1478 | 201512.1429 | 16529.4492 | 394069.1229 | 32324.3327 | 3172400 | 260222.6538 | 5800974.1625 | 475836.8714 | 1984478.2027 | 162780.918 | 7785452.3652 | 638617.7894 | 10957852.3652 | 898840.4432 | 3575000 | 293246.7492 | 14926921.488 | 1224411.5251 | 141602.34 | 11615.224 | 37110.15 | 3044.0366 | 178712.49 | 14659.2606 | 2960974 | 242880 | 53640.8333 | 4400 | 3014614.8333 | 247280 | 3193327.3233 | 261939.2606 | 340560 | 27935.1365 | 2050928 | 168231.5997 | 104060 | 8535.7361 | 37125 | 3045.2547 | 415250 | 34061.7378 | 33000 | 2706.8931 | 817500 | 67057.1238 | 3798423 | 311573.4816 | 3328011.4021 | 272987 | 1664206.8542 | 136510 | 403029.4625 | 33059.323 | 125711.7183 | 10311.763 | 3731040.8646 | 306046.323 | 1789918.5725 | 146821.763 | 5533.4177 | 453.89 | 9900 | 812.0679 | 15433.4177 | 1265.9579 | 0 | 0 | 22471818.7703 | 1843297.2876 | 4983245.8958 | 408761.0236 | 12191098.4848 | 6391883.4145 | 34662917.2552 | 11375129.3102
1233-259R | oh | 3 | 5.1133 | 5.1133 | 4.8975 | 4.8975 | 7.0651 | 20586.83 | 4203.506 | 39440.5 | 8053.1281 | 34595 | 7063.7534 | 98799.6429 | 20173.329 | 193421.9729 | 39493.7166 | 1555400 | 317588.1511 | 2844166.9438 | 580734.037 | 972972.3227 | 198665.6044 | 3817139.2664 | 779399.6414 | 5372539.2664 | 1096987.7925 | 1525000 | 311380.9505 | 7090961.2393 | 1447862.4596 | 69426.39 | 14175.774 | 15315.3 | 3127.1427 | 84741.69 | 17302.9167 | 1189514 | 242880 | 21549.1667 | 4400 | 1211063.1667 | 247280 | 1295804.8567 | 264582.9167 | 162360 | 33151.3516 | 977768 | 199644.8061 | 49610 | 10129.5796 | 16335 | 3335.3494 | 182710 | 37306.5006 | 14520 | 2964.755 | 359700 | 73445.0675 | 1763003 | 359977.4098 | 1336964.1729 | 272987 | 668562.8958 | 136510 | 84055.4876 | 17162.805 | 36786.4747 | 7511.218 | 1421019.6605 | 290149.805 | 705349.3705 | 144021.218 | 2222.9435 | 453.89 | 9900 | 2021.4239 | 12122.9435 | 2475.3139 | 0 | 0 | 10287106.8433 | 2100464.9883 | 2001154.2272 | 408604.1347 | 4897537.8788 | 14130291.223 | 15184644.722 | 16131445.4502
1233-585R | oh | 3 | 6.3422 | 6.3422 | 6.2352 | 6.2352 | 8.5082 | 28128.54 | 4511.2293 | 53889 | 8642.6681 | 48152.5 | 7722.6535 | 134993.5714 | 21650.1445 | 265163.6114 | 42526.6955 | 2125200 | 340837.6162 | 3886089.4875 | 623247.4483 | 1329407.728 | 213209.1855 | 5215497.2155 | 836456.6338 | 7340697.2155 | 1177294.25 | 2400000 | 384909.7868 | 10005860.8269 | 1604730.7322 | 94859.82 | 15213.5305 | 37110.15 | 5951.6916 | 131969.97 | 21165.2221 | 1514412 | 242880 | 27435 | 4400 | 1541847 | 247280 | 1673816.97 | 268445.2221 | 436590 | 70019.9016 | 2629242 | 421675.4073 | 133402.5 | 21394.9699 | 24750 | 3969.3822 | 276833.3333 | 44398.2747 | 22000 | 3528.3397 | 545000 | 87406.5974 | 4067817.8333 | 652392.8729 | 1702135.9875 | 272987 | 851170.875 | 136510 | 106908.2965 | 17145.854 | 46816.3872 | 7508.369 | 1809044.284 | 290132.854 | 897987.2622 | 144018.369 | 2830.1073 | 453.89 | 9900 | 1587.7529 | 12730.1073 | 2041.6429 | 0 | 0 | 15895453.0515 | 2549298.1019 | 2571804.2322 | 412463.5911 | 6235227.2727 | 17016328.6227 | 22130680.3243 | 19588132.8549
1233-587R | oh | 3 | 8.7375 | 8.7375 | 7.6085 | 7.6085 | 9.6691 | 32205.14 | 4232.7717 | 61699 | 8109.1957 | 60775 | 7987.753 | 154557.8571 | 20313.78 | 309236.9971 | 40643.5005 | 2433200 | 319799.2682 | 4449290.8625 | 584777.2323 | 1522075.5147 | 200048.7571 | 5971366.3772 | 784825.9894 | 8404566.3772 | 1104625.2575 | 3100000 | 407437.8314 | 11813803.3743 | 1552706.5894 | 108607.62 | 14274.4688 | 36521.1 | 4800.0251 | 145128.72 | 19074.4939 | 1847958 | 242880 | 33477.5 | 4400 | 1881435.5 | 247280 | 2026564.22 | 266354.4939 | 752400 | 98889.1046 | 4531120 | 595532.1634 | 229900 | 30216.1153 | 29205 | 3838.4587 | 326663.3333 | 42933.871 | 25960 | 3411.9633 | 643100 | 84523.6353 | 6538348.3333 | 859345.3115 | 2077027.7937 | 272987 | 1038639.4375 | 136510 | 130404.571 | 17139.276 | 57116.9671 | 7506.972 | 2207432.3647 | 290126.276 | 1095756.4046 | 144016.972 | 3453.4324 | 453.89 | 9900 | 1301.1724 | 13353.4324 | 1755.0624 | 0 | 0 | 20572937.5047 | 2703933.2394 | 3122320.6246 | 410371.4659 | 7608522.7273 | 19338274.3682 | 28181460.232 | 22460594.9927
1233-589R | oh | 3 | 3.2114 | 3.2114 | 3.2034 | 3.2034 | 4.4711 | 11618.31 | 3626.858 | 22258.5 | 6948.3789 | 19635 | 6129.4076 | 55758.2143 | 17405.8987 | 109270.0243 | 34110.5432 | 877800 | 274020.5747 | 1605123.9187 | 501067.417 | 549103.192 | 171412.1351 | 2154227.1107 | 672479.5521 | 3032027.1107 | 946500.1268 | 1050000 | 327775.807 | 4191297.135 | 1308386.4771 | 39181.23 | 12231.1041 | 10013.85 | 3125.9979 | 49195.08 | 15357.102 | 778044 | 242880 | 14095 | 4400 | 792139 | 247280 | 841334.08 | 262637.102 | 115830 | 36158.354 | 697554 | 217753.6431 | 35392.5 | 11048.386 | 8415 | 2626.889 | 94123.3333 | 29382.2396 | 7480 | 2335.0124 | 185300 | 57844.6258 | 1144094.8333 | 357149.1498 | 874489.0375 | 272987 | 437297.375 | 136510 | 54902.9497 | 17138.913 | 24048.7833 | 7507.247 | 929391.9872 | 290125.913 | 461346.1583 | 144017.247 | 1453.9954 | 453.89 | 9900 | 3090.4576 | 11353.9954 | 3544.3476 | 0 | 0 | 6276137.9509 | 1959205.8875 | 1302680.2383 | 406654.349 | 3203409.0909 | 8942242.4243 | 9479547.0418 | 10244922.6626
1233-591R | oh | 3 | 6.8411 | 6.8411 | 6.4722 | 6.4722 | 7.9601 | 29963.01 | 4629.5231 | 57403.5 | 8869.2968 | 57970 | 8956.8256 | 143797.5 | 22217.8562 | 289134.01 | 44673.5017 | 2263800 | 349775.0856 | 4139530.1063 | 639590.2894 | 1416108.232 | 218799.9726 | 5555638.3383 | 858390.2621 | 7819438.3383 | 1208165.3477 | 2850000 | 440347.6429 | 10958572.3482 | 1693186.4922 | 101046.33 | 15612.4608 | 35343 | 5460.7743 | 136389.33 | 21073.2351 | 1571958 | 242880 | 28477.5 | 4400 | 1600435.5 | 247280 | 1736824.83 | 268353.2351 | 547470 | 84588.4646 | 3296986 | 509410.5311 | 167282.5 | 25846.4753 | 25245 | 3900.5531 | 282370 | 43628.4084 | 22440 | 3467.1583 | 555900 | 85890.9666 | 4897693.5 | 756732.5573 | 1766815.2937 | 272987 | 883514.4375 | 136510 | 110856.3577 | 17128.188 | 48576.1364 | 7505.399 | 1877671.6514 | 290115.188 | 932090.5739 | 144015.399 | 2937.6483 | 453.89 | 9900 | 1529.6287 | 12837.6483 | 1983.5187 | 0 | 0 | 17746775.148 | 2742017.7562 | 2668915.4039 | 412368.6341 | 6472159.0909 | 15920235.8716 | 24218934.2389 | 18589151.2755
1242-1079R | oh | 2 | 3.0375 | 3.0375 | 1.6259 | 1.6259 | 1.7864 | 8968.52 | 5515.8749 | 17182 | 10567.3803 | 1402.5 | 862.5743 | 43041.4286 | 26471.6066 | 70594.4486 | 43417.436 | 677600 | 416741.7589 | 1239043.025 | 762043.9338 | 423869.1307 | 260690.6243 | 1662912.1557 | 1022734.5582 | 2340512.1557 | 1439476.3171 | 50000 | 30751.3104 | 2461106.6042 | 1513645.0635 | 30245.16 | 18601.5661 | 7068.6 | 4347.3743 | 37313.76 | 22948.9403 | 394910 | 242880 | 7154.1667 | 4400 | 402064.1667 | 247280 | 439377.9267 | 270228.9403 | 28710 | 17657.4024 | 172898 | 106336.8014 | 8772.5 | 5395.3174 | 6435 | 3957.6937 | 71976.6667 | 44267.5364 | 5720 | 3517.9499 | 141700 | 87149.2137 | 436212.1667 | 268281.915 | 443862.3854 | 272987 | 221958.0208 | 136510 |  |  |  |  | 443862.3854 | 272987 | 221958.0208 | 136510 | 738.0011 | 453.89 | 9900 | 6088.7595 | 10638.0011 | 6542.6495 | 0 | 0 | 3351819.1574 | 2061456.628 | 661335.9475 | 406738.9403 | 1625946.9697 | 3572872.4128 | 4977766.1271 | 4234208.3603
1242-1084 | oh | 2 | 1.825 | 1.825 | 1.557 | 1.557 | 2.3663 | 6318.73 | 4058.2526 | 12105.5 | 7774.8498 | 10285 | 6605.6198 | 30324.6429 | 19476.2333 | 59033.8729 | 37914.9554 | 477400 | 306613.7939 | 872962.1312 | 560666.592 | 298635.0693 | 191800.6527 | 1171597.2006 | 752467.2447 | 1648997.2006 | 1059081.0387 | 250000 | 160564.4082 | 1958031.0734 | 1257560.4024 | 21309.09 | 13685.9257 | 4123.35 | 2648.253 | 25432.44 | 16334.1787 | 378166 | 242880 | 6850.8333 | 4400 | 385016.8333 | 247280 | 410449.2733 | 263614.1787 | 84150 | 54045.9798 | 506770 | 325476.9006 | 25712.5 | 16514.0494 | 5445 | 3497.0928 | 60903.3333 | 39115.6307 | 4840 | 3108.5269 | 119900 | 77006.6902 | 807720.8333 | 518764.8705 | 425042.8271 | 272987 | 212547.1042 | 136510 |  |  |  |  | 425042.8271 | 272987 | 212547.1042 | 136510 | 706.7102 | 453.89 | 9900 | 6358.3506 | 10606.7102 | 6812.2406 | 0 | 0 | 3201401.444 | 2056124.5134 | 622996.3775 | 400124.1787 | 1557007.5758 | 4732570.8975 | 4758409.0198 | 5355567.275
1243-319R | oh | 2 | 3.321 | 3.321 | 3.321 | 3.321 | 3.871 | 10802.99 | 3252.9106 | 20696.5 | 6231.9658 | 20570 | 6193.8751 | 51845.3571 | 15611.2624 | 103914.8471 | 31290.0139 | 816200 | 245767.6647 | 1492483.6438 | 449404.8269 | 510569.6347 | 153738.6753 | 2003053.2784 | 603143.5021 | 2819253.2784 | 848911.1668 | 825000 | 248417.4508 | 3748168.1256 | 1128618.6315 | 36431.67 | 10970.0153 | 5301.45 | 1596.3305 | 41733.12 | 12566.3458 | 806610 | 242880 | 14612.5 | 4400 | 821222.5 | 247280 | 862955.62 | 259846.3458 | 113850 | 34281.6082 | 685630 | 206451.4628 | 34787.5 | 10474.9358 | 1980 | 596.2019 | 22146.6667 | 6668.6285 | 1760 | 529.9572 | 43600 | 13128.4859 | 903754.1667 | 272131.2803 | 906596.0312 | 272987 | 453352.8125 | 136510 | 53406.0938 | 16081.219 | 24316.4786 | 7321.985 | 960002.125 | 289068.219 | 477669.2911 | 143831.985 | 1507.379 | 453.89 | 9900 | 2981.0094 | 11407.379 | 3434.8994 | 0 | 0 | 5623331.7963 | 1693253.0302 | 1340624.9111 | 403678.3308 | 3321022.7273 | 7741930.2602 | 8944354.5235 | 9082555.1713
1243-45R | oh | 2 | 6.5388 | 6.5388 | 4.2258 | 4.2258 | 4.5615 | 14064.27 | 3328.2245 | 26944.5 | 6376.2531 | 7947.5 | 1880.7279 | 67496.7857 | 15972.7066 | 116453.0557 | 27557.9121 | 1062600 | 251457.8702 | 1943044.7437 | 459809.7995 | 664703.864 | 157298.1535 | 2607748.6077 | 617107.9531 | 3670348.6077 | 868565.8233 | 375000 | 88741.4844 | 4161801.6635 | 984865.2198 | 47429.91 | 11224.0016 | 12959.1 | 3066.6927 | 60389.01 | 14290.6944 | 1026352 | 242880 | 18593.3333 | 4400 | 1044945.3333 | 247280 | 1105334.3433 | 261570.6944 | 148500 | 35141.6278 | 894300 | 211630.692 | 45375 | 10737.7196 | 8910 | 2108.4977 | 99660 | 23583.9369 | 7920 | 1874.2202 | 196200 | 46429.5446 | 1400865 | 331506.2388 | 1153576.8833 | 272987 | 576858.1667 | 136510 | 67949.9409 | 16079.943 | 30940.0969 | 7321.787 | 1221526.8243 | 289066.943 | 607798.2635 | 143831.787 | 1918.0291 | 453.89 | 9900 | 2342.7752 | 11818.0291 | 2796.6652 | 0 | 0 | 6796011.5169 | 1608235.0667 | 1713132.6069 | 405402.4814 | 4225757.5758 | 9122970.3213 | 11021769.0926 | 10836102.9282
1250-27R | oh | 2 | 18.1972 | 2.6189 | 1.6112 | 4.8328 | 5.8887 | 23848.11 | 4934.6718 | 45688.5 | 9453.9045 | 38335 | 7932.3118 | 30324.6429 | 6274.8017 | 138196.2529 | 28595.6897 | 1801800 | 372830.0349 | 3294728.0438 | 681748.0139 | 1127106.552 | 233221.8754 | 4421834.5958 | 914969.8893 | 6223634.5958 | 1287799.9242 | 150000 | 31038.1314 | 6511830.8486 | 1347433.7454 | 80424.63 | 16641.5349 | 84823.2 | 17551.6909 | 165247.83 | 34193.2258 | 1173782 | 242880 | 21264.1667 | 4400 | 1195046.1667 | 247280 | 1360293.9967 | 281473.2258 | 414810 | 85832.8487 | 2498078 | 516904.4888 | 126747.5 | 26226.7038 | 3465 | 716.9808 | 38756.6667 | 8019.5634 | 3080 | 637.3163 | 76300 | 15788.0629 | 3161237.1667 | 654125.9647 | 439829.6229 | 91009.931 | 219941.3958 | 45510.4664 | 26170.6512 | 5415.2541 | 11843.4454 | 2450.6561 | 466000.2741 | 96425.1851 | 231784.8412 | 47961.1225 | 2193.5438 | 453.89 | 9900 | 2048.5167 | 12093.5438 | 2502.4067 | 0 | 0 | 10151161.8332 | 2100487.3018 | 1592078.8379 | 329434.3482 | 4832765.1515 | 11777435.1319 | 14983926.9847 | 13369513.9698
1250-671R | oh | 2 | 17.1782 | 2.6275 | 1.4062 | 2.0739 | 2.4212 | 9783.84 | 4717.6872 | 18744 | 9038.2027 | 13557.5 | 6537.3151 | 28368.2143 | 13678.9198 | 70453.5543 | 33972.1248 | 739200 | 356436.1644 | 1351683.3 | 651770.5775 | 462402.688 | 222966.7756 | 1814085.988 | 874737.3531 | 2553285.988 | 1231173.5175 | 375000 | 180821.9178 | 2998739.5423 | 1445967.5601 | 32994.72 | 15909.7828 | 83056.05 | 40048.9447 | 116050.77 | 55958.7275 | 503700 | 242880 | 9125 | 4400 | 512825 | 247280 | 628875.77 | 303238.7275 | 443520 | 213861.6986 | 2670976 | 1287922.674 | 135520 | 65346.6301 | 8415 | 4057.6438 | 94123.3333 | 45385.4977 | 7480 | 3606.7945 | 185300 | 89350.137 | 3545334.3333 | 1709531.0758 | 383887.9687 | 185107.6233 | 191967.1875 | 92565 | 22874.3522 | 11029.8246 | 10342.5145 | 4987.0755 | 406762.3209 | 196137.4479 | 202309.702 | 97552.0755 | 941.306 | 453.89 | 9900 | 4773.6986 | 10841.306 | 5227.5886 | 0 | 0 | 6961677.5025 | 3356863.6724 | 831185.472 | 400790.803 | 2073863.6364 | 4842304.971 | 9035541.1389 | 5673490.443
1250-677R | oh | 2 | 11.6765 | 11.6765 | 9.5761 | 9.5761 | 12.0488 | 42804.3 | 4469.8925 | 82005 | 8563.4745 | 71060 | 7420.5293 | 205425 | 21451.7622 | 401294.3 | 41905.6585 | 3234000 | 337714.4891 | 5913614.4375 | 617536.5735 | 2023011.76 | 211255.5297 | 7936626.1975 | 828792.1032 | 11170626.1975 | 1166506.5924 | 3900000 | 407262.371 | 15471920.4975 | 1615674.6218 | 144351.9 | 15074.1274 | 45945.9 | 4797.958 | 190297.8 | 19872.0854 | 2325852 | 242880 | 42135 | 4400 | 2367987 | 247280 | 2558284.8 | 267152.0854 | 898920 | 93870.8437 | 5413496 | 565311.081 | 274670 | 28682.7578 | 25740 | 2687.9316 | 287906.6667 | 30065.0133 | 22880 | 2389.2726 | 566800 | 59188.7979 | 7490412.6667 | 782195.698 | 2614160.7375 | 272987 | 1307238.375 | 136510 | 156022.0075 | 16292.793 | 70474.7903 | 7359.418 | 2770182.745 | 289279.793 | 1377713.1653 | 143869.418 | 4346.5125 | 453.89 | 9900 | 1033.8199 | 14246.5125 | 1487.7099 | 0 | 0 | 25746762.4217 | 2688637.8226 | 3935997.9653 | 411021.5034 | 9576136.3636 | 24097629.6765 | 35322898.7853 | 28033627.6418
1250-8R | oh | 2 | 4.2771 | 4.2771 | 4.2055 | 4.2055 | 5.2124 | 21198.32 | 5040.6273 | 40612 | 9656.8953 | 38802.5 | 9226.6246 | 101734.2857 | 24190.8142 | 202347.1057 | 48114.9614 | 1601600 | 380835.3074 | 2928647.15 | 696386.2622 | 1001872.4907 | 238229.5317 | 3930519.6407 | 934615.7939 | 5532119.6407 | 1315451.1012 | 1225000 | 291285.7465 | 6959466.7464 | 1654851.8091 | 71488.56 | 16998.856 | 17082.45 | 4061.9381 | 88571.01 | 21060.7941 | 1021430 | 242880 | 18504.1667 | 4400 | 1039934.1667 | 247280 | 1128505.1767 | 268340.7941 | 351450 | 83569.2862 | 2116510 | 503272.8124 | 107387.5 | 25535.0597 | 13365 | 3177.9869 | 149490 | 35546.3724 | 11880 | 2824.8773 | 294300 | 69979.9144 | 3044382.5 | 723906.3094 | 1148044.7604 | 272987 | 574091.7708 | 136510 | 68522.502 | 16293.574 | 30950.2542 | 7359.484 | 1216567.2624 | 289280.574 | 605042.025 | 143869.484 | 1908.831 | 453.89 | 9900 | 2354.0644 | 11808.831 | 2807.9544 | 0 | 0 | 11232225.3398 | 2670846.6469 | 1733547.2017 | 412210.2781 | 4205492.4242 | 10424862.2616 | 15437717.764 | 12158409.4633
1458-1058F | oh | 3 | 9.4663 | 9.4663 | 1.4693 | 1.4693 | 1.8093 | 6114.9 | 4161.7262 | 11715 | 7973.0858 | 6077.5 | 4136.2722 | 29346.4286 | 19972.8207 | 53253.8286 | 36243.905 | 462000 | 314431.5545 | 844802.0625 | 574961.9606 | 289001.68 | 196691.0119 | 1133803.7425 | 771652.9725 | 1595803.7425 | 1086084.527 | 225000 | 153132.2506 | 1874057.5711 | 1275460.6826 | 20621.7 | 14034.877 | 35343 | 24054.0139 | 55964.7 | 38088.891 | 356868 | 242880 | 6465 | 4400 | 363333 | 247280 | 419297.7 | 285368.891 | 13860 | 9432.9466 | 83468 | 56807.3009 | 4235 | 2882.2892 | 5445 | 3705.8005 | 60903.3333 | 41450.0644 | 4840 | 3294.0449 | 119900 | 81602.4749 | 292651.3333 | 199174.9214 | 401104.7625 | 272987 | 200576.625 | 136510 | 26423.9743 | 17983.834 | 11250.199 | 7656.748 | 427528.7368 | 290970.834 | 211826.824 | 144166.748 | 666.9088 | 453.89 | 9900 | 6737.819 | 10566.9088 | 7191.709 | 0 | 0 | 2604804.55 | 1772798.147 | 631124.524 | 429535.639 | 1469318.1818 | 3618640.7008 | 4074122.7318 | 4249765.2248
1458-1061 | oh | 2 | 3.3057 | 3.3057 | 2.3455 | 2.3455 | 2.9619 | 10802.99 | 4605.926 | 20696.5 | 8824.0891 | 23375 | 9966.0853 | 51845.3571 | 22104.6096 | 106719.8471 | 45500.71 | 816200 | 347992.2481 | 1492483.6438 | 636330.2357 | 510569.6347 | 217684.728 | 2003053.2784 | 854014.9637 | 2819253.2784 | 1202007.2117 | 1475000 | 628875.969 | 4400973.1256 | 1876383.8907 | 36431.67 | 15532.8826 | 17671.5 | 7534.3605 | 54103.17 | 23067.243 | 569664 | 242880 | 10320 | 4400 | 579984 | 247280 | 634087.17 | 270347.243 | 213840 | 91172.093 | 1287792 | 549058.6047 | 65340 | 27858.1395 | 20790 | 8863.9535 | 232540 | 99144.9612 | 18480 | 7879.0698 | 457800 | 195186.0465 | 2296582 | 979162.8682 | 640278.6 | 272987 | 320178 | 136510 | 42341.0508 | 18052.386 | 17986.9602 | 7668.859 | 682619.6508 | 291039.386 | 338164.9602 | 144178.859 | 1064.5784 | 453.89 | 9900 | 4220.9302 | 10964.5784 | 4674.8202 | 0 | 0 | 7391139.3547 | 3151260.9652 | 972252.1302 | 414526.102 | 2345454.5455 | 5923861.8208 | 9736593.9002 | 6896113.951
1458-1131R | oh | 3 | 9.7284 | 9.7284 | 6.2818 | 6.2818 | 8.1439 | 27109.39 | 4315.5324 | 51936.5 | 8267.7496 | 23375 | 3721.0564 | 130102.5 | 20710.9624 | 232523.39 | 37015.3009 | 2048200 | 326052.0984 | 3745289.1437 | 596211.007 | 1281240.7813 | 203960.1823 | 5026529.9251 | 800171.1892 | 7074729.9251 | 1126223.2876 | 775000 | 123371.9247 | 8082253.3151 | 1286610.5133 | 91422.87 | 14553.5683 | 44767.8 | 7126.5673 | 136190.67 | 21680.1356 | 1525728 | 242880 | 27640 | 4400 | 1553368 | 247280 | 1689558.67 | 268960.1356 | 151470 | 24112.4457 | 912186 | 145210.5065 | 46282.5 | 7367.6918 | 40095 | 6382.7062 | 448470 | 71391.7511 | 35640 | 5673.5166 | 882900 | 140548.4805 | 2517043.5 | 400687.0984 | 1714854.7 | 272987 | 857531 | 136510 | 114086.4494 | 18161.374 | 48292.1243 | 7687.603 | 1828941.1494 | 291148.374 | 905823.1243 | 144197.603 | 2851.2545 | 453.89 | 9900 | 1575.9768 | 12751.2545 | 2029.8668 | 0 | 0 | 12440989.2189 | 1980475.8525 | 2595381.7943 | 413157.7386 | 6281818.1818 | 16287861.9116 | 18722807.4008 | 18883243.7059
1458-565R | oh | 3 | 6.0765 | 6.0765 | 5.7011 | 5.7011 | 7.74 | 22217.47 | 3897.0248 | 42564.5 | 7465.9677 | 45815 | 8036.1172 | 106625.3571 | 18702.4744 | 217222.3271 | 38101.5842 | 1678600 | 294432.5294 | 3069447.4937 | 538392.2253 | 1050039.4373 | 184180.7265 | 4119486.9311 | 722572.9518 | 5798086.9311 | 1017005.4812 | 1550000 | 271875.6229 | 7565309.2582 | 1326982.6883 | 74925.51 | 13142.2063 | 30630.6 | 5372.7184 | 105556.11 | 18514.9246 | 1384692 | 242880 | 25085 | 4400 | 1409777 | 247280 | 1515333.11 | 265794.9246 | 311850 | 54699.6213 | 1878030 | 329413.2749 | 95287.5 | 16713.7732 | 23265 | 4080.7654 | 260223.3333 | 45644.1167 | 20680 | 3627.347 | 512300 | 89859.2785 | 3101635.8333 | 544038.1769 | 1556336.1125 | 272987 | 778262.125 | 136510 | 103132.3995 | 18089.797 | 43757.4587 | 7675.217 | 1659468.512 | 291076.797 | 822019.5837 | 144185.217 | 2587.6888 | 453.89 | 9900 | 1736.4959 | 12487.6888 | 2190.3859 | 0 | 0 | 12338901.2923 | 2164288.0481 | 2337352.6937 | 409980.1416 | 5701136.3636 | 15479984.1007 | 18040037.656 | 17817336.7945
1458-601R | oh | 3 | 17.35 | 17.35 | 15.4477 | 15.4477 | 18.7352 | 72359.65 | 4684.1615 | 138627.5 | 8973.9738 | 113602.5 | 7353.9944 | 347266.0714 | 22480.0752 | 671855.7214 | 43492.205 | 5467000 | 353903.1926 | 9996824.4062 | 647138.8464 | 3419853.2133 | 221382.2883 | 13416677.6196 | 868521.1347 | 18883677.6196 | 1222424.3273 | 6200000 | 401353.5383 | 25755533.341 | 1667270.0706 | 244023.45 | 15796.7218 | 73042.2 | 4728.346 | 317065.65 | 20525.0678 | 3751944 | 242880 | 67970 | 4400 | 3819914 | 247280 | 4136979.65 | 267805.0678 | 740520 | 47937.1487 | 4459576 | 288688.1624 | 226270 | 14647.4621 | 89595 | 5799.8823 | 1002136.6667 | 64872.7576 | 79640 | 5155.4509 | 1972900 | 127714.58 | 8570637.6667 | 554815.4441 | 4217028.725 | 272987 | 2108769.25 | 136510 | 280499.4456 | 18157.975 | 118747.1584 | 7687.031 | 4497528.1706 | 291144.975 | 2227516.4084 | 144197.031 | 7011.5689 | 453.89 | 9900 | 640.871 | 16911.5689 | 1094.761 | 0 | 0 | 38840610.7472 | 2514325.2507 | 6364496.0584 | 412002.0988 | 15447727.2727 | 37470449.2493 | 54288338.02 | 43834945.3077
157-165R | oh | 3 | 5.1191 | 5.1191 | 4.8606 | 4.8606 | 6.3775 | 16714.06 | 3438.6782 | 32021 | 6587.8616 | 16830 | 3462.5312 | 80213.5714 | 16502.7921 | 145778.6314 | 29991.8631 | 1262800 | 259802.9925 | 2309125.6375 | 475069.489 | 789937.9253 | 162518.4011 | 3099063.5628 | 637587.8901 | 4361863.5628 | 897390.8826 | 650000 | 133728.1796 | 5157642.1943 | 1061110.9253 | 56365.98 | 11596.4921 | 10602.9 | 2181.3946 | 66968.88 | 13777.8868 | 1180544 | 242880 | 21386.6667 | 4400 | 1201930.6667 | 247280 | 1268899.5467 | 261057.8868 | 138600 | 28514.9626 | 834680 | 171723.4414 | 42350 | 8712.9052 | 13860 | 2851.4963 | 155026.6667 | 31894.5137 | 12320 | 2534.6633 | 305200 | 62790.5237 | 1502036.6667 | 309022.5062 | 1326882.2667 | 272987 | 663521.3333 | 136510 | 107131.6412 | 22040.799 | 40682.5193 | 8369.845 | 1434013.9079 | 295027.799 | 704203.8527 | 144879.845 | 2206.1805 | 453.89 | 9900 | 2036.783 | 12106.1805 | 2490.673 | 0 | 0 | 8105798.9493 | 1667651.9035 | 1973103.3993 | 405937.7318 | 4860606.0606 | 12755028.0763 | 12966405.0099 | 14728131.4756
157-189R | oh | 3 | 30.1703 | 30.1032 | 27.7678 | 27.7678 | 37.3398 | 111087.35 | 4000.5812 | 212822.5 | 7664.3622 | 93500 | 3367.2091 | 533126.7857 | 19199.4586 | 950536.6357 | 34231.6111 | 8393000 | 302256.5376 | 15347237.4688 | 552699.0181 | 5250197.1867 | 189074.9938 | 20597434.6554 | 741774.0119 | 28990434.6554 | 1044030.5495 | 4325000 | 155755.9305 | 34265971.2911 | 1234018.0912 | 374627.55 | 13491.4365 | 97782.3 | 3521.4273 | 472409.85 | 17012.8638 | 6744244 | 242880 | 122178.3333 | 4400 | 6866422.3333 | 247280 | 7338832.1833 | 264292.8638 | 993960 | 35795.4138 | 5985848 | 215567.9365 | 303710 | 10937.4876 | 119790 | 4313.9891 | 1339873.3333 | 48252.7671 | 106480 | 3834.657 | 2637800 | 94994.9118 | 11487461.3333 | 413697.1629 | 7580249.2458 | 272987 | 3790582.7917 | 136510 | 608247.1166 | 21904.762 | 231729.2305 | 8345.249 | 8188496.3625 | 294891.762 | 4022312.0221 | 144855.249 | 12603.5281 | 453.89 | 9900 | 356.528 | 22503.5281 | 810.418 | 0 | 0 | 53964432.5151 | 1943417.4341 | 11361144.2055 | 409148.1128 | 27767803.0303 | 74679540.6187 | 81732235.5454 | 86040684.8242
157-1928R | oh | 3 | 3.4428 | 3.4428 | 3.1864 | 3.1864 | 4.3384 | 11414.48 | 3582.2904 | 21868 | 6862.9957 | 6077.5 | 1907.3466 | 54780 | 17192.0114 | 94139.98 | 29544.6442 | 862400 | 270653.3524 | 1576963.85 | 494910.1954 | 539469.8027 | 169305.7869 | 2116433.6527 | 664215.9823 | 2978833.6527 | 934869.3346 | 275000 | 86305.2782 | 3347973.6327 | 1050719.257 | 38493.84 | 12080.8057 | 8835.75 | 2772.9886 | 47329.59 | 14853.7943 | 773904 | 242880 | 14020 | 4400 | 787924 | 247280 | 835253.59 | 262133.7943 | 105930 | 33244.7932 | 637934 | 200207.5321 | 32367.5 | 10158.1312 | 10395 | 3262.3395 | 116270 | 36489.8716 | 9240 | 2899.8573 | 228900 | 71837.3752 | 1141036.5 | 358099.9001 | 869835.85 | 272987 | 434970.5 | 136510 | 70948.0698 | 22266.156 | 26796.0755 | 8409.61 | 940783.9198 | 295253.156 | 461766.5755 | 144919.61 | 1446.2586 | 453.89 | 9900 | 3106.99 | 11346.2586 | 3560.88 | 0 | 0 | 5441140.3111 | 1707633.1932 | 1297020.1655 | 407053.4043 | 3186363.6364 | 8676891.4968 | 8627503.9474 | 9973911.6623
157-204R | oh | 3 | 13.5155 | 13.5155 | 13.2184 | 13.2184 | 18.5294 | 41581.32 | 3145.7219 | 79662 | 6026.6124 | 32725 | 2475.7211 | 199555.7143 | 15096.846 | 353524.0343 | 26744.9014 | 3141600 | 237669.2218 | 5744654.025 | 434596.2095 | 1965211.424 | 148672.7368 | 7709865.449 | 583268.9463 | 10851465.449 | 820938.1682 | 1175000 | 88891.4361 | 12379989.4833 | 936574.5056 | 140227.56 | 10608.5355 | 9424.8 | 713.0077 | 149652.36 | 11321.5431 | 3210478 | 242880 | 58160.8333 | 4400 | 3268638.8333 | 247280 | 3418291.1933 | 258601.5431 | 304920 | 23067.8951 | 1836296 | 138919.9903 | 93170 | 7048.5235 | 16830 | 1273.228 | 188246.6667 | 14241.2907 | 14960 | 1131.7582 | 370600 | 28036.7372 | 2825022.6667 | 213719.4229 | 3608443.5021 | 272987 | 1804439.8542 | 136510 | 295494.2563 | 22354.816 | 111363.8918 | 8424.933 | 3903937.7583 | 295341.816 | 1915803.746 | 144934.933 | 5999.6865 | 453.89 | 9900 | 748.9576 | 15899.6865 | 1202.8476 | 0 | 0 | 19124849.5948 | 1446838.5921 | 5334094.9393 | 403536.4761 | 13218371.2121 | 37058889.9059 | 32343220.8069 | 42392984.8453
157-207R | oh | 3 | 2.0208 | 2.0208 | 2.0208 | 2.0208 | 3.0917 | 4891.92 | 2420.7439 | 9372 | 4637.6907 |  |  | 23477.1429 | 11617.5552 | 37741.0629 | 18675.9899 | 369600 | 182894.8454 | 675841.65 | 334437.1052 | 231201.344 | 114408.9125 | 907042.994 | 448846.0176 | 1276642.994 | 631740.863 | 0 | 0 | 1314384.0569 | 650416.8529 | 16497.36 | 8163.6421 | 589.05 | 291.4887 | 17086.41 | 8455.1307 | 490820 | 242880 | 8891.6667 | 4400 | 499711.6667 | 247280 | 516798.0767 | 255735.1307 | 0 | 0 | 0 | 0 | 0 | 0 | 2475 | 1224.7423 | 27683.3333 | 13698.9691 | 2200 | 1088.6598 | 54500 | 26969.0722 | 86858.3333 | 42981.4433 | 551661.2292 | 272987 | 275863.9583 | 136510 |  |  |  |  | 551661.2292 | 272987 | 275863.9583 | 136510 | 917.236 | 453.89 | 9900 | 4898.9691 | 10817.236 | 5352.8591 | 0 | 0 | 1963720.8554 | 971738.1552 | 792662.035 | 392245.1307 | 2020833.3333 | 6183424.644 | 3984554.1887 | 6976086.679
157-232R | oh | 3 | 11.0464 | 11.0464 | 10.9006 | 10.9006 | 7.8466 | 44842.6 | 4113.7856 | 85910 | 7881.2406 | 53295 | 4889.1947 | 215207.1429 | 19742.7454 | 399254.7429 | 36626.9662 | 3388000 | 310809.4866 | 6195215.125 | 568338.7344 | 2119345.6533 | 194425.2463 | 8314560.7783 | 762763.9807 | 11702560.7783 | 1073573.4673 | 2625000 | 240813.1353 | 14726815.5212 | 1351013.5688 | 151225.8 | 13873.2034 | 43000.65 | 3944.8081 | 194226.45 | 17818.0116 | 2647530 | 242880 | 47962.5 | 4400 | 2695492.5 | 247280 | 2889718.95 | 265098.0116 | 354420 | 32513.9015 | 2134396 | 195805.9401 | 108295 | 9934.8032 | 51975 | 4768.1001 | 581350 | 53332.0824 | 46200 | 4238.3112 | 1144500 | 104994.527 | 4421136 | 405587.6654 | 2975713.4062 | 272987 | 1488036.5625 | 136510 | 244808.9934 | 22458.37 | 92029.4857 | 8442.632 | 3220522.3997 | 295445.37 | 1580066.0482 | 144952.632 | 4947.6589 | 453.89 | 9900 | 908.2095 | 14847.6589 | 1362.0995 | 0 | 0 | 22383321.5798 | 2053408.7037 | 4469784.9982 | 410050.6436 | 10900568.1818 | 15693195.3994 | 33283889.7616 | 20162980.3976
157-257R | oh | 3 | 23.8805 | 23.6746 | 22.8015 | 23.0074 | 33.1376 | 91723.5 | 3986.6979 | 175725 | 7637.7646 | 76670 | 3332.4081 | 436283.5714 | 18962.7611 | 780402.0714 | 33919.6317 | 6930000 | 301207.6161 | 12672030.9375 | 550780.9856 | 4335025.2 | 188418.8465 | 17007056.1375 | 739199.8321 | 23937056.1375 | 1040407.4483 | 2675000 | 116267.0091 | 27392458.2089 | 1190594.089 | 309325.5 | 13444.6171 | 90124.65 | 3917.205 | 399450.15 | 17361.8221 | 5588034 | 242880 | 101232.5 | 4400 | 5689266.5 | 247280 | 6088716.65 | 264641.8221 | 886050 | 38511.5452 | 5335990 | 231925.0833 | 270737.5 | 11767.4166 | 104940 | 4561.1439 | 1173773.3333 | 51017.2392 | 93280 | 4054.3501 | 2310800 | 100437.3102 | 10175570.8333 | 442274.0885 | 6224517.2167 | 270544.299 | 3112634.8333 | 135288.5019 | 510745.0012 | 22199.1752 | 192249.4701 | 8355.9891 | 6735262.2179 | 292743.4743 | 3304884.3034 | 143644.491 | 10442.8226 | 453.89 | 9900 | 430.2966 | 20342.8226 | 884.1866 | 0 | 0 | 44323634.0827 | 1926495.8384 | 9393600.9534 | 408286.3131 | 23007386.3636 | 66275257.2432 | 67331020.4464 | 75668858.1967
157-273R | oh | 3 | 8.5773 | 8.5773 | 8.4758 | 8.4758 | 11.6395 | 31593.65 | 3727.5311 | 60527.5 | 7141.2496 | 19167.5 | 2261.4498 | 151623.2143 | 17889.0457 | 262911.8643 | 31019.2761 | 2387000 | 281626.7429 | 4364810.6562 | 514975.8729 | 1493175.3467 | 176170.1339 | 5857986.0029 | 691146.0068 | 8244986.0029 | 972772.7497 | 825000 | 97336.4319 | 9332897.8672 | 1101128.4577 | 106545.45 | 12570.6108 | 28863.45 | 3405.4124 | 135408.9 | 15976.0232 | 2058592 | 242880 | 37293.3333 | 4400 | 2095885.3333 | 247280 | 2231294.2333 | 263256.0232 | 446490 | 52678.4769 | 2688862 | 317241.4945 | 136427.5 | 16096.2013 | 30690 | 3620.9153 | 343273.3333 | 40500.6078 | 27280 | 3218.5913 | 675800 | 79733.2857 | 4348822.8333 | 513089.5728 | 2313771.6333 | 272987 | 1157025.6667 | 136510 | 192515.2724 | 22713.636 | 71936.3227 | 8487.303 | 2506286.9057 | 295700.636 | 1228961.9894 | 144997.303 | 3847.0616 | 453.89 | 9900 | 1168.0372 | 13747.0616 | 1621.9272 | 0 | 0 | 16201754.6679 | 1911540.5936 | 3460256.2227 | 408253.3262 | 8475757.5758 | 23279051.8026 | 24677512.2436 | 26739308.0253
157-81R | oh | 3 | 29.6551 | 29.6551 | 27.7907 | 27.7907 | 36.7477 | 115163.95 | 4143.9715 | 220632.5 | 7939.0711 | 169235 | 6089.6228 | 552691.0714 | 19887.6128 | 1057722.5214 | 38060.2781 | 8701000 | 313090.1285 | 15910438.8438 | 572509.0612 | 5442864.9733 | 195851.8899 | 21353303.8171 | 768360.9511 | 30054303.8171 | 1081451.0795 | 8500000 | 305857.4982 | 39612026.3385 | 1425368.8559 | 388375.35 | 13975.0015 | 126056.7 | 4535.9279 | 514432.05 | 18510.9294 | 6749810 | 242880 | 122279.1667 | 4400 | 6872089.1667 | 247280 | 7386521.2167 | 265790.9294 | 1362240 | 49017.8022 | 8203712 | 295196.0975 | 416240 | 14977.6618 | 136125 | 4898.2179 | 1522583.3333 | 54787.474 | 121000 | 4353.9714 | 2997500 | 107859.7472 | 14759400.3333 | 531090.9719 | 7586505.1979 | 272987 | 3793711.1458 | 136510 | 624893.3134 | 22485.683 | 234763.1607 | 8447.538 | 8211398.5114 | 295472.683 | 4028474.3065 | 144957.538 | 12613.9298 | 453.89 | 9900 | 356.234 | 22513.9298 | 810.124 | 0 | 0 | 62605339.113 | 2252742.6348 | 11414995.5232 | 410748.4674 | 27790719.697 | 73495351.7125 | 90396058.8099 | 84910347.2356
175-2024R | oh | 2 | 7.6492 | 7.6492 | 7.3674 | 7.3674 | 9.7202 | 20383 | 2766.6386 | 39050 | 5300.3599 | 34595 | 4695.671 | 97821.4286 | 13277.5615 | 191849.4286 | 26040.2309 | 1540000 | 209028.2776 | 2816006.875 | 382224.0694 | 963338.9333 | 130756.5442 | 3779345.8083 | 512980.6136 | 5319345.8083 | 722008.8912 | 975000 | 132339.3316 | 6486195.2369 | 880388.4537 | 68739 | 9330.1265 | 14137.2 | 1918.8796 | 82876.2 | 11249.0061 | 1789400 | 242880 | 32416.6667 | 4400 | 1821816.6667 | 247280 | 1904692.8667 | 258529.0061 | 665280 | 90300.2159 | 4006464 | 543807.9671 | 203280 | 27591.7326 | 11385 | 1545.3162 | 127343.3333 | 17284.6478 | 10120 | 1373.6144 | 250700 | 34028.1748 | 5274572.3333 | 715931.6689 | 2011211.0417 | 272987 | 1005727.0833 | 136510 | 139586.4098 | 18946.433 | 57639.7508 | 7823.596 | 2150797.4515 | 291933.433 | 1063366.8342 | 144333.596 | 3344.0002 | 453.89 | 9900 | 1343.7532 | 13244.0002 | 1797.6432 | 0 | 0 | 13924809.0219 | 1890051.1989 | 2968059.7008 | 402862.6021 | 7367424.2424 | 19440384.7631 | 21292233.2643 | 22408444.464
175-24R | oh | 2 | 25.0049 | 11.9797 | 3.9511 | 4.8509 | 7.2512 | 17121.72 | 3529.5624 | 32802 | 6761.9787 | 24777.5 | 5107.7656 | 60649.2857 | 12502.5662 | 135350.5057 | 27901.8729 | 1293600 | 266669.5819 | 2365445.775 | 487625.5687 | 809204.704 | 166813.7601 | 3174650.479 | 654439.3288 | 4468250.479 | 921108.9107 | 750000 | 154608.9876 | 5353600.9847 | 1103619.7712 | 57740.76 | 11902.9873 | 110152.35 | 22707.3911 | 167893.11 | 34610.3784 | 1178198 | 242880 | 21344.1667 | 4400 | 1199542.1667 | 247280 | 1367435.2767 | 281890.3784 | 314820 | 64898.6686 | 1895916 | 390834.2045 | 96195 | 19830.1488 | 4950 | 1020.4193 | 55366.6667 | 11413.579 | 4400 | 907.0394 | 109000 | 22469.8395 | 2480647.6667 | 511373.8992 | 1078608.8625 | 222350.1657 | 539369.625 | 111188.5222 | 73925.062 | 15239.3053 | 30750.5445 | 6339.0807 | 1152533.9245 | 237589.471 | 570120.1695 | 117527.603 | 2201.7963 | 453.89 | 9900 | 2040.8386 | 12101.7963 | 2494.7286 | 0 | 0 | 8998884.3722 | 1855077.87 | 1937555.4462 | 399417.9813 | 4850946.9697 | 14502396.7934 | 13849831.3419 | 16439952.2396
175-64R | oh | 3 | 12.1403 | 12.1403 | 10.35 | 10.35 | 13.5914 | 44638.77 | 4312.9246 | 85519.5 | 8262.7536 | 79942.5 | 7723.913 | 214228.9286 | 20698.4472 | 424329.6986 | 40998.0385 | 3372600 | 325855.0725 | 6167055.0563 | 595850.7301 | 2109712.264 | 203836.9337 | 8276767.3202 | 799687.6638 | 11649367.3203 | 1125542.7363 | 3375000 | 326086.9565 | 15448697.0188 | 1492627.7313 | 150538.41 | 14544.7739 | 50658.3 | 4894.5217 | 201196.71 | 19439.2957 | 2513808 | 242880 | 45540 | 4400 | 2559348 | 247280 | 2760544.71 | 266719.2957 | 770220 | 74417.3913 | 4638436 | 448158.0676 | 235345 | 22738.6473 | 41085 | 3969.5652 | 459543.3333 | 44400.3221 | 36520 | 3528.5024 | 904700 | 87410.628 | 7085849.3333 | 684623.124 | 2825415.45 | 272987 | 1412878.5 | 136510 | 195247.399 | 18864.483 | 80822.7981 | 7808.966 | 3020662.849 | 291851.483 | 1493701.2981 | 144318.966 | 4697.7615 | 453.89 | 9900 | 956.5217 | 14597.7615 | 1410.4117 | 0 | 0 | 25569806.9627 | 2470512.75 | 4254246.0081 | 411038.2617 | 10350000 | 27182895.084 | 35919806.9627 | 31437141.0921
175-90R | oh | 3 | 14.8419 | 14.8419 | 11.9254 | 11.9254 | 16.1428 | 51365.16 | 4307.2141 | 98406 | 8251.8134 | 40205 | 3371.3814 | 246510 | 20671.0415 | 436486.16 | 36601.4504 | 3880800 | 325423.6254 | 7096337.325 | 595061.7965 | 2427614.112 | 203567.0443 | 9523951.437 | 798628.8408 | 13404751.437 | 1124052.4662 | 1575000 | 132071.2766 | 15416237.597 | 1292725.1932 | 173222.28 | 14525.516 | 67740.75 | 5680.3856 | 240963.03 | 20205.9016 | 2896436 | 242880 | 52471.6667 | 4400 | 2948907.6667 | 247280 | 3189870.6967 | 267485.9016 | 963270 | 80774.7927 | 5801026 | 486443.7519 | 294332.5 | 24681.1867 | 72270 | 6060.1849 | 808353.3333 | 67784.2899 | 64240 | 5386.831 | 1591400 | 133446.4949 | 9594891.8333 | 804577.532 | 3255473.3792 | 272987 | 1627933.4583 | 136510 | 224373.8315 | 18814.818 | 93020.1965 | 7800.188 | 3479847.2106 | 291801.818 | 1720953.6548 | 144310.188 | 5412.8102 | 453.89 | 9900 | 830.1623 | 15312.8102 | 1284.0523 | 0 | 0 | 28506289.4512 | 2390388.5955 | 4910824.3515 | 411796.0896 | 11925378.7879 | 32285551.8984 | 40431668.239 | 37196376.2499
175-94R | oh | 2 | 17.59 | 17.59 | 2.029 | 2.029 | 2.8973 | 8968.52 | 4420.2171 | 17182 | 8468.3058 | 13090 | 6451.5262 | 43041.4286 | 21213.3616 | 82281.9486 | 40553.4107 | 677600 | 333961.3554 | 1239043.025 | 610673.6836 | 423869.1307 | 208907.7765 | 1662912.1557 | 819581.4601 | 2340512.1557 | 1153542.8155 | 650000 | 320358.443 | 3072794.1042 | 1514454.6691 | 30245.16 | 14906.6036 | 66562.65 | 32806.0106 | 96807.81 | 47712.6143 | 492798 | 242880 | 8927.5 | 4400 | 501725.5 | 247280 | 598533.31 | 294992.6143 | 234630 | 115639.5407 | 1412994 | 696407.012 | 71692.5 | 35334.3041 | 4950 | 2439.6528 | 55366.6667 | 27287.9679 | 4400 | 2168.5802 | 109000 | 53721.6466 | 1893033.1667 | 932998.7044 | 553884.4187 | 272987 | 276975.6875 | 136510 | 38116.6308 | 18786.13 | 15816.45 | 7795.282 | 592001.0496 | 291773.13 | 292792.1375 | 144305.282 | 920.9325 | 453.89 | 9900 | 4879.3055 | 10820.9325 | 5333.1955 | 0 | 0 | 5568649.253 | 2744559.699 | 891325.4475 | 439297.8963 | 2028977.2727 | 5794645.1089 | 7597626.5257 | 6685970.5564
176-161R | oh | 3 | 11.0765 | 11.0765 | 9.7784 | 9.7784 | 13.4334 | 39135.36 | 4002.2216 | 74976 | 7667.5049 | 57502.5 | 5880.5578 | 187817.1429 | 19207.3313 | 359431.0029 | 36757.6156 | 2956800 | 302380.4765 | 5406733.2 | 552925.6497 | 1849610.752 | 189152.5232 | 7256343.952 | 742078.1729 | 10213143.952 | 1044458.6494 | 2075000 | 212202.208 | 12647574.9549 | 1293418.473 | 131978.88 | 13496.9686 | 49480.2 | 5060.1483 | 181459.08 | 18557.1168 | 2374980 | 242880 | 43025 | 4400 | 2418005 | 247280 | 2599464.08 | 265837.1168 | 641520 | 65605.7641 | 3863376 | 395092.4904 | 196020 | 20046.2057 | 35145 | 3594.1429 | 393103.3333 | 40201.1544 | 31240 | 3194.7937 | 773900 | 79143.7536 | 5934304.3333 | 606878.3049 | 2669378.5625 | 272987 | 1334850.625 | 136510 | 190891.0612 | 19521.689 | 77508.677 | 7926.512 | 2860269.6237 | 292508.689 | 1412359.302 | 144436.512 | 4438.3221 | 453.89 | 9900 | 1012.4346 | 14338.3221 | 1466.3246 | 0 | 0 | 21456487.234 | 2194271.7915 | 4011823.382 | 410273.6288 | 9778409.0909 | 26866723.8395 | 31234896.3249 | 30878547.2215
176-164R | oh | 3 | 7.0595 | 7.0595 | 6.0422 | 6.0422 | 8.2983 | 25886.41 | 4284.2443 | 49593.5 | 8207.8074 | 35530 | 5880.2746 | 124233.2143 | 20560.8053 | 235243.1243 | 38933.1316 | 1955800 | 323688.1798 | 3576328.7313 | 591888.4024 | 1223440.4453 | 202481.4454 | 4799769.1766 | 794369.8477 | 6755569.1766 | 1118058.0275 | 1200000 | 198602.0123 | 8190812.3009 | 1355593.1714 | 87298.53 | 14448.0531 | 34753.95 | 5751.837 | 122052.48 | 20199.8901 | 1467538 | 242880 | 26585.8333 | 4400 | 1494123.8333 | 247280 | 1616176.3133 | 267479.8901 | 344520 | 57018.6377 | 2074776 | 343378.9073 | 105270 | 17422.3615 | 30195 | 4997.3231 | 337736.6667 | 55895.9847 | 26840 | 4442.065 | 664900 | 110042.065 | 3584237.6667 | 593197.3445 | 1649451.5646 | 272987 | 824825.4792 | 136510 | 117982.0794 | 19526.232 | 47898.1672 | 7927.227 | 1767433.644 | 292513.232 | 872723.6464 | 144437.227 | 2742.51 | 453.89 | 9900 | 1638.4666 | 12642.51 | 2092.3566 | 0 | 0 | 13555126.1215 | 2243396.1045 | 2488899.9597 | 411917.1171 | 6042234.8485 | 16596602.7984 | 19597360.97 | 19085502.7581
176-1834R | oh | 3 | 21.5934 | 21.4562 | 12.6396 | 12.6396 | 17.2556 | 51161.33 | 4047.707 | 98015.5 | 7754.6464 | 46750 | 3698.6979 | 245531.7857 | 19425.6234 | 441458.6157 | 34926.6747 | 3865400 | 305817.043 | 7068177.2562 | 559209.6725 | 2417980.7227 | 191302.2494 | 9486157.9789 | 750511.9219 | 13351557.9789 | 1056328.9649 | 1700000 | 134498.1045 | 15493016.5946 | 1225753.7441 | 172534.89 | 13650.3622 | 102494.7 | 8109.0252 | 275029.59 | 21759.3874 | 3069902 | 242880 | 55614.1667 | 4400 | 3125516.1667 | 247280 | 3400545.7567 | 269039.3874 | 791010 | 62581.968 | 4763638 | 376882.5185 | 241697.5 | 19122.268 | 33660 | 2663.0625 | 376493.3333 | 29786.8469 | 29920 | 2367.1666 | 741200 | 58641.1736 | 6977618.8333 | 552045.0041 | 3450441.9354 | 272987 | 1725429.5208 | 136510 | 245711.4524 | 19439.838 | 100008.0362 | 7912.289 | 3696153.3878 | 292426.838 | 1825437.557 | 144422.289 | 5736.9805 | 453.89 | 9900 | 783.2537 | 15636.9805 | 1237.1437 | 0 | 0 | 26182425.7962 | 2071462.7299 | 5225983.3137 | 413461.6764 | 12639583.3333 | 34511228.1562 | 38822009.1296 | 39737211.4699
176-1845R | oh | 3 | 8.2917 | 8.2917 | 6.8333 | 6.8333 | 9.4157 | 29351.52 | 4295.3444 | 56232 | 8229.0732 | 38802.5 | 5678.4146 | 140862.8571 | 20614.0767 | 265248.8771 | 38816.9089 | 2217600 | 324526.8293 | 4055049.9 | 593421.9366 | 1387208.064 | 203006.0581 | 5442257.964 | 796427.9947 | 7659857.964 | 1120954.824 | 1675000 | 245121.9512 | 9600106.8411 | 1404893.6841 | 98984.16 | 14485.4868 | 33575.85 | 4913.539 | 132560.01 | 19399.0259 | 1659680 | 242880 | 30066.6667 | 4400 | 1689746.6667 | 247280 | 1822306.6767 | 266679.0259 | 263340 | 38537.561 | 1585892 | 232081.7561 | 80465 | 11775.3659 | 28710 | 4201.4634 | 321126.6667 | 46994.1463 | 25520 | 3734.6341 | 632200 | 92517.0732 | 2937253.6667 | 429842 | 1865411.1667 | 272987 | 932818.3333 | 136510 | 133300.266 | 19507.356 | 54144.7298 | 7923.619 | 1998711.4327 | 292494.356 | 986963.0632 | 144433.619 | 3101.5817 | 453.89 | 9900 | 1448.7805 | 13001.5817 | 1902.6705 | 0 | 0 | 14549073.5221 | 2129132.7106 | 2809269.7398 | 411112.6449 | 6833333.3333 | 18831363.7854 | 21382406.8555 | 21640633.5252
176-194R | oh | 3 | 8.9928 | 8.9928 | 8.461 | 8.461 | 11.241 | 34243.44 | 4047.2168 | 65604 | 7753.7073 | 43477.5 | 5138.5862 | 164340 | 19423.2708 | 307664.94 | 36362.7811 | 2587200 | 305780.0063 | 4730891.55 | 559141.948 | 1618409.408 | 191279.0812 | 6349300.958 | 750421.0292 | 8936500.958 | 1056201.0355 | 1250000 | 147736.9387 | 10494165.898 | 1240300.7553 | 115481.52 | 13648.709 | 40055.4 | 4734.1297 | 155536.92 | 18382.8387 | 2055004 | 242880 | 37228.3333 | 4400 | 2092232.3333 | 247280 | 2247769.2533 | 265662.8387 | 454410 | 53706.5139 | 2736558 | 323432.5612 | 138847.5 | 16410.3237 | 27225 | 3217.7105 | 304516.6667 | 35990.6881 | 24200 | 2860.1871 | 599500 | 70854.6358 | 4285257.1667 | 506472.6203 | 2309738.8708 | 272987 | 1155009.0417 | 136510 | 164944.4121 | 19494.706 | 67021.4239 | 7921.232 | 2474683.2829 | 292481.706 | 1222030.4656 | 144431.232 | 3840.3564 | 453.89 | 9900 | 1170.0766 | 13740.3564 | 1623.9666 | 0 | 0 | 17267846.704 | 2040879.0482 | 3469799.7189 | 410094.0707 | 8460984.8485 | 22481919.7398 | 25728831.5525 | 25951719.4588
176-197F | oh | 3 | 21.4011 | 21.4011 | 12.7636 | 12.7636 | 16.5527 | 55237.93 | 4327.758 | 105825.5 | 8291.1717 | 66852.5 | 5237.7315 | 265096.0714 | 20769.6352 | 493012.0014 | 38626.2964 | 4173400 | 326975.7835 | 7631378.6312 | 597900.0352 | 2610648.5093 | 204537.9886 | 10242027.1406 | 802438.0238 | 14415427.1406 | 1129413.8073 | 3175000 | 248753.5613 | 18083439.142 | 1416793.665 | 186282.69 | 14594.7976 | 126056.7 | 9876.2372 | 312339.39 | 24471.0348 | 3100032 | 242880 | 56160 | 4400 | 3156192 | 247280 | 3468531.39 | 271751.0348 | 1057320 | 82838.4615 | 6367416 | 498871.6239 | 323070 | 25311.7521 | 66330 | 5196.7949 | 741913.3333 | 58127.113 | 58960 | 4619.3732 | 1460600 | 114434.4729 | 10075609.3333 | 789399.5916 | 3484306.8 | 272987 | 1742364 | 136510 | 247451.7708 | 19387.247 | 100858.5864 | 7902.026 | 3731758.5708 | 292374.247 | 1843222.5864 | 144412.026 | 5793.2869 | 453.89 | 9900 | 775.641 | 15693.2869 | 1229.531 | 0 | 0 | 31906500.3331 | 2499797.0346 | 5311753.9764 | 416163.0608 | 12763636.3636 | 33105344.7243 | 44670136.6967 | 38417098.7007
176-200F | oh | 3 | 3.9314 | 3.9314 | 1.1462 | 1.1462 | 1.4898 | 5503.41 | 4801.3888 | 10543.5 | 9198.5592 | 2805 | 2447.191 | 26411.7857 | 23042.6683 | 45263.6957 | 39489.8072 | 415800 | 362760.0793 | 760321.8562 | 663334.3359 | 260101.512 | 226922.6674 | 1020423.3683 | 890257.0034 | 1436223.3683 | 1253017.0827 | 150000 | 130865.8295 | 1631487.064 | 1423372.7194 | 18559.53 | 16192.0553 | 16493.4 | 14389.4831 | 35052.93 | 30581.5384 | 278392 | 242880 | 5043.3333 | 4400 | 283435.3333 | 247280 | 318488.2633 | 277861.5384 | 81180 | 70824.5869 | 488884 | 426521.4012 | 24805 | 21640.846 | 3465 | 3023.0007 | 38756.6667 | 33812.8222 | 3080 | 2687.1117 | 76300 | 66567.0853 | 716470.6667 | 625076.8539 | 312901.0083 | 272987 | 156469.4167 | 136510 | 22340.4158 | 19490.647 | 9077.5965 | 7919.648 | 335241.4242 | 292477.647 | 165547.0132 | 144429.648 | 520.2542 | 453.89 | 9900 | 8637.1447 | 10420.2542 | 9091.0347 | 0 | 0 | 2693619.409 | 2350018.2551 | 484035.2765 | 422291.1864 | 1146212.1212 | 2979650.8287 | 3839831.5302 | 3463686.1053
182-2240F | oh | 2 | 35.0288 | 28.4187 | 10.7377 | 13.7413 | 18.1889 | 47084.73 | 3426.5151 | 90205.5 | 6564.5594 | 51425 | 3742.3712 | 162383.5714 | 11817.2018 | 351098.8014 | 25550.6474 | 3557400 | 258884.0312 | 6504975.8812 | 473389.0985 | 2225312.936 | 161943.5497 | 8730288.8173 | 635332.6482 | 12287688.8173 | 894216.6794 | 2025000 | 147366.0997 | 14663787.6187 | 1067133.4265 | 158787.09 | 11555.4736 | 126056.7 | 9173.5725 | 284843.79 | 20729.0461 | 3337484 | 242880 | 60461.6667 | 4400 | 3397945.6667 | 247280 | 3682789.4567 | 268009.0461 | 1392930 | 101368.2278 | 8388534 | 610461.9941 | 425617.5 | 30973.6252 | 52470 | 3818.4194 | 586886.6667 | 42709.7279 | 46640 | 3394.1506 | 1155400 | 84082.3662 | 12048478.1667 | 876808.5112 | 2931249.6146 | 213316.9497 | 1465801.9792 | 106671.3682 | 181338.2488 | 13196.5978 | 80143.2252 | 5832.2936 | 3112587.8634 | 226513.5474 | 1545945.2044 | 112503.6618 | 6237.0332 | 453.89 | 9900 | 720.4565 | 16137.0332 | 1174.3465 | 0 | 0 | 29840990.6819 | 2171629.8316 | 5228734.661 | 380512.7079 | 13741287.8788 | 36377779.9933 | 43582278.5607 | 41606514.6543
182-2250 | oh | 2 | 1.5445 | 1.5445 | 1.2528 | 1.2528 | 1.5954 | 5503.41 | 4392.7445 | 10543.5 | 8415.6735 | 10285 | 8209.3424 | 26411.7857 | 21081.516 | 52743.6957 | 42099.2764 | 415800 | 331885.7143 | 760321.8562 | 606878.2163 | 260101.512 | 207609.3701 | 1020423.3683 | 814487.5864 | 1436223.3683 | 1146373.3007 | 550000 | 439002.2676 | 2038967.064 | 1627474.8447 | 18559.53 | 14813.9559 | 4123.35 | 3291.2 | 22682.88 | 18105.1559 | 304290 | 242880 | 5512.5 | 4400 | 309802.5 | 247280 | 332485.38 | 265385.1559 | 21780 | 17384.4898 | 131164 | 104693.2608 | 6655 | 5311.9274 | 2475 | 1975.5102 | 27683.3333 | 22096.4475 | 2200 | 1756.0091 | 54500 | 43501.1338 | 246457.3333 | 196718.7785 | 342009.2812 | 272987 | 171025.3125 | 136510 | 21235.6108 | 16949.966 | 9365.1862 | 7475.16 | 363244.8921 | 289936.966 | 180390.4987 | 143985.16 | 568.652 | 453.89 | 9900 | 7902.0408 | 10468.652 | 8355.9308 | 0 | 0 | 2659137.9413 | 2122486.5201 | 512875.8787 | 409370.3159 | 1252840.9091 | 3190752.4405 | 3911978.8504 | 3703628.3193
182-2252R | oh | 2 | 3.5521 | 3.5521 | 3.4146 | 3.4146 | 4.6021 | 16714.06 | 4894.9047 | 32021 | 9377.7181 | 29452.5 | 8625.5034 | 80213.5714 | 23491.4669 | 158401.1314 | 46389.5931 | 1262800 | 369825.5034 | 2309125.6375 | 676254 | 789937.9253 | 231342.4064 | 3099063.5628 | 907596.4064 | 4361863.5628 | 1277421.9098 | 1400000 | 410006.1013 | 5920264.6943 | 1733817.6042 | 56365.98 | 16507.4255 | 17082.45 | 5002.7919 | 73448.43 | 21510.2174 | 829334 | 242880 | 15024.1667 | 4400 | 844358.1667 | 247280 | 917806.5967 | 268790.2174 | 418770 | 122641.6107 | 2521926 | 738575.0336 | 127957.5 | 37473.8255 | 11385 | 3334.2282 | 127343.3333 | 37293.9597 | 10120 | 2963.7584 | 250700 | 73420.3783 | 3468201.8333 | 1015702.7944 | 932136.8604 | 272987 | 466124.7708 | 136510 | 57842.5909 | 16939.868 | 25519.5237 | 7473.686 | 989979.4514 | 289926.868 | 491644.2945 | 143983.686 | 1549.8452 | 453.89 | 9900 | 2899.3289 | 11449.8452 | 3353.2189 | 0 | 0 | 10389895.8242 | 3042800.4854 | 1409450.8912 | 412773.9034 | 3414583.3333 | 9204108.3374 | 13804479.1575 | 10613559.2285
183-440 | oh | 2 | 14.5574 | 9.6042 | 1.6422 | 2.2623 | 2.7037 | 14471.93 | 6396.9686 | 27725.5 | 12255.3905 | 27582.5 | 12192.1808 | 48910.7143 | 21619.8051 | 118690.6443 | 52464.3451 | 1093400 | 483311.1762 | 1999364.8813 | 883771.1656 | 683970.6427 | 302332.7747 | 2683335.5239 | 1186103.9402 | 3776735.5239 | 1669415.1165 | 725000 | 320468.8154 | 4620426.1682 | 2042348.2769 | 48804.69 | 21572.9396 | 89535.6 | 39577.0589 | 138340.29 | 61149.9984 | 549470 | 242880 | 9954.1667 | 4400 | 559424.1667 | 247280 | 697764.4567 | 308429.9984 | 164340 | 72642.545 | 989692 | 437469.5488 | 50215 | 22196.3332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1204247 | 532308.427 | 448308.7646 | 198164.1086 | 224181.4792 | 99094.0318 | 23491.5455 | 10383.8728 | 11508.9099 | 5087.2369 | 471800.31 | 208547.9813 | 235690.3891 | 104181.2687 | 1026.8402 | 453.89 | 9900 | 4376.0569 | 10926.8402 | 4829.9469 | 0 | 0 | 6307400.3184 | 2788034.6322 | 933454.8457 | 412611.2671 | 2262310.6061 | 5407386.5349 | 8569710.9245 | 6340841.3806
185-51F | oh | 2 | 26.5233 | 11.2871 | 7.314 | 9.0737 | 11.345 | 42600.47 | 4694.9525 | 81614.5 | 8994.6474 | 72930 | 8037.5378 | 157492.5 | 17357.0811 | 354637.47 | 39084.2189 | 3218600 | 354718.4871 | 5885454.3688 | 648629.6743 | 2013378.3707 | 221892.2916 | 7898832.7394 | 870521.9659 | 11117432.7394 | 1225240.453 | 3125000 | 344402.9306 | 14597070.2094 | 1608727.6024 | 143664.51 | 15833.113 | 123700.5 | 13632.9007 | 267365.01 | 29466.0138 | 2203814 | 242880 | 39924.1667 | 4400 | 2243738.1667 | 247280 | 2511103.1767 | 276746.0138 | 757350 | 83466.739 | 4560930 | 502655.2506 | 231412.5 | 25503.7258 | 7920 | 872.8548 | 88586.6667 | 9763.0424 | 7040 | 775.8709 | 174400 | 19220.4387 | 5827639.1667 | 642257.9223 | 1996631.0542 | 220046.5876 | 998436.2083 | 110036.594 | 104619.2193 | 11529.973 | 51257.2691 | 5649.0092 | 2101250.2734 | 231576.5606 | 1049693.4775 | 115685.6031 | 4118.45 | 453.89 | 9900 | 1091.0685 | 14018.45 | 1544.9585 | 0 | 0 | 22539978.0995 | 2484107.0439 | 3560796.6541 | 392431.6169 | 9073674.2424 | 22689988.6106 | 31613652.3419 | 26250785.2648
197-1150F | oh | 2 | 1.5936 | 1.4818 | 1.3604 | 1.3604 | 1.7749 | 5911.07 | 4345.0438 | 11324.5 | 8324.2879 | 12622.5 | 9278.4074 | 28368.2143 | 20852.5924 | 58226.2843 | 42800.3315 | 446600 | 328281.7764 | 816641.9938 | 600288.1424 | 279368.2907 | 205354.9457 | 1096010.2844 | 805643.0881 | 1542610.2844 | 1133924.8645 | 600000 | 441041.3476 | 2200836.5687 | 1617766.5436 | 19934.31 | 14653.0916 | 589.05 | 432.9923 | 20523.36 | 15086.0839 | 330418 | 242880 | 5985.8333 | 4400 | 336403.8333 | 247280 | 356927.1933 | 262366.0839 | 2970 | 2183.1547 | 17886 | 13147.4426 | 907.5 | 667.075 | 1980 | 1455.4364 | 22146.6667 | 16279.3262 | 1760 | 1293.7213 | 43600 | 32049.0046 | 91250.1667 | 67075.1608 | 371376.0646 | 272987 | 185710.4792 | 136510 | 19555.8971 | 14374.932 | 9551.1004 | 7020.717 | 390931.9617 | 287361.932 | 195261.5796 | 143530.717 | 617.4795 | 453.89 | 9900 | 7277.1822 | 10517.4795 | 7731.0722 | 0 | 0 | 2693536.1765 | 1979934.7086 | 552188.7729 | 405896.8009 | 1360416.6667 | 3549881.1948 | 4053952.8432 | 4102069.9677
198-37R | oh | 2 | 10.0816 | 7.6434 | 3.9803 | 5.9282 | 7.4994 | 25478.75 | 4297.8755 | 48812.5 | 8233.9222 | 37867.5 | 6387.6681 | 84126.4286 | 14190.8419 | 196285.1786 | 33110.3077 | 1925000 | 324718.0601 | 3520008.5938 | 593771.6167 | 1204173.6667 | 203125.6816 | 4724182.2604 | 796897.2983 | 6649182.2604 | 1121615.3585 | 1125000 | 189770.2949 | 7970467.439 | 1344495.9611 | 85923.75 | 14494.0226 | 40644.45 | 6856.0971 | 126568.2 | 21350.1197 | 1439846 | 242880 | 26084.1667 | 4400 | 1465930.1667 | 247280 | 1592498.3667 | 268630.1197 | 391050 | 65964.1545 | 2354990 | 397250.7971 | 119487.5 | 20155.7139 | 3465 | 584.4925 | 38756.6667 | 6537.6569 | 3080 | 519.5489 | 76300 | 12870.6431 | 2987129.1667 | 503883.0069 | 1086570.9833 | 183287.9075 | 543351.1667 | 91655.0321 | 55869.8101 | 9424.3825 | 27706.3998 | 4673.6459 | 1142440.7934 | 192712.29 | 571057.5665 | 96328.678 | 2690.7596 | 453.89 | 9900 | 1669.9786 | 12590.7596 | 2123.8686 | 0 | 0 | 12112628.1587 | 2043215.1266 | 2163555.9331 | 364958.7977 | 5928219.697 | 14998753.7548 | 18040847.8557 | 17162309.6879
204-32R | oh | 2 | 21.467 | 18.9631 | 17.4794 | 17.7195 | 23.6353 | 68894.54 | 3888.0618 | 131989 | 7448.7962 | 123420 | 6965.2048 | 316941.4286 | 17886.5822 | 641244.9686 | 36188.645 | 5205200 | 293755.3415 | 9518103.2375 | 537153.936 | 3256085.5947 | 183757.1152 | 12774188.8322 | 720911.0511 | 17979388.8322 | 1014666.3927 | 2300000 | 129800.4468 | 20920633.8007 | 1180655.4844 | 232337.82 | 13111.9795 | 24151.05 | 1362.9639 | 256488.87 | 14474.9434 | 4303714 | 242880 | 77965.8333 | 4400 | 4381679.8333 | 247280 | 4638168.7033 | 261754.9434 | 326700 | 18437.3069 | 1967460 | 111033.5596 | 99825 | 5633.6216 | 17325 | 977.736 | 193783.3333 | 10936.1579 | 15400 | 869.0986 | 381500 | 21529.9437 | 3001993.3333 | 169417.4243 | 4771636.9729 | 269287.2221 | 2386106.8958 | 134659.8875 | 251326.6589 | 14183.6142 | 122730.8791 | 6926.3143 | 5022963.6318 | 283470.8363 | 2508837.7749 | 141586.2018 | 8042.7073 | 453.89 | 9900 | 558.7063 | 17942.7073 | 1012.5963 | 0 | 0 | 28963533.4732 | 1634556.3413 | 7147006.4782 | 403341.1452 | 17719507.5758 | 47270667.9878 | 46683041.049 | 54417674.466
206-1817 | oh | 2 | 13.2672 | 7.3169 | 4.4545 | 8.0133 | 9.9195 | 44027.28 | 5494.3049 | 84348 | 10526.0563 | 92565 | 11551.4819 | 103690.7143 | 12939.8953 | 324630.9943 | 40511.7384 | 3326400 | 415112.0775 | 6082574.85 | 759063.9378 | 2080812.096 | 259671.1857 | 8163386.946 | 1018735.1235 | 11489786.946 | 1433847.201 | 2125000 | 265185.5353 | 13939417.9403 | 1739544.4747 | 148476.24 | 18528.8241 | 91302.75 | 11393.9617 | 239778.99 | 29922.7858 | 1946260 | 242880 | 35258.3333 | 4400 | 1981518.3333 | 247280 | 2221297.3233 | 277202.7858 | 599940 | 74868.4283 | 3612972 | 450874.3125 | 183315 | 22876.4642 | 9900 | 1235.4526 | 110733.3333 | 13818.7662 | 8800 | 1098.1801 | 218000 | 27204.9161 | 4743660.3333 | 591976.52 | 1216033 | 151752.641 | 608090 | 75885.4928 |  |  |  |  | 1216033 | 151752.641 | 608090 | 75885.4928 | 3637.1375 | 453.89 | 9900 | 1235.4526 | 13537.1375 | 1689.3426 | 0 | 0 | 19912648.4111 | 2484962.9783 | 2829387.3233 | 353088.2786 | 8013257.5758 | 19838989.8119 | 27925905.9869 | 22668377.1353
209-1769F | oh | 2 | 35.6822 | 21.817 | 14.8672 | 24.3042 | 28.5746 | 126782.26 | 5216.4825 | 242891 | 9993.8008 | 270682.5 | 11137.2878 | 338462.1429 | 13926.0954 | 978817.9029 | 40273.6665 | 9578800 | 394121.7212 | 17515562.7625 | 720681.4783 | 5991968.1653 | 246540.7783 | 23507530.9278 | 967222.2566 | 33086330.9278 | 1361343.9778 | 6975000 | 286987.8279 | 41040148.8307 | 1688605.4722 | 427556.58 | 17591.9045 | 246811.95 | 10155.1291 | 674368.53 | 27747.0336 | 5902996 | 242880 | 106938.3333 | 4400 | 6009934.3333 | 247280 | 6684302.8633 | 275027.0336 | 2038410 | 83870.804 | 12275758 | 505088.6199 | 622847.5 | 25627.1901 | 76230 | 3136.4992 | 852646.6667 | 35082.3247 | 67760 | 2787.9993 | 1678600 | 69066.3466 | 17612252.1667 | 724659.784 | 4058561.8396 | 166990.3723 | 2029526.2292 | 83505.2794 |  |  |  |  | 4058561.8396 | 166990.3723 | 2029526.2292 | 83505.2794 | 11031.4182 | 453.89 | 9900 | 407.3376 | 20931.4182 | 861.2276 | 0 | 0 | 62731894.2551 | 2581116.856 | 8713829.0925 | 358532.3131 | 24304166.6667 | 57149204.9062 | 87036060.9218 | 65863033.9987
210-172R | oh | 2 | 6.6767 | 6.6767 | 6.4924 | 6.4924 | 0.27292 | 21605.98 | 3327.8756 | 41393 | 6375.5846 | 38335 | 5904.5741 | 103690.7143 | 15971.0318 | 205024.6943 | 31579.0661 | 1632400 | 251431.5053 | 2984967.2875 | 459761.5892 | 1021139.2693 | 157281.6611 | 4006106.5568 | 617043.2503 | 5638506.5568 | 868474.7555 | 1800000 | 277246.2077 | 7643531.2511 | 1177300.0293 | 72863.34 | 11222.8248 | 7657.65 | 1179.4747 | 80520.99 | 12402.2995 | 1576880 | 242880 | 28566.6667 | 4400 | 1605446.6667 | 247280 | 1685967.6567 | 259682.2995 | 202950 | 31259.5099 | 1222210 | 188251.7153 | 62012.5 | 9551.5169 | 11385 | 1753.5823 | 127343.3333 | 19614.1424 | 10120 | 1558.7398 | 250700 | 38614.2357 | 1886720.8333 | 290603.4422 | 1772347.4167 | 272987 | 886280.8333 | 136510 | 150349.6518 | 23157.706 | 55613.7295 | 8565.942 | 1922697.0685 | 296144.706 | 941894.5628 | 145075.942 | 2946.8464 | 453.89 | 9900 | 1524.8541 | 12846.8464 | 1978.7441 | 0 | 0 | 11465795.9994 | 1766026.9217 | 2627862.2195 | 404758.2415 | 6492424.2424 | 545840.9091 | 17958220.2418 | 3173703.1286
210-392R | oh | 2 | 10.9206 | 10.9206 | 10.6015 | 10.6015 | 0.68811 | 39543.02 | 3729.9404 | 75757 | 7145.8654 | 61242.5 | 5776.7686 | 189773.5714 | 17900.6084 | 366316.0914 | 34553.1828 | 2987600 | 281808.7752 | 5463053.3375 | 515308.7327 | 1868877.5307 | 176284.0032 | 7331930.8682 | 691592.7359 | 10319530.8682 | 973401.5111 | 2950000 | 278262.1123 | 13635846.9596 | 1286216.8063 | 133353.66 | 12578.736 | 33575.85 | 3167.0803 | 166929.51 | 15745.8163 | 2574896 | 242880 | 46646.6667 | 4400 | 2621542.6667 | 247280 | 2788472.1767 | 263025.8163 | 356400 | 33617.8362 | 2146320 | 202454.0803 | 108900 | 10272.1166 | 31185 | 2941.5607 | 348810 | 32901.9008 | 27720 | 2614.7206 | 686700 | 64773.7602 | 3706035 | 349575.9754 | 2894075.8167 | 272987 | 1447212.8333 | 136510 | 245737.9053 | 23179.508 | 90841.8178 | 8568.758 | 3139813.7219 | 296166.508 | 1538054.6511 | 145078.758 | 4811.9217 | 453.89 | 9900 | 933.8288 | 14711.9217 | 1387.7188 | 0 | 0 | 20496407.6032 | 1933347.0085 | 4326526.8278 | 408104.5743 | 10601515.1515 | 1376215.9091 | 31097922.7548 | 5702742.7369
210-394R | oh | 2 | 3.9195 | 3.9195 | 3.6237 | 3.6237 | 0.13327 | 14879.59 | 4106.2162 | 28506.5 | 7866.7391 | 22907.5 | 6321.6223 | 71409.6429 | 19706.419 | 137703.2329 | 38000.9967 | 1124200 | 310237.6 | 2055685.0188 | 567292.9963 | 703237.4213 | 194067.5056 | 2758922.4401 | 761360.5019 | 3883122.4401 | 1071598.1019 | 1050000 | 289761.1457 | 5070825.6729 | 1399360.2442 | 50179.47 | 13847.6769 | 11191.95 | 3088.5641 | 61371.42 | 16936.2409 | 880118 | 242880 | 15944.1667 | 4400 | 896062.1667 | 247280 | 957433.5867 | 264216.2409 | 235620 | 65022.4011 | 1418956 | 391579.3488 | 71995 | 19867.9559 | 11385 | 3141.8387 | 127343.3333 | 35142.0478 | 10120 | 2792.7455 | 250700 | 69183.9231 | 2126119.3333 | 586730.2608 | 989215.9604 | 272987 | 494667.7708 | 136510 | 84489.2154 | 23315.897 | 31135.7687 | 8592.32 | 1073705.1758 | 296302.897 | 525803.5395 | 145102.32 | 1644.7495 | 453.89 | 9900 | 2732.0337 | 11544.7495 | 3185.9237 | 0 | 0 | 8282194.9316 | 2285579.3257 | 1483237.1262 | 409318.5609 | 3623674.2424 | 266532.9545 | 11905869.174 | 1749770.0807
210-9R | oh | 2 | 7.196 | 7.196 | 2.7176 | 2.7176 | 0.74856 | 14675.76 | 5400.2378 | 28116 | 10345.8415 | 25712.5 | 9461.4259 | 70431.4286 | 25916.6453 | 138935.6886 | 51124.1505 | 1108800 | 408005.0178 | 2027524.95 | 746068.1397 | 693604.032 | 255225.4017 | 2721128.982 | 1001293.5414 | 3829928.982 | 1409298.5591 | 1250000 | 459962.3667 | 5218864.6706 | 1920385.0764 | 49492.08 | 18211.5954 | 35932.05 | 13221.9126 | 85424.13 | 31433.508 | 660054 | 242880 | 11957.5 | 4400 | 672011.5 | 247280 | 757435.63 | 278713.508 | 166320 | 61200.7527 | 1001616 | 368564.5327 | 50820 | 18700.23 | 26235 | 9653.6902 | 293443.3333 | 107978.3121 | 23320 | 8581.0579 | 577700 | 212576.2074 | 2139454.3333 | 787254.7829 | 741873.1937 | 272987 | 370981.4375 | 136510 | 63359.1754 | 23314.269 | 23349.7391 | 8592.001 | 805232.3691 | 296301.269 | 394331.1766 | 145102.001 | 1233.4977 | 453.89 | 9900 | 3642.9019 | 11133.4977 | 4096.7919 | 0 | 0 | 8174684.8707 | 3008037.9202 | 1151766.8066 | 423815.509 | 2717613.6364 | 1497114.1598 | 10892298.507 | 2648880.9664
211-279R | oh | 2 | 15.9898 | 15.9898 | 15.3767 | 15.3767 | 1.2206 | 52995.8 | 3446.4992 | 101530 | 6602.8452 | 88357.5 | 5746.1922 | 254335.7143 | 16540.3265 | 497219.0143 | 32335.8632 | 4004000 | 260393.8957 | 7321617.875 | 476150.0004 | 2504681.2267 | 162888.0375 | 9826299.1017 | 639038.0379 | 13830299.1017 | 899431.9336 | 4200000 | 273140.4501 | 18527518.116 | 1204908.2468 | 178721.4 | 11622.8675 | 28274.4 | 1838.7815 | 206995.8 | 13461.649 | 3734694 | 242880 | 67657.5 | 4400 | 3802351.5 | 247280 | 4009347.3 | 260741.649 | 430650 | 28006.6511 | 2593470 | 168662.2769 | 131587.5 | 8557.5879 | 37620 | 2446.558 | 420786.6667 | 27365.2046 | 33440 | 2174.7183 | 828400 | 53873.7021 | 4475954.1667 | 291086.6989 | 4197640.4437 | 272987 | 2099073.9375 | 136510 | 360327.2689 | 23433.322 | 132433.9745 | 8612.637 | 4557967.7127 | 296420.322 | 2231507.912 | 145122.637 | 6979.3324 | 453.89 | 9900 | 643.8311 | 16879.3324 | 1097.7211 | 0 | 0 | 27578319.3277 | 1793512.9888 | 6240855.212 | 405864.286 | 15376704.5455 | 2441186.3636 | 42955023.8732 | 8682041.5756
211-312R | oh | 2 | 19.8839 | 19.8839 | 18.1587 | 18.1587 | 23.0116 | 74194.12 | 4085.8691 | 142142 | 7827.7578 | 140717.5 | 7749.3106 | 356070 | 19608.7695 | 713123.62 | 39271.7069 | 5605600 | 308700.3066 | 10250265.025 | 564481.9388 | 3506553.7173 | 193105.8598 | 13756818.7423 | 757587.7987 | 19362418.7423 | 1066288.1053 | 6925000 | 381359.6445 | 27000542.3623 | 1486919.4567 | 250209.96 | 13779.0587 | 68329.8 | 3762.921 | 318539.76 | 17541.9797 | 4410388 | 242880 | 79898.3333 | 4400 | 4490286.3333 | 247280 | 4808826.0933 | 264821.9797 | 313830 | 17282.6133 | 1889954 | 104079.738 | 95892.5 | 5280.7985 | 69300 | 3816.3499 | 775133.3333 | 42686.5809 | 61600 | 3392.3111 | 1526000 | 84036.7968 | 4731709.8333 | 260575.1885 | 4957092.3458 | 272987 | 2478845.7917 | 136510 | 425202.3511 | 23415.887 | 156337.2686 | 8609.491 | 5382294.6969 | 296402.887 | 2635183.0602 | 145119.491 | 8242.0578 | 453.89 | 9900 | 545.1928 | 18142.0578 | 999.0828 | 0 | 0 | 37132688.9504 | 2044896.6151 | 7444009.1536 | 409941.4707 | 18158712.1212 | 46023266.6953 | 55291401.0717 | 53467275.8489
211-771R | oh | 3 | 20.1729 | 20.1729 | 14.1159 | 14.1159 | 0.99122 | 51568.99 | 3653.2532 | 98796.5 | 6998.947 | 92097.5 | 6524.3761 | 247488.2143 | 17532.5735 | 489951.2043 | 34709.1499 | 3896200 | 276014.8124 | 7124497.3937 | 504714.0321 | 2437247.5013 | 172659.6201 | 9561744.8951 | 677373.6522 | 13457944.8951 | 953388.4646 | 4025000 | 285139.269 | 17972896.0994 | 1273236.8835 | 173909.67 | 12320.1183 | 38288.25 | 2712.4183 | 212197.92 | 15032.5366 | 3428472 | 242880 | 62110 | 4400 | 3490582 | 247280 | 3702779.92 | 262312.5366 | 1213740 | 85983.8351 | 7309412 | 517813.7627 | 370865 | 26272.8385 | 39105 | 2770.2785 | 437396.6667 | 30986.0785 | 34760 | 2462.4698 | 861100 | 61002.0931 | 10266378.6667 | 727291.3562 | 3853459.675 | 272987 | 1926962.75 | 136510 | 332441.1353 | 23550.813 | 121860.9069 | 8632.877 | 4185900.8103 | 296537.813 | 2048823.6569 | 145142.877 | 6407.07 | 453.89 | 9900 | 701.3363 | 16307.07 | 1155.2263 | 0 | 0 | 32441482.6463 | 2298221.2791 | 5751603.5769 | 407455.4136 | 14115909.0909 | 1982447.7273 | 46557391.7372 | 7734051.3042
212-1177R | oh | 2 | 13.4216 | 13.4216 | 12.4913 | 12.4913 | 16.6559 | 51161.33 | 4095.761 | 98015.5 | 7846.7089 | 21505 | 1721.5999 | 245531.7857 | 19656.2427 | 416213.6157 | 33320.3125 | 3865400 | 309447.6757 | 7068177.2562 | 565848.5598 | 2417980.7227 | 193573.3726 | 9486157.9789 | 759421.9324 | 13351557.9789 | 1068869.608 | 875000 | 70048.8219 | 14642771.5946 | 1172238.7425 | 172534.89 | 13812.418 | 45356.85 | 3631.0788 | 217891.74 | 17443.4968 | 3033884 | 242880 | 54961.6667 | 4400 | 3088845.6667 | 247280 | 3306737.4067 | 264723.4968 | 379170 | 30354.7563 | 2283446 | 182803.0882 | 115857.5 | 9275.0644 | 51480 | 4121.2724 | 575813.3333 | 46097.195 | 45760 | 3663.3532 | 1133600 | 90751.2509 | 4585126.8333 | 367065.9805 | 3409959.2042 | 272987 | 1705185.7083 | 136510 | 212170.7203 | 16985.496 | 93437.5814 | 7480.22 | 3622129.9245 | 289972.496 | 1798623.2897 | 143990.22 | 5669.6707 | 453.89 | 9900 | 792.5524 | 15569.6707 | 1246.4424 | 0 | 0 | 22865598.0231 | 1830523.6614 | 5105360.6964 | 408713.7168 | 12491287.8788 | 33311761.2167 | 35356885.9019 | 38417121.9131
212-1204R | oh | 2 | 10.4665 | 10.4665 | 10.0072 | 10.0072 | 13.5758 | 37912.38 | 3788.5114 | 72633 | 7258.0764 | 24777.5 | 2475.9681 | 181947.8571 | 18181.7004 | 317270.7371 | 31704.2563 | 2864400 | 286233.9983 | 5237772.7875 | 523400.5889 | 1791810.416 | 179052.1783 | 7029583.2035 | 702452.7672 | 9893983.2035 | 988686.7655 | 1075000 | 107422.6882 | 11286253.9406 | 1127813.71 | 127854.54 | 12776.259 | 35343 | 3531.7582 | 163197.54 | 16308.0172 | 2430548 | 242880 | 44031.6667 | 4400 | 2474579.6667 | 247280 | 2637777.2067 | 263588.0172 | 258390 | 25820.4171 | 1556082 | 155496.2898 | 78952.5 | 7889.5719 | 42075 | 4204.4741 | 470616.6667 | 47027.8209 | 37400 | 3737.3103 | 926500 | 92583.368 | 3370016.1667 | 336759.2521 | 2731834.6792 | 272987 | 1366082.4583 | 136510 | 185525.8864 | 18539.246 | 77589.5208 | 7753.372 | 2917360.5656 | 291526.246 | 1443671.9791 | 144263.372 | 4542.1666 | 453.89 | 9900 | 989.288 | 14442.1666 | 1443.178 | 0 | 0 | 17588072.8395 | 1757542.386 | 4081449.1858 | 407851.3892 | 10007196.9697 | 27151662.2613 | 27595269.8092 | 31233111.4471
212-638R | oh | 2 | 4.293 | 4.293 | 4.2816 | 4.2816 | 6.1551 | 15898.74 | 3713.2458 | 30459 | 7113.8815 | 2805 | 655.1245 | 76300.7143 | 17820.488 | 125463.4543 | 29302.7398 | 1201200 | 280547.4411 | 2196485.3625 | 513002.2875 | 751404.368 | 175494.9822 | 2947889.7305 | 688497.2697 | 4149089.7305 | 969044.7108 | 75000 | 17516.6984 | 4349553.1848 | 1015864.149 | 53616.42 | 12522.4354 | 3534.3 | 825.4569 | 57150.72 | 13347.8923 | 1039922 | 242880 | 18839.1667 | 4400 | 1058761.1667 | 247280 | 1115911.8867 | 260627.8923 | 42570 | 9942.478 | 256366 | 59875.8119 | 13007.5 | 3037.9794 | 3960 | 924.8817 | 44293.3333 | 10344.9728 | 3520 | 822.117 | 87200 | 20366.0813 | 450916.8333 | 105314.3221 | 1168828.9979 | 272987 | 584485.1458 | 136510 | 70994.8344 | 16581.268 | 31726.1928 | 7409.842 | 1239823.8323 | 289568.268 | 616211.3387 | 143919.842 | 1943.3885 | 453.89 | 9900 | 2312.2042 | 11843.3885 | 2766.0942 | 0 | 0 | 6052137.2389 | 1413512.8333 | 1732123.2253 | 404547.7343 | 4281628.7879 | 12310146.8599 | 10333766.0268 | 14042270.0852
212-725R | oh | 3 | 11.9794 | 11.9794 | 11.865 | 11.865 | 14.4269 | 38320.04 | 3229.6808 | 73414 | 6187.4618 | 21972.5 | 1851.8812 | 183904.2857 | 15499.7786 | 317610.8257 | 26768.8023 | 2895200 | 244012.5784 | 5294092.925 | 446195.5184 | 1811077.1947 | 152640.7903 | 7105170.1197 | 598836.3087 | 10000370.1197 | 842848.8871 | 925000 | 77960.6366 | 11242980.9454 | 947578.326 | 129229.32 | 10891.6757 | 24740.1 | 2085.1394 | 153969.42 | 12976.8151 | 2881762 | 242880 | 52205.8333 | 4400 | 2933967.8333 | 247280 | 3087937.2533 | 260256.8151 | 1769130 | 149105.4065 | 10654094 | 897945.8924 | 540567.5 | 45559.9853 | 27720 | 2336.2906 | 310053.3333 | 26131.8435 | 24640 | 2076.7028 | 610400 | 51445.592 | 13936604.8333 | 1174601.7131 | 3238980.4146 | 272987 | 1619685.9792 | 136510 | 196752.17 | 16582.621 | 87916.7116 | 7409.776 | 3435732.5846 | 289569.621 | 1707602.6907 | 143919.776 | 5385.3877 | 453.89 | 9900 | 834.3895 | 15285.3877 | 1288.2795 | 0 | 0 | 28630603.751 | 2413037.9396 | 4795539.9441 | 404176.5911 | 11864962.1212 | 28853803.9053 | 40495565.8722 | 33649343.8494
212-734R | oh | 2 | 17.904 | 17.904 | 17.882 | 17.882 | 26.0588 | 52995.8 | 2963.6382 | 101530 | 5677.7741 | 1870 | 104.5744 | 254335.7143 | 14222.9956 | 410731.5143 | 22968.9822 | 4004000 | 223912.2192 | 7321617.875 | 409440.4861 | 2504681.2267 | 140067.1158 | 9826299.1017 | 549507.602 | 13830299.1017 | 773419.8212 | 50000 | 2796.1066 | 14291030.616 | 799184.9101 | 178721.4 | 9994.4818 | 14726.25 | 823.5233 | 193447.65 | 10818.0051 | 4343182 | 242880 | 78680.8333 | 4400 | 4421862.8333 | 247280 | 4615310.4833 | 258098.0051 | 29700 | 1660.8873 | 178860 | 10002.2326 | 9075 | 507.4934 | 23760 | 1328.7099 | 265760 | 14861.866 | 21120 | 1181.0754 | 523200 | 29258.4598 | 1051475 | 58800.7244 | 4881555.6021 | 272987 | 2441072.8542 | 136510 | 303940.5185 | 16997.002 | 133793.8066 | 7482.035 | 5185496.1206 | 289984.002 | 2574866.6607 | 143992.035 | 8116.4644 | 453.89 | 9900 | 553.6291 | 18016.4644 | 1007.5191 | 0 | 0 | 20546018.201 | 1148977.1556 | 7190177.1441 | 402090.0401 | 17882007.5758 | 52117628.1196 | 38428025.7767 | 59307805.2637
212-739R | oh | 3 | 9.8858 | 9.8858 | 9.5873 | 9.5873 | 8.5856 | 36893.23 | 3848.1313 | 70680.5 | 7372.2969 | 35530 | 3705.9402 | 177056.7857 | 18467.8262 | 320160.5157 | 33394.1946 | 2787400 | 290738.4682 | 5096972.4437 | 531637.3541 | 1743643.4693 | 181869.9259 | 6840615.9131 | 713507.28 | 9628015.9131 | 1004245.7482 | 1225000 | 127773.0586 | 11173176.4288 | 1165413.0014 | 124417.59 | 12977.3192 | 22383.9 | 2334.7423 | 146801.49 | 15312.0615 | 2328566 | 242880 | 42184.1667 | 4400 | 2370750.1667 | 247280 | 2517551.6567 | 262592.0615 | 713790 | 74451.5359 | 4298602 | 448363.6941 | 218102.5 | 22749.0804 | 24750 | 2581.5373 | 276833.3333 | 28874.9728 | 22000 | 2294.6998 | 545000 | 56845.973 | 6099077.8333 | 636161.4935 | 2617211.1604 | 272987 | 1308763.7708 | 136510 | 158931.0626 | 16577.231 | 71034.0237 | 7409.171 | 2776142.223 | 289564.231 | 1379797.7945 | 143919.171 | 4351.5844 | 453.89 | 9900 | 1032.6149 | 14251.5844 | 1486.5049 | 0 | 0 | 20062648.0695 | 2092625.2308 | 3897349.4512 | 406511.2325 | 9587310.6061 | 17171134.4458 | 29649958.6756 | 21068483.897
212-743R | oh | 2 | 3.7074 | 3.7074 | 3.6616 | 3.6616 | 5.1759 | 13656.61 | 3729.7316 | 26163.5 | 7145.4653 | 9817.5 | 2681.2393 | 65540.3571 | 17899.6062 | 115177.9671 | 31456.0423 | 1031800 | 281792.9964 | 1886724.6062 | 515279.88 | 645437.0853 | 176274.1329 | 2532161.6916 | 691554.0129 | 3563961.6916 | 973347.0093 | 400000 | 109243.2628 | 4079139.6587 | 1114046.3145 | 46055.13 | 12578.0317 | 4123.35 | 1126.1205 | 50178.48 | 13704.1522 | 889318 | 242880 | 16110.8333 | 4400 | 905428.8333 | 247280 | 955607.3133 | 260984.1522 | 65340 | 17844.887 | 393492 | 107465.8749 | 19965 | 5452.6044 | 5445 | 1487.0739 | 60903.3333 | 16633.1971 | 4840 | 1321.8435 | 119900 | 32745.668 | 669885.3333 | 182951.1488 | 999556.3771 | 272987 | 499838.6042 | 136510 | 62229.9062 | 16995.495 | 27395.0221 | 7481.804 | 1061786.2833 | 289982.495 | 527233.6263 | 143991.804 | 1661.9423 | 453.89 | 9900 | 2703.7708 | 11561.9423 | 3157.6608 | 0 | 0 | 5822373.2177 | 1590137.6191 | 1482840.9396 | 404975.9562 | 3661553.0303 | 10351881.2785 | 9483926.248 | 11834722.2181
212-758R | oh | 2 | 9.79 | 9.79 | 9.6756 | 9.6756 | 13.5687 | 37504.72 | 3876.2292 | 71852 | 7426.1272 | 7947.5 | 821.3988 | 179991.4286 | 18602.6728 | 297295.6486 | 30726.4279 | 2833600 | 292861.3542 | 5181452.65 | 535519.2122 | 1772543.6373 | 183197.8861 | 6953996.2873 | 718717.0982 | 9787596.2873 | 1011578.4524 | 400000 | 41341.2414 | 10484891.9359 | 1083646.1217 | 126479.76 | 13072.0757 | 27096.3 | 2800.4867 | 153576.06 | 15872.5624 | 2350002 | 242880 | 42572.5 | 4400 | 2392574.5 | 247280 | 2546150.56 | 263152.5624 | 206910 | 21384.7907 | 1246058 | 128783.9615 | 63222.5 | 6534.2416 | 33660 | 3478.8655 | 376493.3333 | 38911.7545 | 29920 | 3092.3249 | 741200 | 76605.3203 | 2697463.8333 | 278791.2588 | 2641304.3312 | 272987 | 1320811.8125 | 136510 | 164424.6802 | 16993.801 | 72387.8311 | 7481.507 | 2805729.0115 | 289980.801 | 1393199.6436 | 143991.507 | 4391.6436 | 453.89 | 9900 | 1023.1957 | 14291.6436 | 1477.0857 | 0 | 0 | 16002376.4244 | 1653895.2673 | 3939350.2036 | 407144.0694 | 9675568.1818 | 27137335.2852 | 25677944.6062 | 31076685.4888
212-773R | oh | 2 | 12.8958 | 12.8958 | 11.8402 | 11.8402 | 9.6318 | 47900.05 | 4045.5606 | 91767.5 | 7750.5343 | 40672.5 | 3435.1334 | 229880.3571 | 19415.3222 | 410220.4071 | 34646.5505 | 3619000 | 305654.8724 | 6617616.1562 | 558913.1311 | 2263846.4933 | 191200.8044 | 8881462.6496 | 750113.9355 | 12500462.6496 | 1055768.8078 | 1700000 | 143579.2437 | 14610683.0567 | 1233994.602 | 161536.65 | 13643.1236 | 51247.35 | 4328.2681 | 212784 | 17971.3916 | 2875736 | 242880 | 52096.6667 | 4400 | 2927832.6667 | 247280 | 3140616.6667 | 265251.3916 | 416790 | 35201.4076 | 2510002 | 211990.6993 | 127352.5 | 10755.9857 | 55935 | 4724.1794 | 625643.3333 | 52840.8215 | 49720 | 4199.2706 | 1231700 | 104027.385 | 5017142.8333 | 423739.7492 | 3232207.4417 | 272987 | 1616299.0833 | 136510 | 219509.305 | 18539.4 | 91804.0948 | 7753.625 | 3451716.7467 | 291526.4 | 1708103.1781 | 144263.625 | 5374.1264 | 453.89 | 9900 | 836.1379 | 15274.1264 | 1290.0279 | 0 | 0 | 23094816.7631 | 1950550.7791 | 4848719.8448 | 409515.0166 | 11840151.5152 | 19263624.4037 | 34934968.2782 | 24112344.2485
212-799R | oh | 2 | 5.3398 | 5.3398 | 5.2246 | 5.2246 | 7.3106 | 21605.98 | 4135.4156 | 41393 | 7922.6796 | 13090 | 2505.4448 | 103690.7143 | 19846.5516 | 179779.6943 | 34410.0916 | 1632400 | 312443.7033 | 2984967.2875 | 571327.0238 | 1021139.2693 | 195447.522 | 4006106.5568 | 766774.5458 | 5638506.5568 | 1079218.2491 | 675000 | 129195.969 | 6493286.2511 | 1242824.3096 | 72863.34 | 13946.1479 | 17671.5 | 3382.3505 | 90534.84 | 17328.4983 | 1268956 | 242880 | 22988.3333 | 4400 | 1291944.3333 | 247280 | 1382479.1733 | 264608.4983 | 106920 | 20464.6415 | 643896 | 123242.6187 | 32670 | 6253.0849 | 19800 | 3789.7484 | 221466.6667 | 42389.0379 | 17600 | 3368.6653 | 436000 | 83451.0259 | 1478352.6667 | 282958.8226 | 1426253.6708 | 272987 | 713213.0417 | 136510 | 88792.6674 | 16995.044 | 39089.7643 | 7481.837 | 1515046.3382 | 289982.044 | 752302.806 | 143991.837 | 2371.4033 | 453.89 | 9900 | 1894.8742 | 12271.4033 | 2348.7642 | 0 | 0 | 9498956.6593 | 1818113.9404 | 2134781.9793 | 408600.3353 | 5224621.2121 | 14621153.0809 | 14723577.8714 | 16755935.0602
212-880R | oh | 2 | 1.8669 | 1.8669 | 1.6392 | 1.6392 | 2.4913 | 6114.9 | 3730.4069 | 11715 | 7146.7591 | 3272.5 | 1996.3951 | 29346.4286 | 17902.8472 | 50448.8286 | 30776.4084 | 462000 | 281844.0208 | 844802.0625 | 515373.182 | 289001.68 | 176306.0509 | 1133803.7425 | 691679.2329 | 1595803.7425 | 973523.2537 | 200000 | 122010.3986 | 1846252.5711 | 1126310.0607 | 20621.7 | 12580.3092 | 1767.15 | 1078.0534 | 22388.85 | 13658.3626 | 398130 | 242880 | 7212.5 | 4400 | 405342.5 | 247280 | 427731.35 | 260938.3626 | 111870 | 68246.5165 | 673706 | 410995.688 | 34182.5 | 20853.1023 | 3960 | 2415.8059 | 44293.3333 | 27021.2363 | 3520 | 2147.383 | 87200 | 53196.5338 | 958731.8333 | 584876.2657 | 447481.5312 | 272987 | 223767.8125 | 136510 | 27865.2052 | 16999.224 | 12265.307 | 7482.475 | 475346.7365 | 289986.224 | 236033.1195 | 143992.475 | 744.0186 | 453.89 | 9900 | 6039.5147 | 10644.0186 | 6493.4047 | 0 | 0 | 3290975.1595 | 2007665.9552 | 663764.4695 | 404930.8376 | 1639204.5455 | 4982609.3741 | 4930179.7049 | 5646373.8436
212-886R | oh | 2 | 11.0627 | 11.0627 | 8.9136 | 8.9136 | 7.2075 | 30982.16 | 3475.816 | 59356 | 6659.0107 | 40672.5 | 4562.9526 | 148688.5714 | 16681.0228 | 279699.2314 | 31378.8021 | 2340800 | 262608.873 | 4280330.45 | 480200.2545 | 1464275.1787 | 164273.6049 | 5744605.6287 | 644473.8594 | 8085405.6287 | 907082.7324 | 275000 | 30851.6063 | 8640104.8601 | 969313.1409 | 104483.28 | 11721.7346 | 10013.85 | 1123.4304 | 114497.13 | 12845.165 | 2164944 | 242880 | 39220 | 4400 | 2204164 | 247280 | 2318661.13 | 260125.165 | 162360 | 18214.7884 | 977768 | 109693.5033 | 49610 | 5565.6298 | 9405 | 1055.1249 | 105196.6667 | 11801.7678 | 8360 | 937.8888 | 207100 | 23234.0643 | 1519799.6667 | 170502.7673 | 2433306.85 | 272987 | 1216800.5 | 136510 | 165363.7762 | 18551.775 | 69131.3291 | 7755.682 | 2598670.6262 | 291538.775 | 1285931.8291 | 144265.682 | 4045.8104 | 453.89 | 9900 | 1110.6578 | 13945.8104 | 1564.5478 | 0 | 0 | 12772520.9634 | 1432919.231 | 3604592.9591 | 404390.847 | 8913636.3636 | 14415072.6712 | 21686157.3271 | 18019665.6303
212-888R | oh | 2 | 7.4648 | 7.4648 | 6.9867 | 6.9867 | 9.3936 | 27313.22 | 3909.2925 | 52327 | 7489.4703 | 32725 | 4683.871 | 131080.7143 | 18761.3492 | 243445.9343 | 34843.983 | 2063600 | 295359.3928 | 3773449.2125 | 540087.0654 | 1290874.1707 | 184760.521 | 5064323.3832 | 724847.5864 | 7127923.3832 | 1020206.9792 | 1725000 | 246896.1778 | 9096369.3175 | 1301947.14 | 92110.26 | 13183.5775 | 24740.1 | 3541.0065 | 116850.36 | 16724.5839 | 1696940 | 242880 | 30741.6667 | 4400 | 1727681.6667 | 247280 | 1844532.0267 | 264004.5839 | 118800 | 17003.6324 | 715440 | 102399.653 | 36300 | 5195.5544 | 25245 | 3613.2719 | 282370 | 40415.1152 | 22440 | 3211.7972 | 555900 | 79564.977 | 1756495 | 251404.0011 | 1907289.8542 | 272987 | 953760.2083 | 136510 | 118763.7429 | 16998.443 | 52277.2801 | 7482.354 | 2026053.597 | 289985.443 | 1006037.4885 | 143992.354 | 3171.2125 | 453.89 | 9900 | 1416.9694 | 13071.2125 | 1870.8594 | 0 | 0 | 12891989.127 | 1845207.4435 | 2850569.5151 | 407996.9379 | 6986742.4242 | 18787272.6761 | 19878731.5512 | 21637842.1912
214-1122R | oh | 3 | 21.3551 | 21.3551 | 19.9235 | 19.9235 | 3.0126 | 77047.74 | 3867.1819 | 147609 | 7408.7943 | 95370 | 4786.8132 | 369765 | 18559.2532 | 689791.74 | 34622.0425 | 5821200 | 292177.8014 | 10644505.9875 | 534269.2841 | 3641421.168 | 182770.2932 | 14285927.1555 | 717039.5774 | 20107127.1555 | 1009217.3788 | 3150000 | 158104.8709 | 23946918.8955 | 1201944.2923 | 259833.42 | 13041.5649 | 86001.3 | 4316.5792 | 345834.72 | 17358.1441 | 4839016 | 242880 | 87663.3333 | 4400 | 4926679.3333 | 247280 | 5272514.0533 | 264638.1441 | 1817640 | 91231.0278 | 10946232 | 549413.5229 | 555390 | 27876.1474 | 84150 | 4223.6587 | 941233.3333 | 47242.4047 | 74800 | 3754.3633 | 1853000 | 93005.8177 | 16272445.3333 | 816746.9425 | 5438852.3583 | 272987 | 2719754.9167 | 136510 | 391911.862 | 19670.849 | 158433.0657 | 7952.076 | 5830764.2203 | 292657.849 | 2878187.9824 | 144462.076 | 9043.0705 | 453.89 | 9900 | 496.901 | 18943.0705 | 950.791 | 0 | 0 | 46069071.5197 | 2312299.8747 | 8150702.0357 | 409100.2201 | 19923484.8485 | 6025154.5455 | 65992556.3682 | 14175856.5812
214-1135R | oh | 3 | 12.2667 | 12.2667 | 11.6814 | 11.6814 | 1.2354 | 50753.67 | 4344.813 | 97234.5 | 8323.8458 | 64982.5 | 5562.8847 | 243575.3571 | 20851.4849 | 456546.0271 | 39083.0284 | 3834600 | 328264.3406 | 7011857.1188 | 600256.2597 | 2398713.944 | 205344.0388 | 9410571.0628 | 805600.2985 | 13245171.0628 | 1133864.6391 | 2975000 | 254677.5187 | 16676717.0899 | 1427625.1862 | 171160.11 | 14652.3133 | 58315.95 | 4992.1887 | 229476.06 | 19644.502 | 2837188 | 242880 | 51398.3333 | 4400 | 2888586.3333 | 247280 | 3118062.3933 | 266924.502 | 975150 | 83478.5823 | 5872570 | 502726.5735 | 297962.5 | 25507.3446 | 60885 | 5212.1145 | 681010 | 58298.4662 | 54120 | 4632.9907 | 1340700 | 114771.8149 | 9282397.5 | 794627.8868 | 3188881.0958 | 272987 | 1594633.2917 | 136510 | 177529.9718 | 15197.611 | 83705.9122 | 7165.719 | 3366411.0677 | 288184.611 | 1678339.2039 | 143675.719 | 5302.0885 | 453.89 | 9900 | 847.4983 | 15202.0885 | 1301.3883 | 0 | 0 | 29340727.7461 | 2511739.0723 | 4796401.5972 | 410600.221 | 11681439.3939 | 2470801.1364 | 41022167.14 | 7267202.7336
214-17AE | oh | 3 | 7.4663 | 7.4663 | 6.825 | 6.825 | 10.3087 | 31797.48 | 4658.9714 | 60918 | 8925.7143 | 48152.5 | 7055.3114 | 152601.4286 | 22359.1837 | 293469.4086 | 42999.1807 | 2402400 | 352000 | 4392970.725 | 643658.7143 | 1502808.736 | 220191.7562 | 5895779.461 | 863850.4705 | 8298179.461 | 1215850.4705 | 2100000 | 307692.3077 | 10691648.8696 | 1566541.9589 | 107232.84 | 15711.7714 | 10013.85 | 1467.2308 | 117246.69 | 17179.0022 | 1657656 | 242880 | 30030 | 4400 | 1687686 | 247280 | 1804932.69 | 264459.0022 | 1940400 | 284307.6923 | 11685520 | 1712164.1026 | 592900 | 86871.7949 | 16335 | 2393.4066 | 182710 | 26770.696 | 14520 | 2127.4725 | 359700 | 52703.2967 | 14792085 | 2167338.4615 | 1863136.275 | 272987 | 931680.75 | 136510 | 103749.2206 | 15201.351 | 48910.1613 | 7166.324 | 1966885.4956 | 288188.351 | 980590.9113 | 143676.324 | 3097.7992 | 453.89 | 9900 | 1450.5495 | 12997.7992 | 1904.4395 | 0 | 0 | 27463617.1644 | 4023973.2109 | 2785523.6013 | 408135.3262 | 6825000 | 20617393.7116 | 34288617.1644 | 23402917.3129
214-4R | oh | 3 | 4.0197 | 4.0197 | 3.7494 | 3.7494 | 5.7339 | 18344.7 | 4892.6613 | 35145 | 9373.4202 | 23842.5 | 6358.9635 | 88039.2857 | 23480.7005 | 165371.4857 | 44105.7455 | 1386000 | 369656.0085 | 2534406.1875 | 675944.0658 | 867005.04 | 231236.3798 | 3401411.2275 | 907180.4456 | 4787411.2275 | 1276836.4541 | 975000 | 260039.3999 | 5927782.7132 | 1580981.5995 | 61865.1 | 16499.86 | 8246.7 | 2199.4533 | 70111.8 | 18699.3132 | 910662 | 242880 | 16497.5 | 4400 | 927159.5 | 247280 | 997271.3 | 265979.3132 | 956340 | 255062.6459 | 5759292 | 1536043.9339 | 292215 | 77935.8085 | 14355 | 3828.5801 | 160563.3333 | 42823.3773 | 12760 | 3403.1823 | 316100 | 84306.107 | 7511625.3333 | 2003403.6349 | 1023546.1437 | 272987 | 511834.9375 | 136510 | 57001.9558 | 15202.825 | 26870.2206 | 7166.478 | 1080548.0995 | 288189.825 | 538705.1581 | 143676.478 | 1701.8296 | 453.89 | 9900 | 2640.4001 | 11601.8296 | 3094.2901 | 0 | 0 | 14531557.9757 | 3875669.3495 | 1535976.4581 | 409655.7912 | 3749431.8182 | 11467760.0057 | 18280989.7939 | 13003736.4638
214-536R | oh | 3 | 3.0428 | 3.0428 | 2.6684 | 2.6684 | 0.40319 | 12841.29 | 4812.4076 | 24601.5 | 9219.6692 | 8882.5 | 3328.8097 | 61627.5 | 23095.5497 | 107952.79 | 40456.4363 | 970200 | 363592.59 | 1774084.3313 | 664856.6448 | 606903.528 | 227443.4401 | 2380987.8593 | 892300.0849 | 3351187.8593 | 1255892.6749 | 225000 | 84321.1016 | 3684140.6492 | 1380670.2128 | 43305.57 | 16229.215 | 5890.5 | 2207.5264 | 49196.07 | 18436.7414 | 648094 | 242880 | 11740.8333 | 4400 | 659834.8333 | 247280 | 709030.9033 | 265716.7414 | 509850 | 191071.6162 | 3070430 | 1150675.7328 | 155787.5 | 58382.9938 | 5445 | 2040.5707 | 60903.3333 | 22824.1607 | 4840 | 1813.8406 | 119900 | 44933.7781 | 3927155.8333 | 1471742.6929 | 728430.6521 | 272987 | 364259.3542 | 136510 | 40570.8312 | 15204.343 | 19124.1738 | 7166.984 | 769001.4832 | 288191.343 | 383383.5279 | 143676.984 | 1211.147 | 453.89 | 9900 | 3710.1285 | 11111.147 | 4164.0185 | 0 | 0 | 8391409.1128 | 3144768.2671 | 1092414.4313 | 409393.7254 | 2668371.2121 | 806376.1864 | 11059780.325 | 1898790.6177
214-583R | oh | 3 | 6.2676 | 6.2676 | 6.1356 | 6.1356 | 0.69537 | 30982.16 | 5049.568 | 59356 | 9674.024 | 55632.5 | 9067.1564 | 148688.5714 | 24233.722 | 294659.2314 | 48024.4704 | 2340800 | 381510.8038 | 4280330.45 | 697621.4587 | 1464275.1787 | 238652.0849 | 5744605.6287 | 936273.5436 | 8085405.6287 | 1317784.3474 | 1800000 | 293369.5518 | 10180064.8601 | 1659178.3696 | 104483.28 | 17029.0072 | 22383.9 | 3648.1971 | 126867.18 | 20677.2043 | 1490216 | 242880 | 26996.6667 | 4400 | 1517212.6667 | 247280 | 1644079.8467 | 267957.2043 | 315810 | 51471.6879 | 1901878 | 309973.9425 | 96497.5 | 15727.4602 | 24750 | 4033.8313 | 276833.3333 | 45119.1505 | 22000 | 3585.6279 | 545000 | 88825.781 | 3182768.8333 | 518737.4812 | 1674940.6917 | 272987 | 837571.5833 | 136510 | 93294.7432 | 15205.465 | 43974.8028 | 7167.149 | 1768235.4349 | 288192.465 | 881546.3862 | 143677.149 | 2784.8902 | 453.89 | 9900 | 1613.5325 | 12684.8902 | 2067.4225 | 0 | 0 | 15143754.0185 | 2468175.7383 | 2525626.2328 | 411634.3533 | 6135606.0606 | 1390732.9545 | 21279360.0791 | 3916359.1874
214-613R | oh | 3 | 6.9066 | 6.9066 | 5.4881 | 5.4881 | 1.8498 | 32816.63 | 5979.6323 | 62870.5 | 11455.8526 | 53762.5 | 9796.2522 | 157492.5 | 28697.2564 | 306942.13 | 55928.9936 | 2479400 | 451780.1015 | 4533771.0687 | 826114.2024 | 1550975.6827 | 282608.676 | 6084746.7514 | 1108722.8784 | 8564146.7514 | 1560502.9799 | 2150000 | 391758.9813 | 11021088.8814 | 2008190.9547 | 110669.79 | 20165.5275 | 30041.55 | 5473.9754 | 140711.34 | 25639.5029 | 1332942 | 242880 | 24147.5 | 4400 | 1357089.5 | 247280 | 1497800.84 | 272919.5029 | 1432530 | 261026.276 | 8627014 | 1571958.24 | 437717.5 | 79758.0288 | 33660 | 6133.3057 | 376493.3333 | 68602.1603 | 29920 | 5451.8273 | 741200 | 135056.6311 | 11678534.8333 | 2127986.4693 | 1498171.2687 | 272987 | 749176.1875 | 136510 | 146368.9242 | 26670.391 | 50407.4233 | 9184.912 | 1644540.193 | 299657.391 | 799583.6108 | 145694.912 | 2490.9793 | 453.89 | 9900 | 1803.9134 | 12390.9793 | 2257.8034 | 0 | 0 | 24356554.887 | 4438092.6184 | 2297384.4508 | 418614.4149 | 5488068.1818 | 3699523.8636 | 29844623.0688 | 5996908.3144
214-647R | oh | 3 | 11.4888 | 11.4888 | 11.3023 | 11.3023 | 11.1051 | 42192.81 | 3733.1262 | 80833.5 | 7151.9686 | 43010 | 3805.4293 | 202490.3571 | 17915.8973 | 368526.6671 | 32606.4214 | 3187800 | 282049.4671 | 5829134.2313 | 515748.8562 | 1994111.592 | 176434.5668 | 7823245.8233 | 692183.4229 | 11011045.8232 | 974232.8901 | 1225000 | 108385.2805 | 12604572.4904 | 1115224.592 | 142289.73 | 12589.4794 | 44767.8 | 3960.9556 | 187057.53 | 16550.435 | 2745096 | 242880 | 49730 | 4400 | 2794826 | 247280 | 2981883.53 | 263830.435 | 650430 | 57548.6025 | 3917034 | 346570.4726 | 198742.5 | 17584.2952 | 48015 | 4248.2606 | 537056.6667 | 47517.5816 | 42680 | 3776.2317 | 1057300 | 93547.5568 | 6451258.1667 | 570793.0009 | 3085373.525 | 272987 | 1542873.25 | 136510 | 222922.8061 | 19723.715 | 89977.2349 | 7960.986 | 3308296.3311 | 292710.715 | 1632850.4849 | 144470.986 | 5129.9886 | 453.89 | 9900 | 875.93 | 15029.9886 | 1329.82 | 0 | 0 | 22379156.9768 | 1980058.1278 | 4614734.0149 | 408301.421 | 11302272.7273 | 22210125.4669 | 33681429.704 | 26824859.4818
215-1531R | oh | 2 | 11.689 | 11.689 | 8.4597 | 8.4597 | 10.0851 | 41988.98 | 4963.4364 | 80443 | 9509.012 | 64047.5 | 7570.9316 | 201512.1429 | 23820.3621 | 387991.6229 | 45863.7421 | 3172400 | 375003.291 | 5800974.1625 | 685721.9777 | 1984478.2027 | 234581.3444 | 7785452.3652 | 920303.3221 | 10957852.3652 | 1295306.6131 | 3300000 | 390086.6411 | 14645843.988 | 1731256.9964 | 141602.34 | 16738.5398 | 64206.45 | 7589.7207 | 205808.79 | 24328.2605 | 2054682 | 242880 | 37222.5 | 4400 | 2091904.5 | 247280 | 2297713.29 | 271608.2605 | 750420 | 88705.7022 | 4519196 | 534205.451 | 229295 | 27104.5201 | 49005 | 5792.7866 | 548130 | 64793.3911 | 43560 | 5149.1437 | 1079100 | 127558.3317 | 7218706 | 853309.3263 | 2309376.9562 | 272987 | 1154828.0625 | 136510 | 161605.5782 | 19103.084 | 66421.3179 | 7851.536 | 2470982.5345 | 292090.084 | 1221249.3804 | 144361.536 | 3839.7547 | 453.89 | 9900 | 1170.2599 | 13739.7547 | 1624.1499 | 0 | 0 | 24349272.2772 | 2878280.5566 | 3518962.6704 | 415969.7965 | 8459659.0909 | 20170155.1656 | 32808931.3681 | 23689117.836
215-1534R | oh | 2 | 10.4587 | 10.4587 | 7.8377 | 7.8377 | 1.5538 | 39543.02 | 5045.2395 | 75757 | 9665.7313 | 66852.5 | 8529.6184 | 189773.5714 | 24212.9487 | 371926.0914 | 47453.538 | 2987600 | 381183.7711 | 5463053.3375 | 697023.4546 | 1868877.5307 | 238447.5113 | 7331930.8682 | 935470.966 | 10319530.8682 | 1316654.7371 | 3475000 | 443370.4661 | 14166456.9596 | 1807478.7412 | 133353.66 | 17014.4099 | 61261.2 | 7816.2322 | 194614.86 | 24830.6421 | 1903618 | 242880 | 34485.8333 | 4400 | 1938103.8333 | 247280 | 2132718.6933 | 272110.6421 | 409860 | 52293.4732 | 2468268 | 314922.9162 | 125235 | 15978.5612 | 37620 | 4799.884 | 420786.6667 | 53687.5915 | 33440 | 4266.5636 | 828400 | 105694.4156 | 4323609.6667 | 551643.4053 | 2139587.3146 | 272987 | 1069922.9792 | 136510 | 149639.5486 | 19092.304 | 61522.8991 | 7849.622 | 2289226.8631 | 292079.304 | 1131445.8783 | 144359.622 | 3557.4488 | 453.89 | 9900 | 1263.1274 | 13457.4488 | 1717.0174 | 0 | 0 | 20792750.9383 | 2652918.4678 | 3264164.5716 | 416470.2641 | 7837689.3939 | 3107564.7727 | 28630440.3322 | 6371729.3443
215-1544R | oh | 2 | 4.3646 | 4.3646 | 2.7396 | 2.7396 | 3.7445 | 10395.33 | 3794.4931 | 19915.5 | 7269.5361 | 7947.5 | 2900.9886 | 49888.9286 | 18210.4074 | 88147.2586 | 32175.4252 | 785400 | 286685.9316 | 1436163.5063 | 524226.9833 | 491302.856 | 179334.8828 | 1927466.3623 | 703561.8661 | 2712866.3622 | 990247.7976 | 400000 | 146007.6046 | 3201013.6208 | 1168430.8274 | 35056.89 | 12796.4313 | 15315.3 | 5590.3757 | 50372.19 | 18386.807 | 665390 | 242880 | 12054.1667 | 4400 | 677444.1667 | 247280 | 727816.3567 | 265666.807 | 152460 | 55650.7985 | 918148 | 335141.4753 | 46585 | 17004.4106 | 10890 | 3975.057 | 121806.6667 | 44461.749 | 9680 | 3533.384 | 239800 | 87531.5589 | 1499369.6667 | 547298.4335 | 747870.6354 | 272987 | 373980.5208 | 136510 | 46363.1276 | 16923.423 | 20463.8163 | 7469.682 | 794233.763 | 289910.423 | 394444.3371 | 143979.682 | 1243.4695 | 453.89 | 9900 | 3613.6882 | 11143.4695 | 4067.5782 | 0 | 0 | 5505760.52 | 2009707.262 | 1122260.6938 | 409646.489 | 2739583.3333 | 7488911.3195 | 8245343.8533 | 8611172.0133
215-38R | oh | 3 | 9.422 | 9.422 | 6.4307 | 6.4307 | 7.1713 | 24051.94 | 3740.1851 | 46079 | 7165.4921 | 17297.5 | 2689.8392 | 115429.2857 | 17949.7741 | 202857.7257 | 31545.2904 | 1817200 | 282582.7885 | 3322888.1125 | 516724.0747 | 1136739.9413 | 176768.1831 | 4459628.0538 | 693492.2579 | 6276828.0538 | 976075.0464 | 875000 | 136066.4428 | 7354685.7795 | 1143686.7796 | 81112.02 | 12613.2846 | 34753.95 | 5404.3958 | 115865.97 | 18017.6804 | 1561884 | 242880 | 28295 | 4400 | 1590179 | 247280 | 1706044.97 | 265297.6804 | 310860 | 48340.1308 | 1872068 | 291115.0097 | 94985 | 14770.5955 | 20295 | 3155.964 | 227003.3333 | 35300.0412 | 18040 | 2805.3013 | 446900 | 69494.9638 | 2990151.3333 | 464982.0062 | 1755492.5375 | 272987 | 877852.375 | 136510 | 108948.7657 | 16942.024 | 48058.4209 | 7473.301 | 1864441.3032 | 289929.024 | 925910.7959 | 143983.301 | 2918.8222 | 453.89 | 9900 | 1539.4946 | 12818.8222 | 1993.3846 | 0 | 0 | 12222097.2383 | 1900591.1945 | 2631955.7659 | 409280.9814 | 6430681.8182 | 14342651.0287 | 18652779.0564 | 16974606.7946
216-1859F | oh | 3 | 9.1299 | 9.1299 | 8.4771 | 8.4771 | 3.0466 | 39950.68 | 4712.786 | 76538 | 9028.813 | 77137.5 | 9099.5331 | 191730 | 22617.449 | 385356.18 | 45458.5811 | 3018400 | 356065.8638 | 5519373.475 | 651093.4549 | 1888144.3093 | 222735.136 | 7407517.7843 | 873828.5909 | 10425917.7843 | 1229894.4548 | 3400000 | 401081.3468 | 14211273.9643 | 1676434.3826 | 134728.44 | 15893.2542 | 41822.55 | 4933.6014 | 176550.99 | 20826.8555 | 2058914 | 242880 | 37299.1667 | 4400 | 2096213.1667 | 247280 | 2272764.1567 | 268106.8555 | 482130 | 56874.5146 | 2903494 | 342510.9658 | 147317.5 | 17378.3239 | 42570 | 5021.7744 | 476153.3333 | 56169.4765 | 37840 | 4463.7995 | 937400 | 110580.4866 | 5026904.8333 | 592999.3414 | 2314133.5479 | 272987 | 1157206.6458 | 136510 | 150607.6941 | 17766.452 | 64582.1084 | 7618.435 | 2464741.2421 | 290753.452 | 1221788.7542 | 144128.435 | 3847.6634 | 453.89 | 9900 | 1167.8545 | 13747.6634 | 1621.7445 | 0 | 0 | 21716667.7031 | 2561808.9205 | 3494552.9109 | 412235.2905 | 8477083.3333 | 6093193.3563 | 30193751.0364 | 9587746.2671
217-41AE | oh | 2 | 14.7212 | 14.7212 | 13.7784 | 13.7784 | 17.613 | 68079.22 | 4941.0073 | 130427 | 9466.0421 | 66385 | 4818.0454 | 326723.5714 | 23712.7211 | 591614.7914 | 42937.8158 | 5143600 | 373308.701 | 9405462.9625 | 682623.2913 | 3217552.0373 | 233521.3025 | 12623014.9998 | 916144.5938 | 17766614.9998 | 1289453.2948 | 3125000 | 226804.1237 | 21483229.7913 | 1559195.2343 | 229588.26 | 16662.9005 | 77754.6 | 5643.2205 | 307342.86 | 22306.121 | 3346500 | 242880 | 60625 | 4400 | 3407125 | 247280 | 3714467.86 | 269586.121 | 941490 | 68330.8206 | 5669862 | 411503.3864 | 287677.5 | 20878.8619 | 89595 | 6502.5649 | 1002136.6667 | 72732.3931 | 79640 | 5780.0577 | 1972900 | 143187.7938 | 10043301.1667 | 728915.8785 | 3761326.5625 | 272987 | 1880890.625 | 136510 | 252649.3828 | 18336.615 | 106349.5875 | 7718.568 | 4013975.9453 | 291323.615 | 1987240.2125 | 144228.568 | 6253.8821 | 453.89 | 9900 | 718.5155 | 16153.8821 | 1172.4055 | 0 | 0 | 35556660.7853 | 2580607.1333 | 5701708.0725 | 413814.689 | 13778409.0909 | 35225974.3744 | 49335069.8763 | 40927682.4469
217-48AE | oh | 2 | 24.1801 | 24.1801 | 15.1559 | 15.1559 | 21.0895 | 62779.64 | 4142.2653 | 120274 | 7935.8025 | 61710 | 4071.6894 | 301290 | 19879.4247 | 546053.64 | 36029.1819 | 4743200 | 312961.2236 | 8673301.175 | 572273.349 | 2967083.9147 | 195771.2541 | 11640385.0897 | 768044.6031 | 16383585.0897 | 1081005.8267 | 2400000 | 158354.4731 | 19329638.7297 | 1275389.4817 | 211716.12 | 13969.2478 | 103672.8 | 6840.4382 | 315388.92 | 20809.6859 | 3681058 | 242880 | 66685.8333 | 4400 | 3747743.8333 | 247280 | 4063132.7533 | 268089.6859 | 785070 | 51799.7276 | 4727866 | 311949.4705 | 239882.5 | 15827.6945 | 69795 | 4605.146 | 780670 | 51509.411 | 62040 | 4093.4631 | 1536900 | 101406.2457 | 8202223.5 | 541191.1585 | 4137355.8146 | 272987 | 2068927.9792 | 136510 | 277697.9819 | 18322.799 | 116942.7781 | 7716.005 | 4415053.7965 | 291309.799 | 2185870.7572 | 144226.005 | 6879.0984 | 453.89 | 9900 | 653.2122 | 16779.0984 | 1107.1022 | 0 | 0 | 31963695.1245 | 2108997.5414 | 6249003.5106 | 412315.6909 | 15155871.2121 | 42179098.1989 | 47119566.3366 | 48428101.7095
217-835R | oh | 3 | 18.6464 | 18.6464 | 18.3176 | 18.3176 | 2.8104 | 60741.34 | 3316.0073 | 116369 | 6352.8472 | 39270 | 2143.8382 | 291507.8571 | 15914.0739 | 507888.1971 | 27726.7666 | 4589200 | 250534.8181 | 8391700.4875 | 458121.9287 | 2870750.0213 | 156720.7431 | 11262450.5088 | 614842.6718 | 15851650.5088 | 865377.4899 | 1450000 | 79158.7828 | 17809538.706 | 972263.0393 | 204842.22 | 11182.8006 | 48302.1 | 2636.921 | 253144.32 | 13819.7216 | 4448982 | 242880 | 80597.5 | 4400 | 4529579.5 | 247280 | 4782723.82 | 261099.7216 | 1082070 | 59072.6511 | 6516466 | 355748.6324 | 330632.5 | 18049.9767 | 48015 | 2621.2476 | 537056.6667 | 29319.1393 | 42680 | 2329.9978 | 1057300 | 57720.4008 | 9614220.1667 | 524862.0458 | 5000470.3937 | 272987 | 2500537.4375 | 136510 | 374785.2258 | 20460.374 | 148215.5786 | 8091.424 | 5375255.6195 | 293447.374 | 2648753.0161 | 144601.424 | 8314.1817 | 453.89 | 9900 | 540.4634 | 18214.1817 | 994.3534 | 0 | 0 | 32817228.6738 | 1791566.8124 | 7431476.8361 | 405701.1456 | 18317613.6364 | 5620733.5143 | 51134842.3102 | 13052210.3504
217-837R | oh | 3 | 19.2483 | 19.2256 | 12.6807 | 12.6807 | 16.8619 | 50753.67 | 4002.4401 | 97234.5 | 7667.9236 | 47217.5 | 3723.5774 | 243575.3571 | 19208.3802 | 438781.0271 | 34602.3213 | 3834600 | 302396.989 | 7011857.1188 | 552955.8441 | 2398713.944 | 189162.8525 | 9410571.0628 | 742118.6966 | 13245171.0628 | 1044515.6856 | 2175000 | 171520.7456 | 15858952.0899 | 1250638.7525 | 171160.11 | 13497.7056 | 80110.8 | 6317.5467 | 251270.91 | 19815.2523 | 3079884 | 242880 | 55795 | 4400 | 3135679 | 247280 | 3386949.91 | 267095.2523 | 864270 | 68156.4298 | 5204826 | 410453.1661 | 264082.5 | 20825.5758 | 57420 | 4528.1477 | 642253.3333 | 50648.1704 | 51040 | 4025.0202 | 1264400 | 99710.7268 | 8348291.8333 | 658347.2366 | 3461661.2875 | 272987 | 1731039.875 | 136510 | 212687.4713 | 16772.558 | 94385.4723 | 7443.249 | 3674348.7588 | 289759.558 | 1825425.3473 | 143953.249 | 5755.6347 | 453.89 | 9900 | 780.7151 | 15655.6347 | 1234.6051 | 0 | 0 | 27897248.3167 | 2199980.1522 | 5212375.2573 | 411048.5013 | 12680681.8182 | 33723867.8156 | 40577930.1349 | 38936243.0729
217-972R | oh | 2 | 10.4587 | 10.4587 | 9.7468 | 9.7468 | 6.5145 | 44434.94 | 4558.9352 | 85129 | 8734.0637 | 73865 | 7578.4 | 213250.7143 | 21879.0932 | 416679.6543 | 42750.4921 | 3357200 | 344441.9486 | 6138894.9875 | 629838.2437 | 2100078.8747 | 215463.8567 | 8238973.8622 | 845302.1004 | 11596173.8622 | 1189744.049 | 3625000 | 371917.6884 | 15637853.5165 | 1604412.2295 | 149851.02 | 15374.4124 | 54781.65 | 5620.4868 | 204632.67 | 20994.8992 | 2367298 | 242880 | 42885.8333 | 4400 | 2410183.8333 | 247280 | 2614816.5033 | 268274.8992 | 969210 | 99438.9911 | 5836798 | 598843.7021 | 296147.5 | 30384.1362 | 54450 | 5586.4602 | 609033.3333 | 62485.5916 | 48400 | 4965.7424 | 1199000 | 123014.9816 | 9013038.8333 | 924719.6052 | 2660744.3146 | 272987 | 1330532.9792 | 136510 | 179018.5485 | 18366.942 | 75279.5403 | 7723.529 | 2839762.8631 | 291353.942 | 1405812.5195 | 144233.529 | 4423.9661 | 453.89 | 9900 | 1015.72 | 14323.9661 | 1469.61 | 0 | 0 | 27504979.179 | 2821955.3867 | 4020629.0228 | 412508.4282 | 9746780.303 | 13028993.3314 | 37251759.482 | 17049622.3542
217-983R | oh | 3 | 14.396 | 14.396 | 6.8811 | 6.8811 | 0.13034 | 23848.11 | 3465.7608 | 45688.5 | 6639.7468 | 47217.5 | 6861.9509 | 113472.8571 | 16490.6057 | 230226.9671 | 33458.0641 | 1801800 | 261849.1688 | 3294728.0438 | 478811.0776 | 1127106.552 | 163798.3759 | 4421834.5958 | 642609.4535 | 6223634.5958 | 904458.6223 | 2225000 | 323351.3156 | 8678861.5629 | 1261268.0021 | 80424.63 | 11687.8247 | 45945.9 | 6677.1538 | 126370.53 | 18364.9785 | 1671272 | 242880 | 30276.6667 | 4400 | 1701548.6667 | 247280 | 1827919.1967 | 265644.9785 | 279180 | 40572.2338 | 1681284 | 244335.0083 | 85305 | 12397.0715 | 26730 | 3884.5756 | 298980 | 43449.6972 | 23760 | 3452.9561 | 588600 | 85539.1391 | 2983839 | 433630.6815 | 1878440.0917 | 272987 | 939333.5833 | 136510 | 141028.1835 | 20495.123 | 55715.3491 | 8096.913 | 2019468.2752 | 293482.123 | 995048.9324 | 144606.913 | 3123.2446 | 453.89 | 9900 | 1438.7317 | 13023.2446 | 1892.6217 | 0 | 0 | 13695192.0826 | 1990273.4283 | 2822968.1291 | 410251.8915 | 6881060.6061 | 260684.3683 | 20576252.6887 | 3083652.4973
220-288R | oh | 3 | 7.2415 | 7.2415 | 7.2415 | 7.2415 | 2.2447 | 25274.92 | 3490.2989 | 48422 | 6686.7572 | 6545 | 903.8211 | 121298.5714 | 16750.5285 | 201540.4914 | 27831.4056 | 1909600 | 263703.0993 | 3491848.525 | 482201.1302 | 1194540.2773 | 164958.0924 | 4686388.8023 | 647159.2226 | 6595988.8023 | 910862.3219 | 250000 | 34523.3425 | 7047529.2938 | 973217.07 | 85236.36 | 11770.5762 | 11781 | 1626.878 | 97017.36 | 13397.4542 | 1758810 | 242880 | 31862.5 | 4400 | 1790672.5 | 247280 | 1887689.86 | 260677.4542 | 185130 | 25565.2256 | 1114894 | 153959.4696 | 56567.5 | 7811.5967 | 18810 | 2597.5363 | 210393.3333 | 29053.9244 | 16720 | 2308.9211 | 414200 | 57198.2738 | 2016714.8333 | 278494.9476 | 1976829.1562 | 272987 | 988534.0625 | 136510 | 178398.4561 | 24635.644 | 63918.485 | 8826.719 | 2155227.6124 | 297622.644 | 1052452.5475 | 145336.719 | 3286.8341 | 453.89 | 9900 | 1367.1244 | 13186.8341 | 1821.0144 | 0 | 0 | 11232658.5736 | 1551155.6759 | 2940142.4075 | 406014.1732 | 7241477.2727 | 4489315.3966 | 18474135.8463 | 7429457.8041
220-294R | oh | 3 | 14.2199 | 14.2199 | 13.4125 | 13.4125 | 2.9351 | 55645.59 | 4148.7858 | 106606.5 | 7948.2945 | 86020 | 6413.4203 | 267052.5 | 19910.7176 | 515324.59 | 38421.2183 | 4204200 | 313453.8677 | 7687698.7687 | 573174.1859 | 2629915.288 | 196079.425 | 10317614.0567 | 769253.6109 | 14521814.0567 | 1082707.4786 | 1650000 | 123019.5713 | 16687138.6467 | 1244148.2682 | 187657.47 | 13991.2373 | 47713.05 | 3557.3569 | 235370.52 | 17548.5942 | 3257628 | 242880 | 59015 | 4400 | 3316643 | 247280 | 3552013.52 | 264828.5942 | 1031580 | 76911.836 | 6212404 | 463180.1678 | 315205 | 23500.8388 | 57420 | 4281.0811 | 642253.3333 | 47884.6847 | 51040 | 3805.4054 | 1264400 | 94270.2703 | 9574302.3333 | 713834.2839 | 3661438.1375 | 272987 | 1830940.375 | 136510 | 347070.4608 | 25876.642 | 121314.3323 | 9044.871 | 4008508.5983 | 298863.642 | 1952254.7073 | 145554.871 | 6087.7996 | 453.89 | 9900 | 738.1174 | 15987.7996 | 1192.0074 | 0 | 0 | 30285937.378 | 2258038.2015 | 5504268.2273 | 410383.4652 | 13412500 | 5870112.5 | 43698437.378 | 11374380.7273
220-298R | oh | 3 | 45.2934 | 45.2934 | 33.211 | 33.211 | 6.1508 | 126374.6 | 3805.2048 | 242110 | 7290.0578 | 144457.5 | 4349.6903 | 606492.8571 | 18261.8149 | 1119434.9571 | 33706.7679 | 9548000 | 287495.2382 | 17459242.625 | 525706.8619 | 5972701.3867 | 179841.1403 | 23431944.0117 | 705548.0022 | 32979944.0117 | 993043.2404 | 5300000 | 159585.7522 | 39399378.9688 | 1186335.7605 | 426181.8 | 12832.5553 | 92480.85 | 2784.6464 | 518662.65 | 15617.2017 | 8066284 | 242880 | 146128.3333 | 4400 | 8212412.3333 | 247280 | 8731074.9833 | 262897.2017 | 3206610 | 96552.6923 | 19310918 | 581461.769 | 979797.5 | 29502.2115 | 87615 | 2638.1331 | 979990 | 29508.0078 | 77880 | 2345.0072 | 1929300 | 58092.2249 | 26572110.5 | 800100.0459 | 9066167.1208 | 272987 | 4533631.5417 | 136510 | 857611.4795 | 25823.127 | 300057.7277 | 9034.894 | 9923778.6004 | 298810.127 | 4833689.2694 | 145544.894 | 15074.1339 | 453.89 | 9900 | 298.0941 | 24974.1339 | 751.9841 | 0 | 0 | 75920242.2031 | 2285997.9175 | 13564764.2527 | 408442.0957 | 33210984.8485 | 12301685.0686 | 109131227.0516 | 25866449.3213
221-1230F | oh | 3 | 3.9131 | 3.9131 | 3.8686 | 3.8686 | 5.1422 | 19771.51 | 5110.8182 | 37878.5 | 9791.3679 | 1402.5 | 362.5379 | 94886.7857 | 24527.672 | 153939.2957 | 39792.396 | 1493800 | 386138.451 | 2731526.6688 | 706083.4628 | 934438.7653 | 241546.8854 | 3665965.4341 | 947630.3482 | 5159765.4341 | 1333768.7992 | 25000 | 6462.3519 | 5338704.7298 | 1380023.5471 | 66676.83 | 17235.5656 | 0 | 0 | 66676.83 | 17235.5656 | 939596 | 242880 | 17021.6667 | 4400 | 956617.6667 | 247280 | 1023294.4967 | 264515.5656 | 99000 | 25590.9135 | 596200 | 154114.1682 | 30250 | 7819.4458 | 19800 | 5118.1827 | 221466.6667 | 57247.8214 | 17600 | 4549.4957 | 436000 | 112703.4172 | 1420316.6667 | 367143.4446 | 1056066.7542 | 272987 | 528097.2083 | 136510 |  |  |  |  | 1056066.7542 | 272987 | 528097.2083 | 136510 | 1755.901 | 453.89 | 9900 | 2559.0914 | 11655.901 | 3012.9814 | 0 | 0 | 7826744.0516 | 2023166.9731 | 1551391.705 | 401025.5656 | 3868560.6061 | 10284396.4607 | 11695304.6577 | 11835788.1657
221-23R | oh | 3 | 6.2025 | 6.2025 | 5.8843 | 5.8843 | 7.6438 | 34447.27 | 5854.1178 | 65994.5 | 11215.3903 | 1870 | 317.7959 | 165318.2143 | 28094.8911 | 267629.9843 | 45482.195 | 2602600 | 442297.0807 | 4759051.6188 | 808773.7792 | 1628042.7973 | 276676.622 | 6387094.4161 | 1085450.4013 | 8989694.4161 | 1527747.482 | 100000 | 16994.4317 | 9357324.4004 | 1590224.1087 | 116168.91 | 19742.2461 | 45945.9 | 7808.2446 | 162114.81 | 27550.4907 | 1429174 | 242880 | 25890.8333 | 4400 | 1455064.8333 | 247280 | 1617179.6433 | 274830.4907 | 887040 | 150747.4074 | 5341952 | 907834.3867 | 271040 | 46061.7078 | 42075 | 7150.4072 | 470616.6667 | 79978.6282 | 37400 | 6355.9175 | 926500 | 157453.4102 | 7976623.6667 | 1355581.8649 | 1606332.0271 | 272987 | 803263.1042 | 136510 | 111787.3624 | 18997.627 | 46101.412 | 7834.673 | 1718119.3894 | 291984.627 | 849364.5162 | 144344.673 | 2670.816 | 453.89 | 9900 | 1682.4487 | 12570.816 | 2136.3387 | 0 | 0 | 19064638.2725 | 3239926.9393 | 2466544.1595 | 419175.1637 | 5884280.303 | 15287612.6239 | 24948918.5755 | 17754156.7834
221-344R | oh | 3 | 10.6593 | 10.6593 | 10.397 | 10.397 | 13.5926 | 45657.92 | 4391.4642 | 87472 | 8413.2206 | 22907.5 | 2203.2862 | 219120 | 21075.3716 | 375157.42 | 36083.3426 | 3449600 | 331788.9828 | 6307855.4 | 606701.3355 | 2157879.2107 | 207548.8603 | 8465734.6107 | 814250.1957 | 11915334.6107 | 1146039.1785 | 925000 | 88968.2308 | 13215492.0307 | 1271090.752 | 153975.36 | 14809.6382 | 45356.85 | 4362.5067 | 199332.21 | 19172.1449 | 2525216 | 242880 | 45746.6667 | 4400 | 2570962.6667 | 247280 | 2770294.8767 | 266452.1449 | 1527570 | 146924.541 | 9199366 | 884812.2355 | 466757.5 | 44893.6097 | 47520 | 4570.5625 | 531520 | 51122.5882 | 42240 | 4062.7222 | 1046400 | 100644.71 | 12861373.5 | 1237030.9691 | 2838237.5667 | 272987 | 1419290.3333 | 136510 | 197996.4911 | 19043.673 | 81540.8029 | 7842.747 | 3036234.0578 | 292030.673 | 1500831.1362 | 144352.747 | 4719.0806 | 453.89 | 9900 | 952.2005 | 14619.0806 | 1406.0905 | 0 | 0 | 29127718.669 | 2801558.4846 | 4271126.0129 | 410804.8919 | 10396969.697 | 27185298.677 | 39524688.366 | 31456424.6899
221-37AE | oh | 3 | 6.46 | 6.46 | 6.2108 | 6.2108 | 8.2999 | 30982.16 | 4988.4367 | 59356 | 9556.9079 | 19167.5 | 3086.1586 | 148688.5714 | 23940.3427 | 258194.2314 | 41571.8459 | 2340800 | 376892.1416 | 4280330.45 | 689175.8844 | 1464275.1787 | 235762.905 | 5744605.6287 | 924938.7894 | 8085405.6287 | 1301830.931 | 850000 | 136858.4759 | 9193599.8601 | 1480261.2527 | 104483.28 | 16822.8499 | 34753.95 | 5595.7325 | 139237.23 | 22418.5825 | 1508478 | 242880 | 27327.5 | 4400 | 1535805.5 | 247280 | 1675042.73 | 269698.5825 | 963270 | 155096.0754 | 5801026 | 934023.0317 | 294332.5 | 47390.4675 | 34650 | 5578.9955 | 387566.6667 | 62402.098 | 30800 | 4959.1071 | 763000 | 122850.6084 | 8274645.1667 | 1332300.3836 | 1695466.4187 | 272987 | 847835.6875 | 136510 | 118260.781 | 19041.165 | 48707.2379 | 7842.351 | 1813727.1998 | 292028.165 | 896542.9254 | 144352.351 | 2819.0179 | 453.89 | 9900 | 1593.9987 | 12719.0179 | 2047.8887 | 0 | 0 | 19294691.2445 | 3106637.6901 | 2571585.6554 | 414050.9335 | 6210795.4545 | 16599894.3853 | 25505486.699 | 19171480.0407
221-675R | oh | 2 | 6.9098 | 6.0235 | 6.0235 | 6.9098 | 10.296 | 18956.19 | 2743.3583 | 36316.5 | 5255.7592 | 33660 | 4871.308 | 75322.5 | 10900.7455 | 164255.19 | 23771.171 | 1432200 | 207269.3784 | 2618886.3937 | 379007.7886 | 895905.208 | 129656.2739 | 3514791.6017 | 508664.0625 | 4946991.6017 | 715933.4409 | 1275000 | 184519.2413 | 6386246.7917 | 924223.8532 | 63927.27 | 9251.6168 | 2945.25 | 426.2394 | 66872.52 | 9677.8562 | 1678264 | 242880 | 30403.3333 | 4400 | 1708667.3333 | 247280 | 1775539.8533 | 256957.8562 | 248490 | 35961.7147 | 1496462 | 216569.4376 | 75927.5 | 10988.3017 | 2970 | 429.8213 | 33220 | 4807.6307 | 2640 | 382.0634 | 65400 | 9464.7517 | 1925109.5 | 278603.7211 | 1644333.0583 | 237969.4811 | 822265.9167 | 118999.124 | 114890.0948 | 16627.0064 | 47270.6827 | 6841.0592 | 1759223.1531 | 254596.4875 | 869536.5994 | 125840.1832 | 3136.3111 | 453.89 | 9900 | 1432.7376 | 13036.3111 | 1886.6276 | 0 | 0 | 10083615.756 | 1459310.6894 | 2645076.4527 | 382798.0394 | 6909848.4848 | 20591900.2105 | 16993464.2408 | 23236976.6633
221-6R | oh | 2 | 6.0572 | 5.5852 | 5.5852 | 6.0572 | 7.8515 | 20586.83 | 3398.7387 | 39440.5 | 6511.3451 | 43477.5 | 7177.825 | 89995.7143 | 14857.6503 | 193500.5443 | 31945.5592 | 1555400 | 256785.4418 | 2844166.9438 | 469551.6685 | 972972.3227 | 160630.7881 | 3817139.2664 | 630182.4566 | 5372539.2664 | 886967.8984 | 1925000 | 317803.7646 | 7491039.8107 | 1236717.2222 | 69426.39 | 11461.8016 | 589.05 | 97.248 | 70015.44 | 11559.0496 | 1471172 | 242880 | 26651.6667 | 4400 | 1497823.6667 | 247280 | 1567839.1067 | 258839.0496 | 6930 | 1144.0936 | 41734 | 6889.9856 | 2117.5 | 349.5841 | 1485 | 245.1629 | 16610 | 2742.1925 | 1320 | 217.9226 | 32700 | 5398.5367 | 102896.5 | 16987.478 | 1524694.4375 | 251716.1725 | 762439.375 | 125873.3006 | 106570.5934 | 17594.0446 | 43838.6667 | 7237.4511 | 1631265.0309 | 269310.2171 | 806278.0417 | 133110.7517 | 2749.3011 | 453.89 | 9900 | 1634.4194 | 12649.3011 | 2088.3094 | 0 | 0 | 9237850.6427 | 1525103.2266 | 2374117.1484 | 391949.8012 | 6057196.9697 | 15702937.4889 | 15295047.6124 | 18077054.6372
221-782R | oh | 3 | 3.6625 | 3.6625 | 3.289 | 3.289 | 4.589 | 19160.02 | 5825.4581 | 36707 | 11160.4837 |  |  | 91952.1429 | 27957.3485 | 147819.1629 | 44943.2903 | 1447600 | 440131.7517 | 2647046.4625 | 804814.3108 | 905538.5973 | 275322.1118 | 3552585.0598 | 1080136.4227 | 5000185.0598 | 1520268.1744 | 0 | 0 | 5148004.2227 | 1565211.4647 | 64614.66 | 19645.5951 | 1767.15 | 537.2885 | 66381.81 | 20182.8836 | 798836 | 242880 | 14471.6667 | 4400 | 813307.6667 | 247280 | 879689.4767 | 267462.8836 | 352440 | 107156.697 | 2122472 | 645321.4419 | 107690 | 32742.3241 | 2475 | 752.5049 | 27683.3333 | 8416.9066 | 2200 | 668.8932 | 54500 | 16570.3098 | 2669460.3333 | 811629.0775 | 897858.3792 | 272987 | 448983.4583 | 136510 | 85222.1617 | 25911.149 | 62429.2867 | 18981.149 | 983080.5408 | 298898.149 | 511412.745 | 155491.149 | 1492.8511 | 453.89 | 9900 | 3010.0196 | 11392.8511 | 3463.9096 | 0 | 0 | 8811937.9479 | 2679202.6008 | 1391102.2217 | 422954.0326 | 3289015.1515 | 9177932.1181 | 12100953.0994 | 10569034.3398
221-788 | oh | 3 | 3.5117 | 3.5117 | 3.417 | 3.417 | 5.2021 | 11414.48 | 3340.4531 | 21868 | 6399.6807 | 14960 | 4378.0512 | 54780 | 16031.3934 | 103022.48 | 30149.5785 | 862400 | 252381.7759 | 1576963.85 | 461499.2311 | 539469.8027 | 157876.0979 | 2116433.6527 | 619375.329 | 2978833.6527 | 871757.1049 | 750000 | 219487.8617 | 3831856.1327 | 1121394.545 | 38493.84 | 11265.2408 | 7657.65 | 2241.015 | 46151.49 | 13506.2558 | 829932 | 242880 | 15035 | 4400 | 844967 | 247280 | 891118.49 | 260786.2558 | 324720 | 95029.4646 | 1955536 | 572288.5534 | 99220 | 29036.7808 | 7920 | 2317.7918 | 88586.6667 | 25924.9307 | 7040 | 2060.2594 | 174400 | 51038.2441 | 2657422.6667 | 777696.0248 | 932808.9875 | 272987 | 466460.875 | 136510 | 65206.2312 | 19082.635 | 26821.2748 | 7849.259 | 998015.2187 | 292069.635 | 493282.1498 | 144359.259 | 1550.9628 | 453.89 | 9900 | 2897.2398 | 11450.9628 | 3351.1298 | 0 | 0 | 7498744.9808 | 2194511.3346 | 1384400.6398 | 405145.5148 | 3417045.4545 | 10404123.8993 | 10915790.4353 | 11788524.5391
221-824 | oh | 3 | 2.8462 | 2.8462 | 2.7125 | 2.7125 | 3.2036 | 14471.93 | 5335.2737 | 27725.5 | 10221.3825 | 5142.5 | 1895.8525 | 69453.2143 | 25604.8716 | 116793.1443 | 43057.3804 | 1093400 | 403096.7742 | 1999364.8813 | 737093.0438 | 683970.6427 | 252155.0756 | 2683335.5239 | 989248.1194 | 3776735.5239 | 1392344.8936 | 275000 | 101382.4885 | 4168528.6682 | 1536784.7625 | 48804.69 | 17992.5124 | 15904.35 | 5863.3548 | 64709.04 | 23855.8673 | 658812 | 242880 | 11935 | 4400 | 670747 | 247280 | 735456.04 | 271135.8673 | 148500 | 54746.5438 | 894300 | 329695.8525 | 45375 | 16728.1106 | 16335 | 6022.1198 | 182710 | 67358.5253 | 14520 | 5352.9954 | 359700 | 132608.2949 | 1661440 | 612512.4424 | 740477.2375 | 272987 | 370283.375 | 136510 | 51771.1059 | 19086.122 | 21292.4876 | 7849.765 | 792248.3434 | 292073.122 | 391575.8626 | 144359.765 | 1231.1766 | 453.89 | 9900 | 3649.7696 | 11131.1766 | 4103.6596 | 0 | 0 | 6633348.1883 | 2445473.9865 | 1127031.9026 | 415495.6323 | 2712500 | 6407169.5252 | 9345848.1883 | 7534201.4278
222-1433R | oh | 3 | 6.1799 | 6.1799 | 6.1127 | 6.1127 | 0.057487 | 22013.64 | 3601.3019 | 42174 | 6899.4181 | 27115 | 4435.8544 | 105647.1429 | 17283.2506 | 196949.7829 | 32219.825 | 1663200 | 272089.7289 | 3041287.425 | 497536.7189 | 1040406.048 | 170204.3047 | 4081693.473 | 667741.0236 | 5744893.473 | 939830.7525 | 875000 | 143144.849 | 6816843.2559 | 1115195.4265 | 74238.12 | 12144.9194 | 9424.8 | 1541.8418 | 83662.92 | 13686.7612 | 1484650 | 242880 | 26895.8333 | 4400 | 1511545.8333 | 247280 | 1595208.7533 | 260966.7612 | 166320 | 27208.9729 | 1001616 | 163858.4812 | 50820 | 8313.8528 | 9900 | 1619.5817 | 110733.3333 | 18115.3215 | 8800 | 1439.6282 | 218000 | 35663.5167 | 1566189.3333 | 256219.3549 | 1668684.7396 | 272987 | 834443.2292 | 136510 | 150298.6234 | 24587.97 | 53906.1757 | 8818.733 | 1818983.363 | 297574.97 | 888349.4048 | 145328.733 | 2774.4886 | 453.89 | 9900 | 1619.5817 | 12674.4886 | 2073.4717 | 0 | 0 | 10214690.4408 | 1671063.2232 | 2483558.1582 | 406295.4942 | 6112689.3939 | 114975 | 16327379.8347 | 2598533.1582
222-1503R | oh | 3 | 3.139 | 3.139 | 2.2977 | 2.2977 | 1.4128 | 11822.14 | 5145.145 | 22649 | 9857.1316 | 7480 | 3255.3907 | 56736.4286 | 24692.412 | 98687.5686 | 42950.0793 | 893200 | 388731.9486 | 1633283.9875 | 710825.8699 | 558736.5813 | 243169.2342 | 2192020.5688 | 953995.1041 | 3085220.5688 | 1342727.0527 | 200000 | 87042.5321 | 3383908.1374 | 1472719.6642 | 39868.62 | 17351.3282 | 16493.4 | 7178.1365 | 56362.02 | 24529.4647 | 558072 | 242880 | 10110 | 4400 | 568182 | 247280 | 624544.02 | 271809.4647 | 467280 | 203366.1721 | 2814064 | 1224716.2809 | 142780 | 62139.6637 | 12870 | 5601.1869 | 143953.3333 | 62650.3132 | 11440 | 4978.8328 | 283400 | 123339.2681 | 3875787.3333 | 1686791.7178 | 627249.675 | 272987 | 313662.75 | 136510 | 47800.0294 | 20803.178 | 18730.6453 | 8151.814 | 675049.7044 | 293790.178 | 332393.3953 | 144661.814 | 1042.9154 | 453.89 | 9900 | 4308.6053 | 10942.9154 | 4762.4953 | 0 | 0 | 7945688.0906 | 3458064.0553 | 956937.4153 | 416471.2787 | 2297727.2727 | 2825628.4229 | 10243415.3633 | 3782565.8382
222-1523R | oh | 3 | 20.1818 | 20.1818 | 10.9907 | 10.9907 | 4.3241 | 54218.78 | 4933.1419 | 103873 | 9450.9734 | 39270 | 3573.0144 | 260205 | 23674.9737 | 457566.78 | 41632.1035 | 4096400 | 372714.4457 | 7490578.2875 | 681536.6504 | 2562481.5627 | 233149.5692 | 10053059.8502 | 914686.2196 | 14149459.8502 | 1287400.6653 | 1775000 | 161499.888 | 16382026.6302 | 1490532.6568 | 182845.74 | 16636.3755 | 87768.45 | 7985.6872 | 270614.19 | 24622.0627 | 2669426 | 242880 | 48359.1667 | 4400 | 2717785.1667 | 247280 | 2988399.3567 | 271902.0627 | 2354220 | 214200.7134 | 14177636 | 1289964.2963 | 719345 | 65450.218 | 65340 | 5945.0156 | 730840 | 66496.1004 | 58080 | 5284.4583 | 1438800 | 130910.4444 | 19544261 | 1778251.2464 | 3000323.5979 | 272987 | 1500343.1458 | 136510 | 226190.8138 | 20580.164 | 89161.9717 | 8112.478 | 3226514.4118 | 293567.164 | 1589505.1176 | 144622.478 | 4988.5778 | 453.89 | 9900 | 900.7599 | 14888.5778 | 1354.6499 | 0 | 0 | 39167690.6197 | 3563705.7172 | 4577904.4742 | 416524.5407 | 10990719.697 | 8648137.9624 | 50158410.3167 | 13226042.4367
222-1986R | oh | 3 | 41.1722 | 41.1722 | 20.2812 | 20.2812 | 2.3245 | 79493.7 | 3919.5661 | 152295 | 7509.1525 | 67787.5 | 3342.3729 | 381503.5714 | 18810.6538 | 681079.7714 | 33581.7453 | 6006000 | 296135.5932 | 10982426.8125 | 541506.4068 | 3757021.84 | 185246.0692 | 14739448.6525 | 726752.4759 | 20745448.6525 | 1022888.0692 | 2500000 | 123266.5639 | 23926528.4239 | 1179736.3784 | 268082.1 | 13218.2237 | 133714.35 | 6593.0034 | 401796.45 | 19811.2271 | 4925910 | 242880 | 89237.5 | 4400 | 5015147.5 | 247280 | 5416943.95 | 267091.2271 | 645480 | 31826.4407 | 3887224 | 191665.8983 | 197230 | 9724.7458 | 82665 | 4075.9322 | 924623.3333 | 45590.0565 | 73480 | 3623.0508 | 1820300 | 89752.8505 | 7631002.3333 | 376258.9748 | 5536517.5937 | 272987 | 2768593.4375 | 136510 | 488047.9189 | 24063.996 | 176982.0566 | 8726.388 | 6024565.5126 | 297050.996 | 2945575.4941 | 145236.388 | 9205.4566 | 453.89 | 9900 | 488.1356 | 19105.4566 | 942.0256 | 0 | 0 | 37601201.7264 | 1853988.3748 | 8362519.4441 | 412327.6151 | 20281250 | 4649030.3837 | 57882451.7264 | 13011549.8279
222-1990R | oh | 3 | 15.1515 | 15.1515 | 13.1989 | 13.1989 | 0.71034 | 51568.99 | 3907.078 | 98796.5 | 7485.2277 | 29920 | 2266.8618 | 247488.2143 | 18750.7214 | 427773.7043 | 32409.8889 | 3896200 | 295192.0792 | 7124497.3937 | 539781.1198 | 2437247.5013 | 184655.8589 | 9561744.8951 | 724436.9787 | 13457944.8951 | 1019629.0579 | 975000 | 73869.9957 | 14860718.5994 | 1125908.9425 | 173909.67 | 13176.1093 | 46534.95 | 3525.6785 | 220444.62 | 16701.7878 | 3205740 | 242880 | 58075 | 4400 | 3263815 | 247280 | 3484259.62 | 263981.7878 | 373230 | 28277.4344 | 2247674 | 170292.9935 | 114042.5 | 8640.3272 | 42570 | 3225.2777 | 476153.3333 | 36075.3279 | 37840 | 2866.9135 | 937400 | 71021.2656 | 4228909.8333 | 320399.5397 | 3603118.1875 | 272987 | 1801776.875 | 136510 | 321300.3731 | 24343.033 | 115825.2156 | 8775.393 | 3924418.5606 | 297330.033 | 1917602.0906 | 145285.393 | 5990.8322 | 453.89 | 9900 | 750.0646 | 15890.8322 | 1203.9546 | 0 | 0 | 23029937.8255 | 1744842.4698 | 5401861.7106 | 409267.1808 | 13198863.6364 | 1420689.3494 | 36228801.4618 | 6822551.06
222-2013R | oh | 3 | 18.2794 | 18.2794 | 11.5523 | 11.5523 | 1.23 | 59110.7 | 5116.8027 | 113245 | 9802.833 | 43010 | 3723.0769 | 283682.1429 | 24556.3925 | 499047.8429 | 43199.105 | 4466000 | 386590.5961 | 8166419.9375 | 706910.2444 | 2793682.9067 | 241829.7224 | 10960102.8442 | 948739.9668 | 15426102.8442 | 1335330.5629 | 1250000 | 108203.8166 | 17175150.687 | 1486733.4846 | 199343.1 | 17255.7474 | 84823.2 | 7342.5552 | 284166.3 | 24598.3026 | 2805816 | 242880 | 50830 | 4400 | 2856646 | 247280 | 3140812.3 | 271878.3026 | 1200870 | 103950.9738 | 7231906 | 626015.8646 | 366932.5 | 31762.7976 | 60885 | 5270.3915 | 681010 | 58950.3049 | 54120 | 4684.7924 | 1340700 | 116055.0856 | 10936423.5 | 946690.2105 | 3153620.275 | 272987 | 1577000.75 | 136510 | 238870.2478 | 20677.338 | 93917.3202 | 8129.77 | 3392490.5228 | 293664.338 | 1670918.0702 | 144639.77 | 5243.4611 | 453.89 | 9900 | 856.9742 | 15143.4611 | 1310.8642 | 0 | 0 | 31519208.1709 | 2728398.8973 | 4811730.3702 | 416518.0726 | 11552272.7273 | 2459995.0931 | 43071480.8982 | 7271725.4633
222-2063 | oh | 3 | 4.7672 | 4.7672 | 4.7672 | 4.7672 | 6.7033 | 15491.08 | 3249.4896 | 29678 | 6225.4118 |  |  | 74344.2857 | 15594.8444 | 119513.3657 | 25069.7458 | 1170400 | 245509.1971 | 2140165.225 | 448932.1993 | 732137.5893 | 153576.9922 | 2872302.8143 | 602509.1915 | 4042702.8143 | 848018.3886 | 0 | 0 | 4162216.18 | 873088.1344 | 52241.64 | 10958.4784 | 1767.15 | 370.6866 | 54008.79 | 11329.165 | 1157866 | 242880 | 20975.8333 | 4400 | 1178841.8333 | 247280 | 1232850.6233 | 258609.165 | 213840 | 44856.1916 | 1287792 | 270133.9542 | 65340 | 13706.0586 | 1485 | 311.5013 | 16610 | 3484.2001 | 1320 | 276.8901 | 32700 | 6859.3222 | 1619087 | 339628.1181 | 1301393.1396 | 272987 | 650775.2292 | 136510 | 122946.5434 | 25789.907 | 89909.6059 | 18859.907 | 1424339.683 | 298776.907 | 740684.8351 | 155369.907 | 2163.8002 | 453.89 | 9900 | 2076.6755 | 12063.8002 | 2530.5655 | 0 | 0 | 7217706.6632 | 1514023.725 | 1973535.4584 | 413979.072 | 4767234.8485 | 13406619.5498 | 11984941.5117 | 15380155.0082
222-2085 | oh | 3 | 45.3472 | 45.3472 | 26.5778 | 26.5778 | 6.1699 | 121686.51 | 4578.4949 | 233128.5 | 8771.5364 | 68722.5 | 2585.7067 | 583993.9286 | 21972.9635 | 1007531.4386 | 37908.7015 | 9193800 | 345919.7469 | 16811561.0437 | 632540.51 | 5751133.432 | 216388.2857 | 22562694.4757 | 848928.7957 | 31756494.4757 | 1194848.5426 | 2775000 | 104410.2871 | 35539025.9143 | 1337167.5312 | 410371.83 | 15440.375 | 180838.35 | 6804.1024 | 591210.18 | 22244.4773 | 6455226 | 242880 | 116942.5 | 4400 | 6572168.5 | 247280 | 7163378.68 | 269524.4773 | 3147210 | 118414.8107 | 18953198 | 713120.3044 | 961647.5 | 36182.3033 | 137115 | 5158.9969 | 1533656.6667 | 57704.3362 | 121880 | 4585.7751 | 3019300 | 113602.1549 | 27874007.1667 | 1048768.6815 | 7255405.0562 | 272987 | 3628141.0625 | 136510 | 540976.5897 | 20354.422 | 214555.5742 | 8072.724 | 7796381.646 | 293341.422 | 3842696.6367 | 144582.724 | 12063.4162 | 453.89 | 9900 | 372.4908 | 21963.4162 | 826.3808 | 0 | 0 | 71231378.1432 | 2680104.0155 | 11006075.3167 | 414107.2013 | 26577840.9091 | 12339752.7253 | 97809219.0523 | 23345828.0419
230-127AE | oh | 2 | 13.6759 | 13.6759 | 9.7917 | 9.7917 | 11.9965 | 43619.62 | 4454.7697 | 83567 | 8534.5021 | 81345 | 8307.5745 | 209337.8571 | 21379.1854 | 417869.4771 | 42676.0317 | 3295600 | 336571.9149 | 6026254.7125 | 615447.2898 | 2061545.3173 | 210540.7984 | 8087800.0298 | 825988.0882 | 11383400.0298 | 1162560.003 | 3600000 | 367659.5745 | 15401269.507 | 1572895.6092 | 147101.46 | 15023.1278 | 88357.5 | 9023.7447 | 235458.96 | 24046.8725 | 2378200 | 242880 | 43083.3333 | 4400 | 2421283.3333 | 247280 | 2656742.2933 | 271326.8725 | 946440 | 96657.7021 | 5699672 | 582094.1617 | 289190 | 29534.2979 | 37620 | 3842.0426 | 420786.6667 | 42973.9574 | 33440 | 3415.1489 | 828400 | 84602.5532 | 8255548.6667 | 843119.8638 | 2672997.7083 | 272987 | 1336660.4167 | 136510 | 151936.2831 | 15516.897 | 70706.9665 | 7221.137 | 2824933.9915 | 288503.897 | 1407367.3831 | 143731.137 | 4444.3396 | 453.89 | 9900 | 1011.0638 | 14344.3396 | 1464.9538 | 0 | 0 | 26496096.5047 | 2705984.3239 | 4064109.6765 | 415058.0095 | 9791666.6667 | 23992984.4915 | 36287763.1714 | 28057094.168
230-133AE | oh | 2 | 12.4589 | 12.4589 | 9.582 | 9.582 | 12.6696 | 45250.26 | 4722.4196 | 86691 | 9047.269 | 34595 | 3610.4125 | 217163.5714 | 22663.6819 | 383699.8314 | 40043.7829 | 3418800 | 356793.7066 | 6251535.2625 | 652424.3707 | 2138612.432 | 223190.4343 | 8390147.6945 | 875614.805 | 11808947.6945 | 1232408.5116 | 1650000 | 172197.7349 | 13842647.5259 | 1444650.0294 | 152600.58 | 15925.7419 | 83645.1 | 8729.392 | 236245.68 | 24655.1339 | 2327278 | 242880 | 42160.8333 | 4400 | 2369438.8333 | 247280 | 2605684.5133 | 271935.1339 | 1285020 | 134107.5959 | 7738676 | 807625.7443 | 392645 | 40977.321 | 52470 | 5475.888 | 586886.6667 | 61248.821 | 46640 | 4867.456 | 1155400 | 120580.1593 | 11257737.6667 | 1174882.9854 | 2615763.5021 | 272987 | 1308039.8542 | 136510 | 148697.0431 | 15518.36 | 69194.3597 | 7221.28 | 2764460.5452 | 288505.36 | 1377234.2138 | 143731.28 | 4349.1774 | 453.89 | 9900 | 1033.1864 | 14249.1774 | 1487.0764 | 0 | 0 | 27879094.9152 | 2909525.4512 | 3982918.7272 | 415666.4139 | 9582007.5758 | 25339245.6526 | 37461102.4909 | 29322164.3797
230-1586R | oh | 2 | 16.371 | 16.371 | 7.1585 | 7.1585 | 8.7726 | 36281.74 | 5068.3278 | 69509 | 9709.9643 | 56100 | 7836.8124 | 174122.1429 | 24323.7536 | 336012.8829 | 46938.8581 | 2741200 | 382928.1689 | 5012492.2375 | 700213.2184 | 1714743.3013 | 239538.7102 | 6727235.5388 | 939751.9286 | 9468435.5388 | 1322680.0975 | 2275000 | 317803.0002 | 12079448.4217 | 1687421.9559 | 122355.42 | 17092.2723 | 110152.35 | 15387.5812 | 232507.77 | 32479.8536 | 1738662 | 242880 | 31497.5 | 4400 | 1770159.5 | 247280 | 2002667.27 | 279759.8536 | 806850 | 112711.8025 | 4859030 | 678775.5219 | 246537.5 | 34439.7174 | 40095 | 5601.016 | 448470 | 62648.4007 | 35640 | 4978.6808 | 882900 | 123335.5028 | 7319522.5 | 1022490.6421 | 1954183.6437 | 272987 | 977209.9375 | 136510 | 111061.4449 | 15514.576 | 51688.8149 | 7220.598 | 2065245.0886 | 288501.576 | 1028898.7524 | 143730.598 | 3249.1819 | 453.89 | 9900 | 1382.9669 | 13149.1819 | 1836.8569 | 0 | 0 | 21477365.1922 | 3000251.0309 | 3031566.0224 | 423490.4516 | 7158522.7273 | 17545271.4342 | 28635887.9195 | 20576837.4566
230-1606R | oh | 2 | 10.7066 | 10.7066 | 2.4663 | 2.4663 | 2.9812 | 10802.99 | 4380.2632 | 20696.5 | 8391.7616 | 9350 | 3791.1227 | 51845.3571 | 21021.6162 | 92694.8471 | 37584.7637 | 816200 | 330942.7123 | 1492483.6438 | 605153.8657 | 510569.6347 | 207019.4802 | 2003053.2784 | 812173.3459 | 2819253.2784 | 1143116.0582 | 475000 | 192597.1433 | 3386948.1256 | 1373297.9652 | 36431.67 | 14771.8644 | 57726.9 | 23406.3916 | 94158.57 | 38178.256 | 599012 | 242880 | 10851.6667 | 4400 | 609863.6667 | 247280 | 704022.2367 | 285458.256 | 269280 | 109184.3342 | 1621664 | 657532.3238 | 82280 | 33361.8799 | 9405 | 3813.4234 | 105196.6667 | 42653.8473 | 8360 | 3389.7097 | 207100 | 83972.3545 | 2303285.6667 | 933907.8728 | 673264.5292 | 272987 | 336672.9583 | 136510 | 38283.5677 | 15522.749 | 17811.5187 | 7221.995 | 711548.0969 | 288509.749 | 354484.4771 | 143731.995 | 1119.4234 | 453.89 | 9900 | 4014.1299 | 11019.4234 | 4468.0199 | 0 | 0 | 6412801.3125 | 2600183.607 | 1058506.7137 | 429190.251 | 2466287.8788 | 5962462.1874 | 8879089.1913 | 7020968.9011
230-181 | oh | 2 | 3.8195 | 3.8195 | 2.422 | 2.422 | 3.0685 | 9580.01 | 3955.4624 | 18353.5 | 7577.9231 | 3272.5 | 1351.173 | 45976.0714 | 18982.926 | 77182.0814 | 31867.4844 | 723800 | 298847.6697 | 1323523.2312 | 546465.6444 | 452769.2987 | 186942.5944 | 1776292.5299 | 733408.2388 | 2500092.5299 | 1032255.9085 | 150000 | 61933.0622 | 2727274.6113 | 1126056.4551 | 32307.33 | 13339.2792 | 12370.05 | 5107.4338 | 44677.38 | 18446.713 | 588248 | 242880 | 10656.6667 | 4400 | 598904.6667 | 247280 | 643582.0467 | 265726.713 | 137610 | 56817.3913 | 828718 | 342166.9565 | 42047.5 | 17360.8696 | 10890 | 4496.3403 | 121806.6667 | 50292.3991 | 9680 | 3996.747 | 239800 | 99010.3222 | 1390552.1667 | 574141.026 | 661166.2417 | 272987 | 330623.0833 | 136510 | 37620.2712 | 15532.924 | 17495.9288 | 7223.843 | 698786.5129 | 288519.924 | 348119.0122 | 143733.843 | 1099.3078 | 453.89 | 9900 | 4087.5821 | 10999.3078 | 4541.4721 | 0 | 0 | 4827612.5987 | 1993258.8772 | 991701.0588 | 409460.556 | 2421969.697 | 6137081.8367 | 7249582.2957 | 7128782.8955
230-2060R | oh | 2 | 10.8561 | 10.8561 | 8.228 | 8.228 | 10.5717 | 37504.72 | 4558.165 | 71852 | 8732.5882 | 31790 | 3863.6221 | 179991.4286 | 21875.3969 | 321138.1486 | 39029.7722 | 2833600 | 344383.7584 | 5181452.65 | 629731.8385 | 1772543.6373 | 215427.4562 | 6953996.2873 | 845159.2947 | 9787596.2873 | 1189543.0531 | 1375000 | 167111.684 | 11483734.4359 | 1395684.5093 | 126479.76 | 15371.815 | 71864.1 | 8734.0587 | 198343.86 | 24105.8738 | 1998424 | 242880 | 36203.3333 | 4400 | 2034627.3333 | 247280 | 2232971.1933 | 271385.8738 | 744480 | 90480.9502 | 4483424 | 544896.3889 | 227480 | 27646.957 | 43560 | 5294.0981 | 487226.6667 | 59215.4682 | 38720 | 4705.865 | 959200 | 116577.1108 | 6984090.6667 | 848816.8382 | 2246145.3083 | 272987 | 1123208.4167 | 136510 | 127787.9918 | 15530.812 | 59435.0123 | 7223.48 | 2373933.3001 | 288517.812 | 1182643.429 | 143733.48 | 3734.6207 | 453.89 | 9900 | 1203.2041 | 13634.6207 | 1657.0941 | 0 | 0 | 20855393.0233 | 2534676.2536 | 3415614.6223 | 415119.3538 | 8228030.303 | 21143401.4989 | 29083423.3264 | 24559016.1212
230-371AE | oh | 2 | 4.3672 | 4.3672 | 1.2375 | 1.2375 | 1.6524 | 6318.73 | 5106.0444 | 12105.5 | 9782.2222 | 10752.5 | 8688.8889 | 30324.6429 | 24504.7619 | 59501.3729 | 48081.9175 | 477400 | 385777.7778 | 872962.1312 | 705423.9444 | 298635.0693 | 241321.2681 | 1171597.2006 | 946745.2126 | 1648997.2006 | 1332522.9904 | 575000 | 464646.4646 | 2283498.5734 | 1845251.3725 | 21309.09 | 17219.4667 | 23562 | 19040 | 44871.09 | 36259.4667 | 300564 | 242880 | 5445 | 4400 | 306009 | 247280 | 350880.09 | 283539.4667 | 102960 | 83200 | 620048 | 501048.8889 | 31460 | 25422.2222 | 6435 | 5200 | 71976.6667 | 58162.963 | 5720 | 4622.2222 | 141700 | 114505.0505 | 980299.6667 | 792161.3468 | 337821.4125 | 272987 | 168931.125 | 136510 | 19233.1012 | 15541.9 | 8941.4251 | 7225.394 | 357054.5137 | 288528.9 | 177872.5501 | 143735.394 | 561.6889 | 453.89 | 9900 | 8000 | 10461.6889 | 8453.89 | 0 | 0 | 3631314.4427 | 2934395.5093 | 528752.6401 | 427274.8607 | 1237500 | 3304807.5797 | 4868814.4427 | 3833560.2198
231-1136R | oh | 2 | 16.1254 | 16.1254 | 11.6807 | 11.6807 | 15.3945 | 51772.82 | 4432.3457 | 99187 | 8491.542 | 100045 | 8564.9966 | 248466.4286 | 21271.5689 | 499471.2486 | 42760.4532 | 3911600 | 334877.7118 | 7152657.4625 | 612349.3109 | 2446880.8907 | 209480.9985 | 9599538.3532 | 821830.3094 | 13511138.3532 | 1156708.0213 | 4875000 | 417355.7739 | 18885609.6017 | 1616824.2484 | 174597.06 | 14947.5059 | 83645.1 | 7160.9775 | 258242.16 | 22108.4834 | 2837004 | 242880 | 51395 | 4400 | 2888399 | 247280 | 3146641.16 | 269388.4834 | 913770 | 78229.1663 | 5502926 | 471113.4235 | 279207.5 | 23903.3564 | 21780 | 1864.6172 | 243613.3333 | 20856.0885 | 19360 | 1657.4375 | 479600 | 41059.247 | 7460256.8333 | 638683.3363 | 3188674.2875 | 272987 | 1594529.875 | 136510 | 163962.3848 | 14037.056 | 81308.9458 | 6960.976 | 3352636.6723 | 287024.056 | 1675838.8208 | 143470.976 | 5301.7447 | 453.89 | 9900 | 847.5533 | 15201.7447 | 1301.4433 | 0 | 0 | 29713704.852 | 2543833.0839 | 4822479.9808 | 412859.4594 | 11680681.8182 | 30789031.632 | 41394386.6702 | 35611511.6128
231-1635R | oh | 2 | 50.4174 | 50.4174 | 26.3958 | 26.3958 | 0.66443 | 125355.45 | 4749.062 | 240157.5 | 9098.311 | 244502.5 | 9262.9203 | 601601.7857 | 22791.5436 | 1211617.2357 | 45901.8369 | 9471000 | 358806.6298 | 17318442.2812 | 656105.1535 | 5924534.44 | 224449.6078 | 23242976.7213 | 880554.7613 | 32713976.7213 | 1239361.3912 | 12075000 | 457458.5635 | 46000593.957 | 1742721.7916 | 422744.85 | 16015.5902 | 328100.85 | 12430.0243 | 750845.7 | 28445.6145 | 6411020 | 242880 | 116141.6667 | 4400 | 6527161.6667 | 247280 | 7278007.3667 | 275725.6145 | 3092760 | 117168.4925 | 18625288 | 705614.6993 | 945010 | 35801.4838 | 106920 | 4050.6393 | 1195920 | 45307.1507 | 95040 | 3600.5683 | 2354400 | 89195.8958 | 26415338 | 1000738.9298 | 7205719.3542 | 272987 | 3603295.2083 | 136510 | 370511.08 | 14036.726 | 183737.8588 | 6960.866 | 7576230.4342 | 287023.726 | 3787033.0671 | 143470.866 | 11980.8048 | 453.89 | 9900 | 375.0592 | 21880.8048 | 828.9492 | 0 | 0 | 80014043.196 | 3031313.3965 | 11065040.4338 | 419196.4805 | 26395833.3333 | 1328855.2505 | 106409876.5293 | 12393895.6843
233-123R | oh | 2 | 27.1652 | 27.1042 | 12.9273 | 12.9883 | 16.9609 | 59926.02 | 4613.8614 | 114807 | 8839.2919 | 110797.5 | 8530.59 | 286616.7857 | 22067.3777 | 572147.3057 | 44051.121 | 4527600 | 348591.7933 | 8279060.2125 | 637426.5497 | 2832216.464 | 218059.7703 | 11111276.6765 | 855486.32 | 15638876.6765 | 1204078.1133 | 5225000 | 402286.4475 | 21436023.9822 | 1650415.6818 | 202092.66 | 15559.6437 | 141372 | 10884.6009 | 343464.66 | 26444.2446 | 3154588 | 242880 | 57148.3333 | 4400 | 3211736.3333 | 247280 | 3555200.9933 | 273724.2446 | 1326600 | 102138.4117 | 7989080 | 615100.2129 | 405350 | 31208.9591 | 36135 | 2782.1284 | 404176.6667 | 31118.6211 | 32120 | 2473.003 | 795700 | 61263.029 | 10989161.6667 | 846084.3652 | 3528977.4 | 271705.2214 | 1764702 | 135869.0332 | 181470.8052 | 13971.913 | 89986.8618 | 6928.3244 | 3710448.2052 | 285677.1344 | 1854688.8618 | 142797.3576 | 5895.2402 | 453.89 | 9900 | 762.227 | 15795.2402 | 1216.117 | 0 | 0 | 36151429.0943 | 2783393.2984 | 5409889.8551 | 416521.6022 | 12988257.5758 | 33921727.479 | 49139686.6701 | 39331617.3341
233-41R | oh | 2 | 13.3646 | 13.2521 | 9.1436 | 9.2371 | 12.0439 | 45454.09 | 4920.8069 | 87081.5 | 9427.3419 | 84150 | 9109.9811 | 218141.7857 | 23615.776 | 434827.3757 | 47073.906 | 3434200 | 371782.4982 | 6279695.3312 | 679832.5135 | 2148245.8213 | 232566.5943 | 8427941.1526 | 912399.1078 | 11862141.1526 | 1284181.606 | 3975000 | 430328.8772 | 16271968.5283 | 1761584.3892 | 153287.97 | 16594.7774 | 75398.4 | 8162.5431 | 228686.37 | 24757.3205 | 2243512 | 242880 | 40643.3333 | 4400 | 2284155.3333 | 247280 | 2512841.7033 | 272037.3205 | 448470 | 48550.8406 | 2700786 | 292383.9514 | 137032.5 | 14834.9791 | 32670 | 3536.8162 | 365420 | 39559.9442 | 29040 | 3143.8366 | 719400 | 77881.4074 | 4432818.5 | 479891.7756 | 2496073.1792 | 270221.9795 | 1248187.4583 | 135127.3226 | 128353.6006 | 13895.4115 | 63648.81 | 6890.5461 | 2624426.7798 | 284117.3911 | 1311836.2683 | 142017.8688 | 4192.6369 | 453.89 | 9900 | 1071.7625 | 14092.6369 | 1525.6525 | 0 | 0 | 23343306.4451 | 2527119.2084 | 3824677.9717 | 414055.1893 | 9237121.2121 | 24087762.8705 | 32580427.6572 | 27912440.8422
233-81F | oh | 2 | 21.66 | 21.66 | 4.0311 | 4.0311 | 5.1031 | 18344.7 | 4550.8371 | 35145 | 8718.5491 | 34127.5 | 8466.1342 | 88039.2857 | 21840.2287 | 175656.4857 | 43575.7491 | 1386000 | 343830.1071 | 2534406.1875 | 628719.4451 | 867005.04 | 215081.1225 | 3401411.2275 | 843800.5676 | 4787411.2275 | 1187630.6747 | 1450000 | 359706.822 | 6413067.7132 | 1590913.2459 | 61865.1 | 15347.1024 | 126645.75 | 31417.476 | 188510.85 | 46764.5785 | 979064 | 242880 | 17736.6667 | 4400 | 996800.6667 | 247280 | 1185311.5167 | 294044.5785 | 360360 | 89395.8279 | 2170168 | 538361.5411 | 110110 | 27315.3918 | 20295 | 5034.6551 | 227003.3333 | 56313.5501 | 18040 | 4475.249 | 446900 | 110864.1233 | 3352876.3333 | 831760.3383 | 1100427.1417 | 272987 | 550280.0833 | 136510 | 56587.1057 | 14037.771 | 28060.3822 | 6961.042 | 1157014.2473 | 287024.771 | 578340.4655 | 143471.042 | 1829.6581 | 453.89 | 9900 | 2455.9293 | 11729.6581 | 2909.8193 | 0 | 0 | 10934687.952 | 2712608.1745 | 1763651.9822 | 437515.6205 | 4031060.6061 | 10206223.5718 | 14965748.558 | 11969875.554
233-86F | oh | 2 | 23.0947 | 22.9665 | 16.3538 | 16.3672 | 22.228 | 67263.9 | 4109.6679 | 128865 | 7873.3519 | 122952.5 | 7512.1119 | 322810.7143 | 19722.9842 | 641892.1143 | 39218.116 | 5082000 | 310498.3858 | 9292822.6875 | 567769.863 | 3179018.48 | 194230.6388 | 12471841.1675 | 762000.5018 | 17553841.1675 | 1072498.8876 | 6150000 | 375750.703 | 24345733.2818 | 1487467.7065 | 226838.7 | 13859.3172 | 117220.95 | 7161.9275 | 344059.65 | 21021.2448 | 3975274 | 242880 | 72015.8333 | 4400 | 4047289.8333 | 247280 | 4391349.4833 | 268301.2448 | 830610 | 50748.3401 | 5002118 | 305617.7813 | 253797.5 | 15506.4372 | 47025 | 2873.1182 | 525983.3333 | 32136.3589 | 41800 | 2553.8828 | 1035500 | 63266.6428 | 7736833.8333 | 472702.5612 | 4464371.4917 | 272762.7197 | 2232455.5833 | 136397.8463 | 253888.8445 | 15512.0182 | 118110.3922 | 7216.2704 | 4718260.3362 | 288274.7379 | 2350565.9756 | 143614.1167 | 7428.9242 | 453.89 | 9900 | 604.867 | 17328.9242 | 1058.757 | 0 | 0 | 36818156.3755 | 2249503.7626 | 6741915.4589 | 411915.3615 | 16367234.8485 | 44456074.7129 | 53185391.224 | 51197990.1718
234-48R | oh | 2 | 14.8633 | 14.8633 | 9.2966 | 9.2966 | 11.0533 | 44434.94 | 4779.7026 | 85129 | 9157.0126 | 92097.5 | 9906.5884 | 213250.7143 | 22938.5929 | 434912.1543 | 46781.8966 | 3357200 | 361121.6233 | 6138894.9875 | 660338.2947 | 2100078.8747 | 225897.7398 | 8238973.8622 | 886236.0346 | 11596173.8622 | 1247357.6578 | 4575000 | 492115.8783 | 16606086.0165 | 1786255.4326 | 149851.02 | 16118.9216 | 95426.1 | 10264.6337 | 245277.12 | 26383.5553 | 2257956 | 242880 | 40905 | 4400 | 2298861 | 247280 | 2544138.12 | 273663.5553 | 1260270 | 135562.5963 | 7589626 | 816388.0797 | 385082.5 | 41421.9044 | 29205 | 3141.4741 | 326663.3333 | 35137.9701 | 25960 | 2792.4215 | 643100 | 69175.8954 | 10259906.8333 | 1103620.3414 | 2537848.4625 | 272987 | 1269077.625 | 136510 | 130501.9826 | 14037.617 | 64713.9598 | 6961.042 | 2668350.4451 | 287024.617 | 1333791.5848 | 143471.042 | 4219.6296 | 453.89 | 9900 | 1064.9065 | 14119.6296 | 1518.7965 | 0 | 0 | 29548462.9245 | 3178419.1876 | 3877929.7048 | 417134.5973 | 9296590.9091 | 22106645.8189 | 38845053.8336 | 25984575.5237
235-897R | oh | 2 | 7.9962 | 7.9962 | 4.3263 | 4.3263 | 4.5748 | 27313.22 | 6313.2601 | 52327 | 12095.0208 | 46750 | 10805.9362 | 131080.7143 | 30298.3921 | 257470.9343 | 59512.6092 | 2063600 | 476986.7355 | 3773449.2125 | 872206.4458 | 1290874.1707 | 298376.5539 | 5064323.3832 | 1170582.9997 | 7127923.3832 | 1647569.7353 | 2125000 | 491178.917 | 9510394.3175 | 2198261.2615 | 92110.26 | 21290.6436 | 65973.6 | 15249.3371 | 158083.86 | 36539.9808 | 1050778 | 242880 | 19035.8333 | 4400 | 1069813.8333 | 247280 | 1227897.6933 | 283819.9808 | 165330 | 38214.8755 | 995654 | 230138.4722 | 50517.5 | 11676.7675 | 7425 | 1716.2369 | 83050 | 19196.4278 | 6600 | 1525.5439 | 163500 | 37791.8837 | 1472076.5 | 340260.2075 | 1181030.6896 | 272987 | 590586.7292 | 136510 | 73064.668 | 16888.388 | 32289.8654 | 7463.577 | 1254095.3576 | 289875.388 | 622876.5946 | 143973.577 | 1963.676 | 453.89 | 9900 | 2288.3159 | 11863.676 | 2742.2059 | 0 | 0 | 12248429.851 | 2831139.0629 | 1850774.2879 | 427793.5578 | 4326325.7576 | 9149613.1728 | 16574755.6086 | 11000387.4607
235-899R | oh | 2 | 12.9521 | 12.9521 | 9.9434 | 9.9434 | 0.039437 | 55849.42 | 5616.749 | 106997 | 10760.6362 | 100512.5 | 10108.4932 | 268030.7143 | 26955.7184 | 531389.6343 | 53441.5967 | 4219600 | 424363.1169 | 7715858.8375 | 775980.1654 | 2639548.6773 | 265458.1249 | 10355407.5148 | 1041438.2903 | 14575007.5148 | 1465801.4072 | 4925000 | 495304.8513 | 20031397.1491 | 2014547.8552 | 188344.86 | 18941.7508 | 101316.6 | 10189.3611 | 289661.46 | 29131.112 | 2415046 | 242880 | 43750.8333 | 4400 | 2458796.8333 | 247280 | 2748458.2933 | 276411.112 | 564300 | 56751.3762 | 3398340 | 341769.3987 | 172425 | 17340.6983 | 30690 | 3086.4784 | 343273.3333 | 34522.8319 | 27280 | 2743.5363 | 675800 | 67964.8769 | 5212108.3333 | 524179.1966 | 2714411.0771 | 272987 | 1357369.6042 | 136510 | 170914.9273 | 17188.831 | 74733.4235 | 7515.904 | 2885326.0044 | 290175.831 | 1432103.0276 | 144025.904 | 4513.1968 | 453.89 | 9900 | 995.6382 | 14413.1968 | 1449.5282 | 0 | 0 | 28143244.6836 | 2830352.411 | 4180561.321 | 420437.016 | 9943371.2121 | 78874.4694 | 38086615.8958 | 4259435.7904
236-1535R | oh | 3 | 7.6265 | 7.6265 | 6.7146 | 6.7146 | 8.4134 | 33224.29 | 4948.0792 | 63651.5 | 9479.5904 | 60775 | 9051.1945 | 159448.9286 | 23746.6602 | 317099.7186 | 47225.5243 | 2510200 | 373843.0034 | 4590091.2062 | 683600.3038 | 1570242.4613 | 233855.5326 | 6160333.6676 | 917455.8363 | 8670533.6676 | 1291298.8397 | 2975000 | 443065.467 | 11962633.3862 | 1781589.831 | 112044.57 | 16686.7495 | 51836.4 | 7719.9727 | 163880.97 | 24406.7222 | 1630838 | 242880 | 29544.1667 | 4400 | 1660382.1667 | 247280 | 1824263.1367 | 271686.7222 | 746460 | 111169.9659 | 4495348 | 669490.2389 | 228085 | 33968.6007 | 30690 | 4570.6485 | 343273.3333 | 51123.5495 | 27280 | 4062.7986 | 675800 | 100646.6025 | 6546936.3333 | 975032.4046 | 1832993.9604 | 272987 | 916607.7708 | 136510 | 113949.7827 | 16970.492 | 50213.1179 | 7478.218 | 1946943.7432 | 289957.492 | 966820.8888 | 143988.218 | 3047.6822 | 453.89 | 9900 | 1474.4027 | 12947.6822 | 1928.2927 | 0 | 0 | 20469461.1449 | 3048508.0203 | 2791084.0254 | 415674.9402 | 6714583.3333 | 16826780.3039 | 27184044.4782 | 19617864.3294
236-1561R | oh | 3 | 4.4405 | 4.4405 | 4.4405 | 4.4405 | 6.1074 | 19975.34 | 4498.4132 | 38269 | 8618.1148 | 23375 | 5264.0109 | 95865 | 21588.6377 | 177484.34 | 39969.1766 | 1509200 | 339869.3167 | 2759686.7375 | 621476.8393 | 944072.1547 | 212603.4708 | 3703758.8922 | 834080.3101 | 5212958.8922 | 1173949.6268 | 850000 | 191418.5789 | 6240443.2322 | 1405337.3823 | 67364.22 | 15170.3097 | 26507.25 | 5969.3884 | 93871.47 | 21139.6981 | 1078516 | 242880 | 19538.3333 | 4400 | 1098054.3333 | 247280 | 1191925.8033 | 268419.6981 | 220770 | 49717.0349 | 1329526 | 299407.0323 | 67457.5 | 15191.3162 | 20295 | 4570.4001 | 227003.3333 | 51120.7711 | 18040 | 4062.5778 | 446900 | 100641.1328 | 2329991.8333 | 524710.2653 | 1212207.0458 | 272987 | 606176.7917 | 136510 | 83398.1058 | 18781.114 | 34617.4817 | 7795.799 | 1295605.1517 | 291768.114 | 640794.2734 | 144305.799 | 2015.5123 | 453.89 | 9900 | 2229.4634 | 11915.5123 | 2683.3534 | 0 | 0 | 9877955.7295 | 2224499.1151 | 1832720.0767 | 412725.4971 | 4440530.303 | 12214844.1959 | 14318486.0325 | 14047564.2726
236-1563R | oh | 3 | 3.6261 | 3.6261 | 3.6028 | 3.6028 | 5.5123 | 14268.1 | 3960.2359 | 27335 | 7587.0683 | 26647.5 | 7396.2466 | 68475 | 19005.835 | 136725.6 | 37949.3859 | 1078000 | 299208.3268 | 1971204.8125 | 547125.1333 | 674337.2533 | 187168.2015 | 2645542.0658 | 734293.3348 | 3723542.0658 | 1033501.6615 | 1325000 | 367765.3367 | 5185267.6658 | 1439216.3841 | 48117.3 | 13355.3774 | 16493.4 | 4577.8874 | 64610.7 | 17933.2648 | 875058 | 242880 | 15852.5 | 4400 | 890910.5 | 247280 | 955521.2 | 265213.2648 | 150480 | 41767.0399 | 906224 | 251530.3958 | 45980 | 12762.1511 | 14355 | 3984.3558 | 160563.3333 | 44565.7572 | 12760 | 3541.6496 | 316100 | 87736.3192 | 1606462.3333 | 445887.6686 | 983528.7312 | 272987 | 491823.8125 | 136510 | 67659.223 | 18779.409 | 28086.7858 | 7795.733 | 1051187.9542 | 291766.409 | 519910.5983 | 144305.733 | 1635.2935 | 453.89 | 9900 | 2747.8316 | 11535.2935 | 3201.7216 | 0 | 0 | 7854453.2469 | 2180072.1833 | 1475431.7983 | 409518.9978 | 3602840.9091 | 11024559.6535 | 11457294.156 | 12499991.4518
236-1567R | oh | 3 | 7.2792 | 7.2792 | 5.4419 | 5.4419 | 6.6125 | 26090.24 | 4794.3642 | 49984 | 9185.1015 | 35530 | 6529.0224 | 125211.4286 | 23008.9564 | 236815.6686 | 43517.4444 | 1971200 | 362229.353 | 3604488.8 | 662363.8626 | 1233073.8347 | 226590.6744 | 4837562.6347 | 888954.537 | 6808762.6347 | 1251183.89 | 1800000 | 330769.4985 | 8845578.3032 | 1625470.8329 | 87985.92 | 16168.3659 | 43000.65 | 7901.8352 | 130986.57 | 24070.2011 | 1321718 | 242880 | 23944.1667 | 4400 | 1345662.1667 | 247280 | 1476648.7367 | 271350.2011 | 493020 | 90597.7656 | 2969076 | 545599.8775 | 150645 | 27682.6506 | 26235 | 4820.9654 | 293443.3333 | 53923.3912 | 23320 | 4285.3026 | 577700 | 106158.6329 | 4533439.3333 | 833068.5859 | 1485555.9604 | 272987 | 742867.7708 | 136510 | 102141.5649 | 18769.619 | 42410.8059 | 7793.445 | 1587697.5253 | 291756.619 | 785278.5767 | 144303.445 | 2470.004 | 453.89 | 9900 | 1819.2322 | 12370.004 | 2273.1222 | 0 | 0 | 14979085.1659 | 2752569.1601 | 2261927.3134 | 415653.6461 | 5441856.0606 | 13224926.9842 | 20420941.2266 | 15486854.2976
236-1569R | oh | 3 | 15.536 | 15.536 | 13.5648 | 13.5648 | 16.0274 | 62779.64 | 4628.138 | 120274 | 8866.6432 | 112200 | 8271.425 | 301290 | 22211.2088 | 596543.64 | 43977.415 | 4743200 | 349670.4365 | 8673301.175 | 639398.9306 | 2967083.9147 | 218734.5099 | 11640385.0897 | 858133.4405 | 16383585.0897 | 1207803.8769 | 5300000 | 390717.9358 | 22280128.7297 | 1642499.2278 | 211716.12 | 15607.7897 | 100727.55 | 7425.6718 | 312443.67 | 23033.4615 | 3294612 | 242880 | 59685 | 4400 | 3354297 | 247280 | 3666740.67 | 270313.4615 | 849420 | 62619.5527 | 5115396 | 377108.8615 | 259545 | 19133.7522 | 73755 | 5437.2455 | 824963.3333 | 60816.5983 | 65560 | 4833.1071 | 1624100 | 119729.2452 | 8812739.3333 | 649678.3625 | 3703006.6125 | 272987 | 1851727.125 | 136510 | 254028.9096 | 18727.104 | 105612.9059 | 7785.822 | 3957035.5221 | 291714.104 | 1957340.0309 | 144295.822 | 6156.9147 | 453.89 | 9900 | 729.8316 | 16056.9147 | 1183.7216 | 0 | 0 | 35065960.4998 | 2585075.4159 | 5624080.7009 | 414609.2835 | 13564772.7273 | 32054811.6835 | 48630733.2271 | 37678892.3844
236-1573R | oh | 3 | 8.1616 | 8.1616 | 6.2801 | 6.2801 | 7.6873 | 26701.73 | 4251.7909 | 51155.5 | 8145.6329 | 44880 | 7146.3675 | 128146.0714 | 20405.0562 | 250883.3014 | 39948.8474 | 2017400 | 321236.2255 | 3688969.0063 | 587404.8178 | 1261974.0027 | 200947.6382 | 4950943.0089 | 788352.456 | 6968343.0089 | 1109588.6814 | 2125000 | 338369.6734 | 9344226.3103 | 1487907.2022 | 90048.09 | 14338.6084 | 45356.85 | 7222.2977 | 135404.94 | 21560.906 | 1525314 | 242880 | 27632.5 | 4400 | 1552946.5 | 247280 | 1688351.44 | 268840.906 | 201960 | 32158.6538 | 1216248 | 193666.5593 | 61710 | 9826.2553 | 33165 | 5280.9554 | 370956.6667 | 59068.4641 | 29480 | 4694.1826 | 730300 | 116287.7047 | 2643819.6667 | 420982.7751 | 1714389.3812 | 272987 | 857298.3125 | 136510 | 117907.8775 | 18774.8 | 48950.8356 | 7794.578 | 1832297.2587 | 291761.8 | 906249.1481 | 144304.578 | 2850.4808 | 453.89 | 9900 | 1576.4046 | 12750.4808 | 2030.2946 | 0 | 0 | 13833093.7165 | 2202682.0719 | 2594600.5881 | 413145.484 | 6280113.6364 | 15374660.8533 | 20113207.3529 | 17969261.4414
237-1761R | oh | 3 | 7.4354 | 7.4354 | 7.3464 | 7.3464 | 0.087683 | 23236.62 | 3162.9935 | 44517 | 6059.7015 | 19635 | 2672.7371 | 111516.4286 | 15179.7351 | 198905.0486 | 27075.1671 | 1755600 | 238974.1422 | 3210247.8375 | 436982.3554 | 1098206.384 | 149489.0229 | 4308454.2215 | 586471.3782 | 6064054.2215 | 825445.5204 | 500000 | 68060.5326 | 6762959.2701 | 920581.2201 | 78362.46 | 10666.7815 | 10013.85 | 1363.0959 | 88376.31 | 12029.8775 | 1784294 | 242880 | 32324.1667 | 4400 | 1816618.1667 | 247280 | 1904994.4767 | 259309.8775 | 108900 | 14823.584 | 655820 | 89270.917 | 33275 | 4529.4284 | 9900 | 1347.5985 | 110733.3333 | 15073.1393 | 8800 | 1197.8654 | 218000 | 29674.3922 | 1145428.3333 | 155916.9249 | 2005472.1104 | 272987 | 1002857.2708 | 136510 | 128904.0897 | 17546.562 | 55682.1752 | 7579.517 | 2134376.2001 | 290533.562 | 1058539.446 | 144089.517 | 3334.4582 | 453.89 | 9900 | 1347.5985 | 13234.4582 | 1801.4885 | 0 | 0 | 10055998.2617 | 1368833.1955 | 2963533.9227 | 403399.3945 | 7346401.5152 | 175365.9091 | 17402399.7768 | 3138899.8318
237-1765R | oh | 3 | 8.208 | 8.208 | 7.3027 | 7.3027 | 0 | 32408.97 | 4437.973 | 62089.5 | 8502.3227 | 28050 | 3841.0706 | 155536.0714 | 21298.5751 | 278084.5414 | 38079.9414 | 2448600 | 335302.8684 | 4477450.9313 | 613126.742 | 1531708.904 | 209746.953 | 6009159.8352 | 822873.695 | 8457759.8352 | 1158176.5634 | 1325000 | 181440.9461 | 10060844.3767 | 1377697.4508 | 109295.01 | 14966.483 | 48302.1 | 6614.3236 | 157597.11 | 21580.8066 | 1773668 | 242880 | 32131.6667 | 4400 | 1805799.6667 | 247280 | 1963396.7767 | 268860.8066 | 305910 | 41890.264 | 1842258 | 252272.4789 | 93472.5 | 12799.8029 | 37125 | 5083.7699 | 415250 | 56862.9078 | 33000 | 4518.9066 | 817500 | 111945.6403 | 3544515.5 | 485373.7704 | 1993528.9292 | 272987 | 996884.9583 | 136510 | 152665.3403 | 20905.467 | 59659.8294 | 8169.612 | 2146194.2694 | 293892.467 | 1056544.7878 | 144679.612 | 3314.6005 | 453.89 | 9900 | 1355.672 | 13214.6005 | 1809.562 | 0 | 0 | 15764768.7466 | 2158773.2502 | 3019941.5644 | 413540.4186 | 7302651.5152 | 0 | 23067420.2618 | 3019941.5644
237-17R | oh | 2 | 12.2879 | 12.2879 | 10.4949 | 10.4949 | 0.084091 | 57887.72 | 5515.8025 | 110902 | 10567.2416 | 97240 | 9265.4648 | 277812.8571 | 26471.2592 | 543842.5771 | 51819.7681 | 4373600 | 416736.2893 | 7997459.525 | 762033.9323 | 2735882.5707 | 260687.2029 | 10733342.0957 | 1022721.1352 | 15106942.0957 | 1439457.4245 | 4775000 | 454983.4876 | 20425784.6728 | 1946260.6802 | 195218.76 | 18601.3219 | 94248 | 8980.3736 | 289466.76 | 27581.6955 | 2548998 | 242880 | 46177.5 | 4400 | 2595175.5 | 247280 | 2884642.26 | 274861.6955 | 851400 | 81125.2233 | 5127320 | 488554.1227 | 260150 | 24788.2627 | 40095 | 3820.432 | 448470 | 42732.2397 | 35640 | 3395.9396 | 882900 | 84126.6851 | 7645975 | 728542.9051 | 2864967.5437 | 272987 | 1432656.9375 | 136510 | 180401.6392 | 17189.48 | 78882.4835 | 7516.278 | 3045369.183 | 290176.48 | 1511539.421 | 144026.278 | 4763.524 | 453.89 | 9900 | 943.3166 | 14663.524 | 1397.2066 | 0 | 0 | 31131792.3798 | 2966377.2719 | 4396181.681 | 418887.9735 | 10494886.3636 | 168181.8182 | 41626678.7434 | 4564363.4992
237-26F | oh | 2 | 3.3064 | 3.3064 | 1.7693 | 1.7693 | 0.016365 | 14675.76 | 8294.585 | 28116 | 15890.8671 | 21972.5 | 12418.6256 | 70431.4286 | 39807.1016 | 135195.6886 | 76411.1792 | 1108800 | 626682.0809 | 2027524.95 | 1145935.7457 | 693604.032 | 392017.6931 | 2721128.982 | 1537953.4388 | 3829928.982 | 2164635.5197 | 1200000 | 678227.3603 | 5165124.6706 | 2919274.0592 | 49492.08 | 27972.4023 | 22383.9 | 12651.1445 | 71875.98 | 40623.5468 | 429732 | 242880 | 7785 | 4400 | 437517 | 247280 | 509392.98 | 287903.5468 | 28710 | 16226.5896 | 172898 | 97720.1285 | 8772.5 | 4958.1246 | 1485 | 839.3064 | 16610 | 9387.797 | 1320 | 746.0501 | 32700 | 18481.6956 | 262495.5 | 148359.6917 | 483000.8625 | 272987 | 241529.625 | 136510 | 30044.4364 | 16980.799 | 13234.9282 | 7480.242 | 513045.2989 | 289967.799 | 254764.5532 | 143990.242 | 803.0758 | 453.89 | 9900 | 5595.3757 | 10703.0758 | 6049.2657 | 0 | 0 | 5951368.5453 | 3363650.8156 | 764157.5332 | 431893.7888 | 1769318.1818 | 32730.9864 | 7720686.7271 | 796888.5196
237-28F | oh | 2 | 2.8803 | 2.8803 | 1.4282 | 1.4282 | 0 | 8764.69 | 6136.794 | 16791.5 | 11756.9447 | 14025 | 9819.9178 | 42063.2143 | 29451.5013 | 81644.4043 | 57165.1578 | 662200 | 463654.1573 | 1210882.9563 | 847826.8146 | 414235.7413 | 290036.4294 | 1625118.6976 | 1137863.244 | 2287318.6976 | 1601517.4013 | 575000 | 402599.1248 | 2943963.1019 | 2061281.6838 | 29557.77 | 20695.5345 | 14137.2 | 9898.4771 | 43694.97 | 30594.0116 | 346886 | 242880 | 6284.1667 | 4400 | 353170.1667 | 247280 | 396865.1367 | 277874.0116 | 32670 | 22874.632 | 196746 | 137756.1172 | 9982.5 | 6989.4709 | 8910 | 6238.536 | 99660 | 69779.1805 | 7920 | 5545.3653 | 196200 | 137373.8231 | 552088.5 | 386557.125 | 389885.4104 | 272987 | 194966.2708 | 136510 | 24322.6314 | 17030.035 | 10695.6831 | 7488.822 | 414208.0418 | 290017.035 | 205661.9539 | 143998.822 | 648.2546 | 453.89 | 9900 | 6931.7067 | 10548.2546 | 7385.5967 | 0 | 0 | 3920807.8984 | 2745241.4406 | 602527.0906 | 421872.8336 | 1428219.697 | 0 | 5349027.5953 | 602527.0906
237-2R | oh | 3 | 21.0485 | 21.0485 | 14.6977 | 14.6977 | 0.068561 | 70321.35 | 4784.505 | 134722.5 | 9166.2131 | 62645 | 4262.2236 | 337483.9286 | 22961.6404 | 605172.7786 | 41174.5821 | 5313000 | 361484.4596 | 9715223.7188 | 661001.7684 | 3323519.32 | 226124.7102 | 13038743.0388 | 887126.4786 | 18351743.0388 | 1248610.9382 | 2650000 | 180299.9845 | 21606915.8173 | 1470085.5048 | 237149.55 | 16135.1171 | 124878.6 | 8496.4565 | 362028.15 | 24631.5735 | 3569784 | 242880 | 64670 | 4400 | 3634454 | 247280 | 3996482.15 | 271911.5735 | 930600 | 63315.9116 | 5604280 | 381302.4896 | 284350 | 19346.5285 | 91080 | 6196.8764 | 1018746.6667 | 69313.2107 | 80960 | 5508.3346 | 2005600 | 136456.4713 | 10015616.6667 | 681439.8227 | 4012288.475 | 272987 | 2006386.75 | 136510 | 257663.5493 | 17530.843 | 111364.9735 | 7577.02 | 4269952.0243 | 290517.843 | 2117751.7235 | 144087.02 | 6671.1514 | 453.89 | 9900 | 673.5735 | 16571.1514 | 1127.4635 | 0 | 0 | 35909055.6597 | 2443170.634 | 6114233.8735 | 415998.5935 | 14697727.2727 | 137121.2121 | 50606782.9324 | 6251355.0856
237-30R | oh | 3 | 39.8695 | 39.8695 | 31.7307 | 31.7307 | 5.0304 | 115571.61 | 3642.2668 | 221413.5 | 6977.8992 | 144457.5 | 4552.6125 | 554647.5 | 17479.8482 | 1036090.11 | 32652.6268 | 8731800 | 275184.7581 | 15966758.9812 | 503196.2147 | 5462131.752 | 172140.384 | 21428890.7332 | 675336.5987 | 30160690.7332 | 950521.3568 | 4600000 | 144970.0963 | 35796780.8432 | 1128144.0799 | 389750.13 | 12283.0682 | 136659.6 | 4306.8599 | 526409.73 | 16589.9281 | 7706748 | 242880 | 139615 | 4400 | 7846363 | 247280 | 8372772.73 | 263869.9281 | 1161270 | 36597.7008 | 6993426 | 220399.4872 | 354832.5 | 11182.6308 | 103455 | 3260.409 | 1157163.3333 | 36468.2782 | 91960 | 2898.1413 | 2278100 | 71794.8644 | 12140206.8333 | 382601.5118 | 8662063.6375 | 272987 | 4331555.375 | 136510 | 792657.8798 | 24980.802 | 282045.3365 | 8888.726 | 9454721.5173 | 297967.802 | 4613600.7115 | 145398.726 | 14402.2392 | 453.89 | 9900 | 312.0009 | 24302.2392 | 765.8909 | 0 | 0 | 57416011.4331 | 1809479.2845 | 12986373.4415 | 409268.6541 | 31730681.8182 | 10060781.2566 | 89146693.2513 | 23047154.698
239-2207R | oh | 3 | 6.9589 | 6.9589 | 6.8148 | 6.8148 | 9.42 | 22625.13 | 3320.0124 | 43345.5 | 6360.5203 | 44412.5 | 6517.0919 | 108581.7857 | 15933.2952 | 218964.9157 | 32130.9198 | 1709400 | 250837.4187 | 3125767.6313 | 458675.2569 | 1069306.216 | 156910.0334 | 4195073.8472 | 615585.2902 | 5904473.8472 | 866422.709 | 2025000 | 297148.5743 | 8148438.763 | 1195702.203 | 76300.29 | 11196.3074 | 18260.55 | 2679.5538 | 94560.84 | 13875.8611 | 1655172 | 242880 | 29985 | 4400 | 1685157 | 247280 | 1779717.84 | 261155.8611 | 713790 | 104741.5708 | 4298602 | 630777.0152 | 218102.5 | 32004.3689 | 14850 | 2179.0895 | 166100 | 24373.5201 | 13200 | 1936.9685 | 327000 | 47983.992 | 5751644.5 | 843996.5249 | 1860344.3625 | 272987 | 930284.625 | 136510 | 105956.5702 | 15548.071 | 49246.3895 | 7226.417 | 1966300.9327 | 288535.071 | 979531.0145 | 143736.417 | 3093.1572 | 453.89 | 9900 | 1452.7264 | 12993.1572 | 1906.6164 | 0 | 0 | 15879377.3529 | 2330140.4153 | 2759248.8545 | 404892.2781 | 6814772.7273 | 18840051.5404 | 22694150.0801 | 21599300.3949
239-2211R | oh | 3 | 2.7451 | 2.7451 | 2.7451 | 2.7451 | 3.9166 | 10599.16 | 3861.1539 | 20306 | 7397.2458 | 18700 | 6812.1982 | 50867.1429 | 18530.3239 | 100472.3029 | 36600.9217 | 800800 | 291722.3679 | 1464323.575 | 533436.4893 | 500936.2453 | 182485.3992 | 1965259.8203 | 715921.8885 | 2766059.8203 | 1007644.2563 | 625000 | 227680.4195 | 3491532.1232 | 1271925.5975 | 35744.28 | 13021.2363 | 13548.15 | 4935.4376 | 49292.43 | 17956.6738 | 666724 | 242880 | 12078.3333 | 4400 | 678802.3333 | 247280 | 728094.7633 | 265236.6738 | 125730 | 45802.0146 | 757174 | 275829.9103 | 38417.5 | 13995.06 | 12870 | 4688.3952 | 143953.3333 | 52440.5685 | 11440 | 4167.4624 | 283400 | 103239.4094 | 1372984.8333 | 500162.8205 | 749369.9958 | 272987 | 374730.2917 | 136510 | 47333.6295 | 17243.105 | 20658.9323 | 7525.815 | 796703.6254 | 290230.105 | 395389.224 | 144035.815 | 1245.9624 | 453.89 | 9900 | 3606.4578 | 11145.9624 | 4060.3478 | 0 | 0 | 5672366.5443 | 2066378.8708 | 1123483.9873 | 409272.4888 | 2745075.7576 | 7833287.7624 | 8417442.3019 | 8956771.7497
239-2213R | oh | 3 | 6.0583 | 6.0583 | 5.4023 | 5.4023 | 7.8552 | 22828.96 | 4225.8066 | 43736 | 8095.8519 | 35530 | 6576.8616 | 109560 | 20280.3534 | 211654.96 | 39178.8735 | 1724800 | 319273.0332 | 3153927.7 | 583814.9718 | 1078939.6053 | 199719.5736 | 4232867.3053 | 783534.5454 | 5957667.3053 | 1102807.5786 | 1475000 | 273033.2352 | 7644322.2653 | 1415019.6873 | 76987.68 | 14250.9799 | 25329.15 | 4688.61 | 102316.83 | 18939.5899 | 1312104 | 242880 | 23770 | 4400 | 1335874 | 247280 | 1438190.83 | 266219.5899 | 498960 | 92361.1275 | 3004848 | 556219.2343 | 152460 | 28221.4556 | 15840 | 2932.0993 | 177173.3333 | 32796.0735 | 14080 | 2606.3105 | 348800 | 64565.4186 | 4212161.3333 | 779701.7193 | 1474750.225 | 272987 | 737464.25 | 136510 | 93152.1936 | 17243.149 | 40657.0994 | 7525.925 | 1567902.4186 | 290230.149 | 778121.3494 | 144035.925 | 2452.0376 | 453.89 | 9900 | 1832.5621 | 12352.0376 | 2286.4521 | 0 | 0 | 13436738.0548 | 2487238.0076 | 2216312.1794 | 410255.5149 | 5402272.7273 | 15710369.7872 | 18839010.7821 | 17926681.9665
239-2215R | oh | 3 | 12.5752 | 12.5752 | 12.0589 | 12.0589 | 16.9011 | 51365.16 | 4259.5223 | 98406 | 8160.4448 | 69657.5 | 5776.4383 | 246510 | 20442.1605 | 465938.66 | 38638.5658 | 3880800 | 321820.3578 | 7096337.325 | 588472.9481 | 2427614.112 | 201313.0391 | 9523951.437 | 789785.9871 | 13404751.437 | 1111606.3449 | 3550000 | 294388.3401 | 17420690.097 | 1444633.2508 | 173222.28 | 14364.6815 | 57726.9 | 4787.0778 | 230949.18 | 19151.7594 | 2928866 | 242880 | 53059.1667 | 4400 | 2981925.1667 | 247280 | 3212874.3467 | 266431.7594 | 849420 | 70439.2518 | 5115396 | 424200.8274 | 259545 | 21523.1047 | 52965 | 4392.1911 | 592423.3333 | 49127.4709 | 47080 | 3904.1699 | 1166300 | 96716.9355 | 8083129.3333 | 670303.9512 | 3291923.3479 | 272987 | 1646160.6458 | 136510 | 207654.477 | 17220.016 | 90705.176 | 7521.844 | 3499577.8249 | 290207.016 | 1736865.8218 | 144031.844 | 5473.4148 | 453.89 | 9900 | 820.9703 | 15373.4148 | 1274.8603 | 0 | 0 | 29018770.6701 | 2406419.0784 | 4949740.1685 | 410463.6034 | 12058901.5152 | 33802256.8151 | 41077672.1852 | 38751996.9836
239-2217R | oh | 3 | 15.8422 | 15.8422 | 4.9148 | 4.9148 | 7.2656 | 20790.66 | 4230.2383 | 39831 | 8104.3422 | 41140 | 8370.6821 | 99777.8571 | 20301.6218 | 201539.5171 | 41006.8844 | 1570800 | 319607.8613 | 2872327.0125 | 584427.2303 | 982605.712 | 199929.0235 | 3854932.7245 | 784356.2538 | 5425732.7245 | 1103964.115 | 1825000 | 371329.4798 | 7452272.2416 | 1516300.4792 | 70113.78 | 14265.9252 | 63617.4 | 12944.1184 | 133731.18 | 27210.0436 | 1193700 | 242880 | 21625 | 4400 | 1215325 | 247280 | 1349056.18 | 274490.0436 | 609840 | 124083.052 | 3672592 | 747255.7133 | 186340 | 37914.2659 | 12375 | 2517.9191 | 138416.6667 | 28163.3911 | 11000 | 2238.1503 | 272500 | 55445.0867 | 4903063.6667 | 997617.5784 | 1341669.0625 | 272987 | 670915.625 | 136510 | 76319.7609 | 15528.645 | 35499.4378 | 7223.007 | 1417988.8234 | 288515.645 | 706415.0628 | 143733.007 | 2230.7662 | 453.89 | 9900 | 2014.3353 | 12130.7662 | 2468.2253 | 0 | 0 | 13785455.4979 | 2804901.9279 | 2055471.2428 | 418223.0506 | 4914772.7273 | 14531212.058 | 18700228.2252 | 16586683.3008
239-89R | oh | 3 | 2.9216 | 2.9216 | 2.8193 | 2.8193 | 3.8333 | 9580.01 | 3397.9882 | 18353.5 | 6509.9073 | 7480 | 2653.1237 | 45976.0714 | 16307.5143 | 81389.5814 | 28868.5335 | 723800 | 256728.7384 | 1323523.2312 | 469447.9821 | 452769.2987 | 160595.3175 | 1776292.5299 | 630043.2996 | 2500092.5299 | 886772.038 | 325000 | 115276.0983 | 2906482.1113 | 1030916.6699 | 32307.33 | 11459.2706 | 5890.5 | 2089.3349 | 38197.83 | 13548.6056 | 684756 | 242880 | 12405 | 4400 | 697161 | 247280 | 735358.83 | 260828.6056 | 58410 | 20717.7751 | 351758 | 124767.0455 | 17847.5 | 6330.4313 | 8910 | 3160.3386 | 99660 | 35348.9722 | 7920 | 2809.1898 | 196200 | 69591.2938 | 740705.5 | 262725.0464 | 769637.2125 | 272987 | 384865.125 | 136510 | 43846.2168 | 15552.064 | 20375.5846 | 7227.132 | 813483.4293 | 288539.064 | 405240.7096 | 143737.132 | 1279.6603 | 453.89 | 9900 | 3511.4873 | 11179.6603 | 3965.3773 | 0 | 0 | 4471850.701 | 1586146.1575 | 1140599.5396 | 404565.7376 | 2819318.1818 | 7666577.5692 | 7291168.8828 | 8807177.1088
240-1028R | oh | 2 | 4.7691 | 4.7691 | 4.7506 | 4.7506 | 6.1194 | 20383 | 4290.6447 | 39050 | 8220.0694 | 38802.5 | 8167.9703 | 97821.4286 | 20591.5219 | 196056.9286 | 41270.2062 | 1540000 | 324171.7498 | 2816006.875 | 592772.6468 | 963338.9333 | 202783.94 | 3779345.8083 | 795556.5869 | 5319345.8083 | 1119728.3366 | 1625000 | 342064.3464 | 7140402.7369 | 1503062.8892 | 68739 | 14469.6376 | 21794.85 | 4587.8407 | 90533.85 | 19057.4783 | 1153818 | 242880 | 20902.5 | 4400 | 1174720.5 | 247280 | 1265254.35 | 266337.4783 | 215820 | 45430.3552 | 1299716 | 273591.6948 | 65945 | 13881.4974 | 10395 | 2188.1593 | 116270 | 24474.9671 | 9240 | 1945.0305 | 228900 | 48183.7101 | 1946286 | 409695.4144 | 1296843.3562 | 272987 | 648500.0625 | 136510 | 69480.3803 | 14625.699 | 33560.845 | 7064.596 | 1366323.7366 | 287612.699 | 682060.9075 | 143574.596 | 2156.2354 | 453.89 | 9900 | 2083.9612 | 12056.2354 | 2537.8512 | 0 | 0 | 10465068.7089 | 2202908.8539 | 1947315.2575 | 409912.0743 | 4750568.1818 | 12238846.4106 | 15215636.8907 | 14186161.668
240-1044 | oh | 3 | 2.1725 | 2.1725 | 2.1725 | 2.1725 | 2.3866 | 8357.03 | 3846.6671 | 16010.5 | 7369.4918 | 15427.5 | 7101.142 | 40106.7857 | 18460.7993 | 79901.8157 | 36778.1002 | 631400 | 290627.8441 | 1154562.8188 | 531435.0696 | 394968.9627 | 181800.7256 | 1549531.7814 | 713235.7951 | 2180931.7814 | 1003863.6393 | 275000 | 126580.0715 | 2535833.5971 | 1167221.8109 | 28182.99 | 12972.3814 | 8246.7 | 3795.8832 | 36429.69 | 16768.2646 | 527666 | 242880 | 9559.1667 | 4400 | 537225.1667 | 247280 | 573654.8567 | 264048.2646 | 71280 | 32809.5545 | 429264 | 197586.4284 | 21780 | 10025.1417 | 3960 | 1822.753 | 44293.3333 | 20387.8302 | 3520 | 1620.2249 | 87200 | 40137.3899 | 661297.3333 | 304389.3226 | 593074.5979 | 272987 | 296573.1458 | 136510 | 34595.1738 | 15923.853 | 15846.4457 | 7293.979 | 627669.7717 | 288910.853 | 312419.5915 | 143803.979 | 986.0932 | 453.89 | 9900 | 4556.8826 | 10886.0932 | 5010.7726 | 0 | 0 | 3835686.7954 | 1765532.7591 | 886074.4482 | 407852.2436 | 2172537.8788 | 4773207.061 | 6008224.6742 | 5659281.5091
240-1148 | oh | 3 | 3.9112 | 3.9112 | 3.2212 | 3.2212 | 4.2457 | 13248.95 | 4113.0325 | 25382.5 | 7879.7977 | 24310 | 7546.8485 | 63583.9286 | 19739.1312 | 126525.3786 | 39278.8099 | 1001000 | 310752.587 | 1830404.4688 | 568234.6893 | 626170.3067 | 194389.6531 | 2456574.7754 | 762624.3423 | 3457574.7754 | 1073376.9293 | 850000 | 263875.8231 | 4434100.154 | 1376531.5624 | 44680.35 | 13870.6637 | 14726.25 | 4571.6486 | 59406.6 | 18442.3123 | 782368 | 242880 | 14173.3333 | 4400 | 796541.3333 | 247280 | 855947.9333 | 265722.3123 | 92070 | 28582.4083 | 554466 | 172129.6143 | 28132.5 | 8733.5136 | 10395 | 3227.0461 | 116270 | 36095.1082 | 9240 | 2868.4854 | 228900 | 71060.207 | 1039473.5 | 322696.3829 | 879349.0333 | 272987 | 439727.6667 | 136510 | 47104.967 | 14623.367 | 22755.7473 | 7064.343 | 926454.0004 | 287610.367 | 462483.414 | 143574.343 | 1462.076 | 453.89 | 9900 | 3073.3772 | 11362.076 | 3527.2672 | 0 | 0 | 6411389.7303 | 1990365.5795 | 1318431.3473 | 409296.6553 | 3221212.1212 | 8491367.6009 | 9632601.8515 | 9809798.9482
240-2004R | oh | 3 | 18.914 | 18.914 | 15.8669 | 15.8669 | 19.992 | 82754.98 | 5215.5877 | 158543 | 9992.0866 | 129497.5 | 8161.5097 | 397155 | 25030.4785 | 767950.48 | 48399.6626 | 6252400 | 394054.1199 | 11432987.9125 | 720557.8641 | 3911156.0693 | 246498.4906 | 15344143.9818 | 967056.3547 | 21596543.9818 | 1361110.4745 | 5825000 | 367117.4666 | 28189494.4618 | 1776627.6037 | 279080.34 | 17588.8871 | 121344.3 | 7647.6587 | 400424.64 | 25236.5458 | 3853742 | 242880 | 69814.1667 | 4400 | 3923556.1667 | 247280 | 4323980.8067 | 272516.5458 | 884070 | 55718.0324 | 5324066 | 335546.3729 | 270132.5 | 17024.9543 | 60390 | 3806.047 | 675473.3333 | 42571.3406 | 53680 | 3383.1529 | 1329800 | 83809.924 | 8597611.8333 | 541859.8241 | 4331445.4354 | 272987 | 2165984.5208 | 136510 | 231977.9894 | 14620.287 | 112079.8377 | 7063.771 | 4563423.4248 | 287607.287 | 2278064.3585 | 143573.771 | 7201.8073 | 453.89 | 9900 | 623.9421 | 17101.8073 | 1077.8321 | 0 | 0 | 41367631.5273 | 2607172.5469 | 6602045.1652 | 416090.3168 | 15866856.0606 | 39983938.6348 | 57234487.5879 | 46585983.8
240-2006R | oh | 3 | 10.6405 | 10.6405 | 10.6277 | 10.6277 | 14.4949 | 38727.7 | 3644.0506 | 74195 | 6981.3166 | 36932.5 | 3475.1328 | 185860.7143 | 17488.4088 | 335715.9143 | 31588.9088 | 2926000 | 275319.5281 | 5350413.0625 | 503442.6519 | 1830343.9733 | 172224.6887 | 7180757.0358 | 675667.3406 | 10106757.0358 | 950986.8687 | 1475000 | 138788.894 | 11917472.9501 | 1121364.6715 | 130604.1 | 12289.0838 | 42411.6 | 3990.6841 | 173015.7 | 16279.7679 | 2581244 | 242880 | 46761.6667 | 4400 | 2628005.6667 | 247280 | 2801021.3667 | 263559.7679 | 479160 | 45086.1603 | 2885608 | 271518.8766 | 146410 | 13776.3268 | 29205 | 2748.0201 | 326663.3333 | 30737.1137 | 25960 | 2442.6845 | 643100 | 60511.9578 | 4536106.3333 | 426821.1398 | 2901210.7042 | 272987 | 1450780.7083 | 136510 | 155403.9821 | 14622.608 | 75075.0375 | 7064.123 | 3056614.6862 | 287609.608 | 1525855.7458 | 143574.123 | 4823.7847 | 453.89 | 9900 | 931.5322 | 14723.7847 | 1385.4222 | 0 | 0 | 19524917.7544 | 1837180.8416 | 4326877.1125 | 407133.8909 | 10627651.5152 | 28989742.8333 | 30152569.2696 | 33316619.9458
240-2032R | oh | 3 | 25.8642 | 25.8642 | 12.5852 | 12.5852 | 16.4355 | 54218.78 | 4308.1288 | 103873 | 8253.5657 | 64982.5 | 5163.395 | 260205 | 20675.4312 | 483279.28 | 38400.5207 | 4096400 | 325492.7314 | 7490578.2875 | 595188.1619 | 2562481.5627 | 203610.2732 | 10053059.8502 | 798798.435 | 14149459.8502 | 1124291.1664 | 1075000 | 85417.6072 | 15707739.1302 | 1248109.2943 | 182845.74 | 14528.6006 | 96604.2 | 7675.9996 | 279449.94 | 22204.6002 | 3056700 | 242880 | 55375 | 4400 | 3112075 | 247280 | 3391524.94 | 269484.6002 | 508860 | 40433.1196 | 3064468 | 243497.2316 | 155485 | 12354.5643 | 55440 | 4405.1648 | 620106.6667 | 49272.5839 | 49280 | 3915.702 | 1220800 | 97002.6185 | 5674439.6667 | 450880.9848 | 3435603.4375 | 272987 | 1718009.375 | 136510 | 200278.9156 | 15913.81 | 91773.9566 | 7292.197 | 3635882.3531 | 288900.81 | 1809783.3316 | 143802.197 | 5712.3088 | 453.89 | 9900 | 786.6366 | 15612.3088 | 1240.5266 | 0 | 0 | 25033673.4588 | 1989131.6157 | 5201308.2716 | 413286.7972 | 12585227.2727 | 32870939.9498 | 37618900.7315 | 38072248.2213
242-1426F | oh | 2 | 5.2652 | 4.9487 | 2.4206 | 2.5816 | 3.3556 | 13452.78 | 5210.9661 | 25773 | 9983.2323 | 22440 | 8692.1869 | 54780 | 21219.1622 | 116445.78 | 45105.5475 | 1016400 | 393704.9373 | 1858564.5375 | 719919.3572 | 635803.696 | 246280.0612 | 2494368.2335 | 966199.4184 | 3510768.2335 | 1359904.3557 | 925000 | 358300.9317 | 4552214.0135 | 1763310.835 | 45367.74 | 17573.3011 | 34164.9 | 13233.8546 | 79532.64 | 30807.1557 | 627026 | 242880 | 11359.1667 | 4400 | 638385.1667 | 247280 | 717917.8067 | 278087.1557 | 148500 | 57521.8253 | 894300 | 346409.2143 | 45375 | 17576.1133 | 10395 | 4026.5278 | 116270 | 45037.4587 | 9240 | 3579.1358 | 228900 | 88664.9549 | 1452980 | 562815.23 | 660804.3271 | 255964.1147 | 330442.1042 | 127997.5284 | 40731.2364 | 15777.3405 | 18040.9407 | 6988.2009 | 701535.5634 | 271741.4551 | 348483.0448 | 134985.7293 | 1171.7755 | 453.89 | 9900 | 3834.7884 | 11071.7755 | 4288.6784 | 0 | 0 | 6717801.3524 | 2602156.1984 | 1066400.8515 | 413072.885 | 2581628.7879 | 6711240.3176 | 9299430.1403 | 7777641.1691
246-34R | oh | 3 | 25.6091 | 25.6091 | 12.821 | 12.821 | 16.1426 | 63594.96 | 4960.2096 | 121836 | 9502.83 | 120615 | 9407.5958 | 305202.8571 | 23804.8761 | 611248.8171 | 47675.5116 | 4804800 | 374759.4948 | 8785941.45 | 685276.1778 | 3005617.472 | 234428.8389 | 11791558.922 | 919705.0167 | 16596358.922 | 1294464.5115 | 7025000 | 547928.2074 | 24232607.7391 | 1890068.2305 | 214465.68 | 16727.6577 | 130769.1 | 10199.5841 | 345234.78 | 26927.2419 | 3113970 | 242880 | 56412.5 | 4400 | 3170382.5 | 247280 | 3515617.28 | 274207.2419 | 911790 | 71116.7915 | 5491002 | 428281.1221 | 278602.5 | 21730.1307 | 64845 | 5057.7088 | 725303.3333 | 56571.41 | 57640 | 4495.7412 | 1427900 | 111371.7704 | 8957082.8333 | 698624.6748 | 3499972.5312 | 272987 | 1750197.8125 | 136510 | 187437.4418 | 14619.539 | 90562.512 | 7063.595 | 3687409.973 | 287606.539 | 1840760.3245 | 143573.595 | 5819.334 | 453.89 | 9900 | 772.1693 | 15719.334 | 1226.0593 | 0 | 0 | 36892819.8795 | 2877525.5036 | 5356377.6045 | 417780.8369 | 12821022.7273 | 32285128.7923 | 49713842.6068 | 37641506.3968
247-46 | oh | 3 | 28.1953 | 28.1953 | 6.4578 | 6.4578 | 8.3706 | 32816.63 | 5081.7317 | 62870.5 | 9735.6436 | 64515 | 9990.2983 | 157492.5 | 24388.0811 | 317694.63 | 49195.7547 | 2479400 | 383940.8746 | 4533771.0687 | 702065.0275 | 1550975.6827 | 240172.203 | 6084746.7514 | 942237.2305 | 8564146.7514 | 1326178.105 | 3400000 | 526497.9324 | 12281841.3814 | 1901871.7921 | 110669.79 | 17137.4752 | 137837.7 | 21344.4894 | 248507.49 | 38481.9646 | 1568462 | 242880 | 28414.1667 | 4400 | 1596876.1667 | 247280 | 1845383.6567 | 285761.9646 | 330660 | 51203.4724 | 1991308 | 308358.6896 | 101035 | 15645.5055 | 25740 | 3985.8991 | 287906.6667 | 44583.019 | 22880 | 3543.0214 | 566800 | 87770.3024 | 3326329.6667 | 515089.9094 | 1762885.9354 | 272987 | 881549.5208 | 136510 | 94428.8711 | 14622.531 | 45618.9446 | 7064.2 | 1857314.8065 | 287609.531 | 927168.4654 | 143574.2 | 2931.115 | 453.89 | 9900 | 1533.0381 | 12831.115 | 1986.9281 | 0 | 0 | 17478316.9696 | 2706558.1605 | 2772552.1221 | 429336.1646 | 6457765.1515 | 16741257.7838 | 23936082.1212 | 19513809.9059
249-24R | oh | 3 | 16.94 | 16.94 | 12.4773 | 12.4773 | 14.8873 | 59722.19 | 4786.4779 | 114416.5 | 9169.9927 | 109862.5 | 8805.0091 | 286616.7857 | 22971.1085 | 570617.9757 | 45732.5882 | 4512200 | 361633.5155 | 8250900.1437 | 661274.3285 | 2822583.0747 | 226217.9513 | 11073483.2184 | 887492.2798 | 15585683.2184 | 1249125.7953 | 4775000 | 382695.8106 | 20931301.1941 | 1677554.1941 | 201405.27 | 16141.7703 | 107207.1 | 8592.1902 | 308612.37 | 24733.9604 | 3030480 | 242880 | 54900 | 4400 | 3085380 | 247280 | 3393992.37 | 272013.9604 | 524700 | 42052.459 | 3159860 | 253249.2532 | 160325 | 12849.3625 | 61380 | 4919.3443 | 686546.6667 | 55023.7766 | 54560 | 4372.7505 | 1351600 | 108324.9545 | 5998971.6667 | 480791.9004 | 3406133.25 | 272987 | 1703272.5 | 136510 | 189680.1862 | 15202.055 | 89419.3357 | 7166.577 | 3595813.4362 | 288189.055 | 1792691.8357 | 143676.577 | 5663.3093 | 453.89 | 9900 | 793.4426 | 15563.3093 | 1247.3326 | 0 | 0 | 30541649.6064 | 2447782.4821 | 5186684.2057 | 415690.5374 | 12477272.7273 | 29774542.8664 | 43018922.3336 | 34961227.0721
252-129 | oh | 2 | 5.6705 | 4.8229 | 4.2652 | 4.6669 | 6.1435 | 19363.85 | 4149.228 | 37097.5 | 7949.1417 | 43010 | 9216.0545 | 85104.6429 | 18235.9691 | 184575.9929 | 39550.3933 | 1463000 | 313487.2773 | 2675206.5312 | 573235.278 | 915171.9867 | 196100.3242 | 3590378.5179 | 769335.6022 | 5053378.5179 | 1082822.8795 | 1850000 | 396412.4833 | 7087954.5108 | 1518785.7561 | 65302.05 | 13992.7285 | 17082.45 | 3660.3764 | 82384.5 | 17653.105 | 1133486 | 242880 | 20534.1667 | 4400 | 1154020.1667 | 247280 | 1236404.6667 | 264933.105 | 15840 | 3394.148 | 95392 | 20440.3133 | 4840 | 1037.1008 | 1980 | 424.2685 | 22146.6667 | 4745.5217 | 1760 | 377.1276 | 43600 | 9342.478 | 185558.6667 | 39760.9578 | 1164330.9167 | 249489.3568 | 582235.8333 | 124759.7581 | 59909.2522 | 12837.1759 | 29696.9363 | 6363.371 | 1224240.1689 | 262326.5327 | 611932.7697 | 131123.1291 | 2118.2393 | 453.89 | 9900 | 2121.3425 | 12018.2393 | 2575.2325 | 0 | 0 | 8509771.5857 | 1823448.479 | 1848337.4363 | 396056.2341 | 4666856.0606 | 12286944.3316 | 13176627.6463 | 14135281.768
283-55R | oh | 3 | 8.8134 | 8.8134 | 7.2309 | 7.2309 | 10.2801 | 19771.51 | 2734.3192 | 37878.5 | 5238.4421 | 30387.5 | 4202.4673 | 94886.7857 | 13122.4555 | 182924.2957 | 25297.6841 | 1493800 | 206586.448 | 2731526.6688 | 377758.9987 | 934438.7653 | 129229.0705 | 3665965.4341 | 506988.0691 | 5159765.4341 | 713574.5172 | 1625000 | 224730.873 | 6967689.7298 | 963603.0743 | 66676.83 | 9221.1337 | 27096.3 | 3747.3078 | 93773.13 | 12968.4415 | 1756234 | 242880 | 31815.8333 | 4400 | 1788049.8333 | 247280 | 1881822.9633 | 260248.4415 | 80190 | 11089.95 | 482922 | 66786.1432 | 24502.5 | 3388.5958 | 26730 | 3696.65 | 298980 | 41347.7147 | 23760 | 3285.9111 | 588600 | 81400.9796 | 1525684.5 | 210995.9444 | 1973933.8396 | 272987 | 987086.2292 | 136510 | 139051.0996 | 19230.2 | 56939.7629 | 7874.537 | 2112984.9392 | 292217.2 | 1044025.9921 | 144384.537 | 3282.0201 | 453.89 | 9900 | 1369.1296 | 13182.0201 | 1823.0196 | 0 | 0 | 10619541.1891 | 1468639.2383 | 2925848.9554 | 404632.9785 | 7230871.2121 | 20560275.1849 | 17850412.4012 | 23486124.1403
283-71F | oh | 3 | 12.9267 | 12.9267 | 5.1858 | 5.1858 | 6.8845 | 23032.79 | 4441.5153 | 44126.5 | 8509.1092 | 41607.5 | 8023.3593 | 110538.2143 | 21315.5755 | 219305.0043 | 42289.5593 | 1740200 | 335570.5051 | 3182087.7687 | 613616.136 | 1088572.9947 | 209914.3717 | 4270660.7634 | 823530.5077 | 6010860.7634 | 1159101.0128 | 2125000 | 409773.2004 | 8355165.7677 | 1611163.7725 | 77675.07 | 14978.4292 | 68918.85 | 13289.9283 | 146593.92 | 28268.3575 | 1259526 | 242880 | 22817.5 | 4400 | 1282343.5 | 247280 | 1428937.42 | 275548.3575 | 243540 | 46962.9013 | 1466652 | 282821.0277 | 74415 | 14349.7754 | 25245 | 4868.1056 | 282370 | 54450.6629 | 22440 | 4327.205 | 555900 | 107196.6692 | 2670562 | 514976.3471 | 1415654.7437 | 272987 | 707912.9375 | 136510 | 99436.041 | 19174.694 | 40784.1136 | 7864.582 | 1515090.7847 | 292161.694 | 748697.0511 | 144374.582 | 2353.7807 | 453.89 | 9900 | 1909.061 | 12253.7807 | 2362.951 | 0 | 0 | 12553072.3331 | 2420664.7646 | 2177634.4711 | 419922.9395 | 5185795.4545 | 13768929.8627 | 17738867.7877 | 15946564.3338
288-2380F | oh | 2 | 7.4085 | 7.3737 | 1.753 | 1.753 | 2.3267 | 7134.05 | 4069.5532 | 13667.5 | 7796.4996 | 13090 | 7467.07 | 34237.5 | 19530.4667 | 68129.05 | 38863.5895 | 539000 | 307467.5886 | 985602.4062 | 562227.8203 | 337168.6267 | 192334.7395 | 1322771.0329 | 754562.5598 | 1861771.0329 | 1062030.1484 | 525000 | 299481.4175 | 2454900.0829 | 1400375.1553 | 24058.65 | 13724.0354 | 34753.95 | 19825.0709 | 58812.6 | 33549.1063 | 425776 | 242880 | 7713.3333 | 4400 | 433489.3333 | 247280 | 492301.9333 | 280829.1063 | 323730 | 184668.7986 | 1949574 | 1112116.5428 | 98917.5 | 56426.5774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2372221.5 | 1353211.9188 | 478554.4833 | 272987 | 239306.1667 | 136510 | 25636.5939 | 14624.159 | 12384.3544 | 7064.541 | 504191.0772 | 287611.159 | 251690.5211 | 143574.541 | 795.6829 | 453.89 | 9900 | 5647.3639 | 10695.6829 | 6101.2539 | 0 | 0 | 5342008.3431 | 3047299.487 | 743992.4544 | 424403.6473 | 1753030.303 | 4653397.7918 | 7095038.6461 | 5397390.2463
296-68F | oh | 2 | 10.1415 | 7.6667 | 1.0165 | 1.0314 | 1.3047 | 6318.73 | 6126.1282 | 12105.5 | 11736.5112 | 9817.5 | 9518.2519 | 28368.2143 | 27503.5203 | 56609.9443 | 54884.4116 | 477400 | 462848.329 | 872962.1312 | 846353.2965 | 298635.0693 | 289532.3478 | 1171597.2006 | 1135885.6443 | 1648997.2006 | 1598733.9734 | 650000 | 630187.2934 | 2355607.1449 | 2283805.6785 | 21309.09 | 20659.5658 | 52425.45 | 50827.4653 | 73734.54 | 71487.0311 | 250516 | 242880 | 4538.3333 | 4400 | 255054.3333 | 247280 | 328788.8733 | 318767.0311 | 42570 | 41272.4201 | 256366 | 248551.6856 | 13007.5 | 12611.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 311943.5 | 302435.123 | 277485.0812 | 269027.0343 | 138759.3125 | 134529.7778 |  |  |  |  | 277485.0812 | 269027.0343 | 138759.3125 | 134529.7778 | 468.16 | 453.89 | 9900 | 9598.2372 | 10368.16 | 10052.1272 | 0 | 0 | 2955403.8861 | 2865319.9631 | 467548.1858 | 453296.8089 | 1031439.3939 | 2609339.9404 | 3986843.2801 | 3076888.1263
300-483F | oh | 2 | 5.4989 | 5.4989 | 5.4324 | 5.4324 | 7.6923 | 14064.27 | 2588.9672 | 26944.5 | 4959.9749 | 1402.5 | 258.1738 | 67496.7857 | 12424.8868 | 109908.0557 | 20232.0027 | 1062600 | 195604.6439 | 1943044.7437 | 357677.9363 | 664703.864 | 122359.4604 | 2607748.6077 | 480037.3967 | 3670348.6077 | 675642.0405 | 50000 | 9204.0582 | 3830256.6635 | 705078.1014 | 47429.91 | 8730.953 | 589.05 | 108.433 | 48018.96 | 8839.386 | 1319418 | 242880 | 23902.5 | 4400 | 1343320.5 | 247280 | 1391339.46 | 256119.386 | 32670 | 6013.9316 | 196746 | 36217.2325 | 9982.5 | 1837.5902 | 3465 | 637.8412 | 38756.6667 | 7134.3723 | 3080 | 566.97 | 76300 | 14045.3927 | 361000.1667 | 66453.3305 | 1482970.8562 | 272987 | 741575.0625 | 136510 |  |  |  |  | 1482970.8562 | 272987 | 741575.0625 | 136510 | 2465.7058 | 453.89 | 9900 | 1822.4035 | 12365.7058 | 2276.2935 | 0 | 0 | 5686593.3922 | 1046794.7255 | 2132914.5225 | 392629.386 | 5432386.3636 | 15384670.3451 | 11118979.7559 | 17517584.8676
300-484F | oh | 2 | 16.0884 | 16.0884 | 10.4775 | 10.4775 | 14.8091 | 39746.85 | 3793.557 | 76147.5 | 7267.7428 | 71527.5 | 6826.7963 | 190751.7857 | 18205.9151 | 378173.6357 | 36094.0113 | 3003000 | 286615.2094 | 5491213.4062 | 524097.6625 | 1878510.92 | 179290.6429 | 7369724.3262 | 703388.3054 | 10372724.3262 | 990003.5148 | 4100000 | 391316.1367 | 14850897.962 | 1417413.6628 | 134041.05 | 12793.2746 | 36521.1 | 3485.6819 | 170562.15 | 16278.9565 | 2544766 | 242880 | 46100.8333 | 4400 | 2590866.8333 | 247280 | 2761428.9833 | 263558.9565 | 152460 | 14551.2337 | 918148 | 87630.763 | 46585 | 4446.2103 | 3465 | 330.7099 | 38756.6667 | 3699.051 | 3080 | 293.9643 | 76300 | 7282.2979 | 1238794.6667 | 118234.23 | 2860210.9521 | 272987 | 1430278.3542 | 136510 | 147069.1497 | 14036.715 | 72932.9014 | 6960.932 | 3007280.1018 | 287023.715 | 1503211.2555 | 143470.932 | 4755.6153 | 453.89 | 9900 | 944.8853 | 14655.6153 | 1398.7753 | 0 | 0 | 19111628.3457 | 1824070.3831 | 4264640.2389 | 407029.8885 | 10477462.1212 | 29618100.5284 | 29589090.4669 | 33882740.7672
307-1538F | oh | 2 | 19.7352 | 12.2021 | 2.2172 | 2.2172 | 2.9476 | 9987.67 | 4504.5612 | 19134.5 | 8629.8932 | 19635 | 8855.6248 | 47932.5 | 21618.143 | 96689.67 | 43608.2222 | 754600 | 340333.8174 | 1379843.3687 | 622326.214 | 472036.0773 | 212894.0368 | 1851879.4461 | 835220.2507 | 2606479.4461 | 1175554.0681 | 725000 | 326983.8558 | 3428169.1161 | 1546146.1461 | 33682.11 | 15191.043 | 113097.6 | 51008.3991 | 146779.71 | 66199.4421 | 538522 | 242880 | 9755.8333 | 4400 | 548277.8333 | 247280 | 695057.5433 | 313479.4421 | 511830 | 230841.582 | 3082354 | 1390179.3047 | 156392.5 | 70534.9278 | 5940 | 2679.0126 | 66440 | 29965.2516 | 5280 | 2381.3445 | 130800 | 58992.3977 | 3959036.5 | 1785573.8208 | 605276.2896 | 272987 | 302674.7292 | 136510 | 37090.9466 | 16728.47 | 16485.7242 | 7435.263 | 642367.2362 | 289715.47 | 319160.4534 | 143945.263 | 1006.3807 | 453.89 | 9900 | 4465.0209 | 10906.3807 | 4918.9109 | 0 | 0 | 8040479.233 | 3626354.3479 | 1014217.9967 | 457424.7051 | 2217234.8485 | 5895126.5618 | 10257714.0815 | 6909344.5586
307-234R | oh | 2 | 22.6583 | 19.0241 | 4.125 | 4.6394 | 6.2517 | 21605.98 | 4657.0695 | 41393 | 8922.0705 | 34127.5 | 7356.0255 | 85104.6429 | 18343.9139 | 182231.1229 | 39279.0794 | 1632400 | 351856.3031 | 2984967.2875 | 643395.9535 | 1021139.2693 | 220101.8673 | 4006106.5568 | 863497.8209 | 5638506.5568 | 1215354.1239 | 900000 | 193990.8556 | 6720737.6797 | 1448624.059 | 72863.34 | 15705.3574 | 118988.1 | 25647.337 | 191851.44 | 41352.6944 | 1126816 | 242880 | 20413.3333 | 4400 | 1147229.3333 | 247280 | 1339080.7733 | 288632.6944 | 1066230 | 229820.9667 | 6421074 | 1384032.9327 | 325792.5 | 70223.0732 | 25740 | 5548.1385 | 287906.6667 | 62056.9562 | 22880 | 4931.6786 | 566800 | 122171.13 | 8716423.1667 | 1878784.8759 | 1126071.375 | 242719.4995 | 563103.75 | 121374.4203 | 69039.8775 | 14881.2277 | 30673.9537 | 6611.6295 | 1195111.2525 | 257600.7272 | 593777.7037 | 127986.0498 | 2105.7745 | 453.89 | 9900 | 2133.8994 | 12005.7745 | 2587.7894 | 0 | 0 | 16644277.8734 | 3587597.4515 | 1932858.4771 | 416618.7442 | 4639393.9394 | 12503471.9168 | 21283671.8128 | 14436330.3939
311-43 | oh | 2 | 8.3212 | 3.5424 | 1.8943 | 2.0208 | 2.1442 | 17733.21 | 8775.1967 | 33973.5 | 16811.6289 | 39737.5 | 19663.9175 | 78257.1429 | 38725.1841 | 169701.3529 | 83975.9272 | 1339800 | 662993.8144 | 2449925.9813 | 1212334.5062 | 838104.872 | 414732.3078 | 3288030.8533 | 1627066.814 | 4627830.8532 | 2290060.6284 | 1575000 | 779381.4433 | 6372532.2061 | 3153417.9989 | 59802.93 | 29593.2025 | 58315.95 | 28857.3773 | 118118.88 | 58450.5798 | 490820 | 242880 | 8891.6667 | 4400 | 499711.6667 | 247280 | 617830.5467 | 305730.5798 | 150480 | 74464.3299 | 906224 | 448440.7423 | 45980 | 22752.9897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1102684 | 545658.0619 | 517124.2375 | 255896.5299 | 258593.375 | 127963.732 | 27244.2811 | 13481.7061 | 13301.7431 | 6582.3059 | 544368.5186 | 269378.236 | 271895.1181 | 134546.0378 | 917.236 | 453.89 | 9900 | 4898.9691 | 10817.236 | 5352.8591 | 0 | 0 | 8030401.9607 | 3973807.1558 | 889725.6648 | 440276.6176 | 2020833.3333 | 4288311.404 | 10051235.2941 | 5178037.0689
315-485AE | oh | 2 | 10.8049 | 10.5871 | 1.5218 | 1.5218 | 1.9911 | 6930.22 | 4554.0214 | 13277 | 8724.6497 | 10752.5 | 7065.7374 | 33259.2857 | 21855.5107 | 64219.0057 | 42199.9191 | 523600 | 344070.6907 | 957442.3375 | 629159.3705 | 327535.2373 | 215231.6183 | 1284977.5748 | 844390.9888 | 1808577.5748 | 1188461.6795 | 500000 | 328562.5389 | 2372796.5805 | 1559224.1376 | 23371.26 | 15357.841 | 59494.05 | 39095.0322 | 82865.31 | 54452.8733 | 369610 | 242880 | 6695.8333 | 4400 | 376305.8333 | 247280 | 459171.1433 | 301732.8733 | 312840 | 205575.0093 | 1883992 | 1238018.3895 | 95590 | 62814.5862 | 990 | 650.5538 | 11073.3333 | 7276.565 | 880 | 578.2701 | 21800 | 14325.3267 | 2327165.3333 | 1529238.7007 | 415426.2396 | 272987 | 207738.2292 | 136510 |  |  |  |  | 415426.2396 | 272987 | 207738.2292 | 136510 | 690.7209 | 453.89 | 9900 | 6505.5383 | 10590.7209 | 6959.4283 | 0 | 0 | 5125978.8743 | 3368409.2665 | 666909.3725 | 438242.8733 | 1521780.303 | 3982111.7848 | 6647759.1774 | 4649021.1573
350-2188R | oh | 2 | 27.1629 | 27.1629 | 22.0426 | 22.0426 | 28.9498 | 97226.91 | 4410.8612 | 186268.5 | 8450.3818 | 178585 | 8101.8069 | 466608.2143 | 21168.4613 | 928688.6243 | 42131.5112 | 7345800 | 333254.4916 | 13432352.7937 | 609381.1294 | 4595126.712 | 208465.6016 | 18027479.5058 | 817846.731 | 25373279.5058 | 1151101.2226 | 9000000 | 408300.0387 | 35301968.13 | 1601532.7725 | 327885.03 | 14875.0523 | 128412.9 | 5825.6658 | 456297.93 | 20700.7181 | 5353710 | 242880 | 96987.5 | 4400 | 5450697.5 | 247280 | 5906995.43 | 267980.7181 | 1779030 | 80708.6686 | 10713714 | 486045.5378 | 543592.5 | 24660.9821 | 99990 | 4536.2134 | 1118406.6667 | 50738.3872 | 88880 | 4032.1897 | 2201800 | 99888.3361 | 16545413.1667 | 750610.3151 | 6017346.9687 | 272987 | 3009037.1875 | 136510 | 351762.7514 | 15958.305 | 160902.02 | 7299.589 | 6369109.7202 | 288945.305 | 3169939.2075 | 143809.589 | 10004.9219 | 453.89 | 9900 | 449.13 | 19904.9219 | 903.02 | 0 | 0 | 58236395.9388 | 2641991.4126 | 9076934.6375 | 411790.3071 | 22042613.6364 | 57899562.5546 | 80279009.5751 | 66976497.1922
350-2192R | oh | 2 | 40.7845 | 40.7845 | 31.8587 | 31.8587 | 40.3011 | 144719.3 | 4542.5345 | 277255 | 8702.6431 | 247775 | 7777.3075 | 694532.1429 | 21800.3835 | 1364281.4429 | 42822.8686 | 10934000 | 343202.825 | 19993648.8125 | 627572.4121 | 6839706.4267 | 214688.7294 | 26833355.2392 | 842261.1415 | 37767355.2392 | 1185463.9665 | 12225000 | 383725.4925 | 51356636.682 | 1612012.3276 | 488046.9 | 15319.1032 | 200277 | 6286.4123 | 688323.9 | 21605.5155 | 7737844 | 242880 | 140178.3333 | 4400 | 7878022.3333 | 247280 | 8566346.2333 | 268885.5155 | 2193840 | 68861.5407 | 13211792 | 414699.5004 | 670340 | 21041.0263 | 156420 | 4909.803 | 1749586.6667 | 54917.0557 | 139040 | 4364.2693 | 3444400 | 108114.8537 | 21565418.6667 | 676908.049 | 8697014.2458 | 272987 | 4349032.7917 | 136510 | 508035.7174 | 15946.524 | 232484.7145 | 7297.367 | 9205049.9633 | 288933.524 | 4581517.5062 | 143807.367 | 14460.3508 | 453.89 | 9900 | 310.747 | 24360.3508 | 764.637 | 0 | 0 | 82151465.6628 | 2578618.5377 | 13147863.7395 | 412692.8825 | 31858712.1212 | 80602206.3148 | 114010177.784 | 93750070.0543
350-2196R | oh | 2 | 36.5333 | 36.5333 | 34.4453 | 34.4453 | 45.1126 | 145330.79 | 4219.1805 | 278426.5 | 8083.1574 | 118277.5 | 3433.7811 | 697466.7857 | 20248.5533 | 1239501.5757 | 35984.6722 | 10980200 | 318772.4046 | 20078129.0188 | 582899.5344 | 6868606.5947 | 199406.4079 | 26946735.6134 | 782305.9423 | 37926935.6134 | 1101078.347 | 5825000 | 169108.8739 | 44991437.1891 | 1306171.893 | 490109.07 | 14228.634 | 156098.25 | 4531.7767 | 646207.32 | 18760.4107 | 8366066 | 242880 | 151559.1667 | 4400 | 8517625.1667 | 247280 | 9163832.4867 | 266040.4107 | 2806650 | 81481.4456 | 16902270 | 490699.3726 | 857587.5 | 24897.1084 | 144540 | 4196.2226 | 1616706.6667 | 46935.5268 | 128480 | 3729.9756 | 3182800 | 92401.6693 | 25639034.1667 | 744341.321 | 9403109.5979 | 272987 | 4702123.1458 | 136510 | 549473.9698 | 15952.09 | 251398.7677 | 7298.5 | 9952583.5677 | 288939.09 | 4953521.9135 | 143808.5 | 15634.3614 | 453.89 | 9900 | 287.4125 | 25534.3614 | 741.3025 | 0 | 0 | 80608589.2849 | 2340193.6066 | 14117354.4002 | 409848.9107 | 34445265.1515 | 90225100.8119 | 115053854.4364 | 104342455.2121
350-2201R | oh | 3 | 17.4256 | 17.4256 | 14.5687 | 14.5687 | 19.8231 | 60741.34 | 4169.2897 | 116369 | 7987.5761 | 64515 | 4428.314 | 291507.8571 | 20009.1193 | 533133.1971 | 36594.2992 | 4589200 | 315003.003 | 8391700.4875 | 576006.8975 | 2870750.0213 | 197048.4785 | 11262450.5088 | 773055.376 | 15851650.5088 | 1088058.379 | 3150000 | 216216.2162 | 19534783.706 | 1340868.8944 | 204842.22 | 14060.384 | 69507.9 | 4771.027 | 274350.12 | 18831.4111 | 3538458 | 242880 | 64102.5 | 4400 | 3602560.5 | 247280 | 3876910.62 | 266111.4111 | 1085040 | 74477.2201 | 6534352 | 448518.3698 | 331540 | 22756.9284 | 67815 | 4654.8263 | 758523.3333 | 52065.0937 | 60280 | 4137.6233 | 1493300 | 102500.2145 | 10330850.3333 | 709110.276 | 3977079.3562 | 272987 | 1988780.0625 | 136510 | 232415.7932 | 15953.036 | 106331.7847 | 7298.621 | 4209495.1495 | 288940.036 | 2095111.8472 | 143808.621 | 6612.6099 | 453.89 | 9900 | 679.5367 | 16512.6099 | 1133.4267 | 0 | 0 | 34091641.7987 | 2340052.6331 | 5972022.4672 | 409920.0321 | 14568750 | 39646233.7488 | 48660391.7987 | 45618256.216
350-41R | oh | 2 | 19.0729 | 19.0729 | 16.303 | 16.303 | 20.9241 | 76436.25 | 4688.4689 | 146437.5 | 8982.2258 | 144925 | 8889.4517 | 366830.3571 | 22500.7468 | 734629.1071 | 45060.8932 | 5775000 | 354228.6245 | 10560025.7812 | 647733.9234 | 3612521 | 221585.8606 | 14172546.7812 | 869319.784 | 19947546.7812 | 1223548.4085 | 7750000 | 475371.7472 | 28432175.8884 | 1743981.0489 | 257771.25 | 15811.2477 | 92480.85 | 5672.6172 | 350252.1 | 21483.8649 | 3959680 | 242880 | 71733.3333 | 4400 | 4031413.3333 | 247280 | 4381665.4333 | 268763.8649 | 1619640 | 99345.948 | 9753832 | 598283.3755 | 494890 | 30355.7063 | 77220 | 4736.5428 | 863720 | 52979.1078 | 68640 | 4210.2602 | 1700400 | 104299.6283 | 14578342 | 894210.5688 | 4450515.3333 | 272987 | 2225526.6667 | 136510 | 259998.9013 | 15947.888 | 118975.8307 | 7297.774 | 4710514.2347 | 288934.888 | 2344502.4973 | 143807.774 | 7399.7824 | 453.89 | 9900 | 607.2491 | 17299.7824 | 1061.1391 | 0 | 0 | 47738331.9055 | 2928187.6448 | 6726167.9307 | 412571.6389 | 16303030.303 | 41848180.4809 | 64041362.2085 | 48574348.4115
351-819R | oh | 2 | 12.289 | 12.289 | 10.4894 | 10.4894 | 13.3773 | 46065.58 | 4391.6341 | 88253 | 8413.5462 | 78072.5 | 7442.9944 | 221076.4286 | 21076.187 | 433467.5086 | 41324.3616 | 3480400 | 331801.82 | 6364175.5375 | 606724.8093 | 2177145.9893 | 207556.8905 | 8541321.5268 | 814281.6998 | 12021721.5268 | 1146083.5198 | 3350000 | 319370.2152 | 15805189.0354 | 1506778.0967 | 155350.14 | 14810.2112 | 72453.15 | 6907.277 | 227803.29 | 21717.4883 | 2547664 | 242880 | 46153.3333 | 4400 | 2593817.3333 | 247280 | 2821620.6233 | 268997.4883 | 957330 | 91266.4741 | 5765254 | 549626.9883 | 292517.5 | 27886.9782 | 39600 | 3775.2419 | 442933.3333 | 42226.7803 | 35200 | 3355.7706 | 872000 | 83131.5904 | 8404834.8333 | 801269.8238 | 2863468.1833 | 272987 | 1431907.1667 | 136510 | 177082.0324 | 16882.008 | 78270.0534 | 7461.828 | 3040550.2157 | 289869.008 | 1510177.2201 | 143971.828 | 4761.031 | 453.89 | 9900 | 943.8105 | 14661.031 | 1397.7005 | 0 | 0 | 27265235.1155 | 2599314.629 | 4331797.8434 | 412969.3163 | 10489393.9394 | 26754504.0212 | 37754629.0549 | 31086301.8646
351-871R | oh | 3 | 4.1699 | 4.1699 | 4.1407 | 4.1407 | 5.4069 | 17121.72 | 4134.9623 | 32802 | 7921.8113 | 28985 | 6999.9909 | 82170 | 19844.3763 | 161078.72 | 38901.1408 | 1293600 | 312409.4589 | 2365445.775 | 571264.4053 | 809204.704 | 195426.1006 | 3174650.479 | 766690.5058 | 4468250.479 | 1079099.9647 | 1450000 | 350180.6705 | 6079329.199 | 1468181.7761 | 57740.76 | 13944.6193 | 20616.75 | 4979.0258 | 78357.51 | 18923.6451 | 1005698 | 242880 | 18219.1667 | 4400 | 1023917.1667 | 247280 | 1102274.6767 | 266203.6451 | 195030 | 47100.5077 | 1174514 | 283649.7242 | 59592.5 | 14391.8218 | 12870 | 3108.1553 | 143953.3333 | 34765.293 | 11440 | 2762.8047 | 283400 | 68442.2083 | 1880799.8333 | 454220.515 | 1130362.6479 | 272987 | 565249.6458 | 136510 | 69973.7157 | 16898.926 | 30910.046 | 7464.897 | 1200336.3637 | 289885.926 | 596159.6919 | 143974.897 | 1879.4313 | 453.89 | 9900 | 2390.8887 | 11779.4313 | 2844.7787 | 0 | 0 | 9172244.8273 | 2215132.9958 | 1698434.3685 | 410178.5421 | 4140719.697 | 10813744.7008 | 13312964.5242 | 12512179.0693
352-27R | oh | 3 | 15.0155 | 15.0155 | 13.0331 | 13.0331 | 17.0369 | 57683.89 | 4425.9382 | 110511.5 | 8479.2664 | 92097.5 | 7066.407 | 276834.6429 | 21240.8183 | 537127.5329 | 41212.43 | 4358200 | 334393.606 | 7969299.4562 | 611464.0867 | 2726249.1813 | 209178.1687 | 10695548.6376 | 820642.2554 | 15053748.6376 | 1155035.8615 | 4675000 | 358700.8646 | 20265876.1704 | 1554949.1561 | 194531.37 | 14925.8975 | 81877.95 | 6282.2869 | 276409.32 | 21208.1844 | 3165490 | 242880 | 57345.8333 | 4400 | 3222835.8333 | 247280 | 3499245.1533 | 268488.1844 | 1515690 | 116295.0403 | 9127822 | 700354.5762 | 463127.5 | 35534.5957 | 55935 | 4291.7503 | 625643.3333 | 48004.0224 | 49720 | 3814.8892 | 1231700 | 94505.2096 | 13069637.8333 | 1002800.0837 | 3557878.8646 | 272987 | 1779154.4792 | 136510 | 207832.1957 | 15946.436 | 95109.3549 | 7297.499 | 3765711.0603 | 288933.436 | 1874263.834 | 143807.499 | 5915.6137 | 453.89 | 9900 | 759.6018 | 15815.6137 | 1213.4918 | 0 | 0 | 37117040.6778 | 2847896.1677 | 5373508.9874 | 412295.6834 | 13033143.9394 | 34073742.166 | 50150184.6172 | 39447251.1534
353-1429R | oh | 2 | 21.6004 | 21.6004 | 5.9517 | 5.9517 | 7.333 | 33020.46 | 5548.0677 | 63261 | 10629.0558 | 60307.5 | 10132.8115 | 158470.7143 | 26626.1057 | 315059.6743 | 52936.0407 | 2494800 | 419174.0334 | 4561931.1375 | 766491.5324 | 1560609.072 | 262212.1209 | 6122540.2095 | 1028703.6533 | 8617340.2095 | 1447877.6868 | 3175000 | 533460.6205 | 12107399.8838 | 2034274.348 | 111357.18 | 18710.1324 | 114864.75 | 19299.4711 | 226221.93 | 38009.6035 | 1445550 | 242880 | 26187.5 | 4400 | 1471737.5 | 247280 | 1697959.43 | 285289.6035 | 1007820 | 169333.0024 | 6069316 | 1019760.9699 | 307945 | 51740.6396 | 32670 | 5489.1838 | 365420 | 61397.537 | 29040 | 4879.2745 | 719400 | 120872.9356 | 8531611 | 1433473.5427 | 1624737.9687 | 272987 | 812467.1875 | 136510 | 100454.7917 | 16878.323 | 44407.0603 | 7461.234 | 1725192.7605 | 289865.323 | 856874.2478 | 143971.234 | 2701.4192 | 453.89 | 9900 | 1663.389 | 12601.4192 | 2117.279 | 0 | 0 | 22376805.0634 | 3759730.4928 | 2554833.6778 | 429260.8375 | 5951704.5455 | 14666096.4518 | 28328509.6089 | 17220930.1296
353-593F | oh | 2 | 2.6587 | 2.6587 | 2.0775 | 2.0775 | 2.5344 | 9376.18 | 4513.2857 | 17963 | 8646.6077 | 14025 | 6751.0256 | 44997.8571 | 21660.0133 | 86362.0371 | 41570.9323 | 708400 | 340992.9802 | 1295363.1625 | 623531.5433 | 443135.9093 | 213306.3726 | 1738499.0718 | 836837.9159 | 2446899.0718 | 1177830.8961 | 750000 | 361017.4127 | 3283261.109 | 1580419.2411 | 31619.94 | 15220.4652 | 13548.15 | 6521.4907 | 45168.09 | 21741.956 | 504574 | 242880 | 9140.8333 | 4400 | 513714.8333 | 247280 | 558882.9233 | 269021.956 | 336600 | 162024.6148 | 2027080 | 975748.2359 | 102850 | 49507.5212 | 6930 | 3335.8009 | 77513.3333 | 37311.5507 | 6160 | 2965.1563 | 152600 | 73455.0096 | 2709733.3333 | 1304347.8895 | 567120.1521 | 272987 | 283594.3542 | 136510 | 35113.3001 | 16902.017 | 15508.6121 | 7465.172 | 602233.4522 | 289889.017 | 299102.9662 | 143975.172 | 942.9393 | 453.89 | 9900 | 4765.4298 | 10842.9393 | 5219.3198 | 0 | 0 | 6606070.8338 | 3179875.4674 | 857985.8896 | 412997.128 | 2077462.1212 | 5068853.8537 | 8683532.955 | 5926839.7432
353-594F | oh | 2 | 1.2869 | 1.2869 | 1.221 | 1.221 | 1.4574 | 5095.75 | 4173.3457 | 9762.5 | 7995.3467 | 9817.5 | 8040.3909 | 24455.3571 | 20028.5847 | 49131.1071 | 40237.668 | 385000 | 315309.4463 | 704001.7188 | 576567.2522 | 240834.7333 | 197240.1725 | 944836.4521 | 773807.4247 | 1329836.4521 | 1089116.8709 | 425000 | 348068.8692 | 1803967.5592 | 1477423.4082 | 17184.75 | 14074.0624 | 1178.1 | 964.8469 | 18362.85 | 15038.9093 | 296562 | 242880 | 5372.5 | 4400 | 301934.5 | 247280 | 320297.35 | 262318.9093 | 97020 | 79457.9805 | 584276 | 478513.6156 | 29645 | 24278.8274 | 990 | 810.7957 | 11073.3333 | 9068.9003 | 880 | 720.7073 | 21800 | 17853.8855 | 745684.3333 | 610704.7123 | 333323.3312 | 272987 | 166681.8125 | 136510 | 20639.6004 | 16903.535 | 9115.2253 | 7465.238 | 353962.9317 | 289890.535 | 175797.0378 | 143975.238 | 554.21 | 453.89 | 9900 | 8107.9572 | 10454.21 | 8561.8472 | 0 | 0 | 2914069.0342 | 2386580.5027 | 496094.3878 | 406294.1473 | 1221022.7273 | 2914799.5285 | 4135091.7615 | 3410893.9163
353-900F | oh | 2 | 8.7237 | 8.7237 | 1.0098 | 1.0098 | 1.2243 | 5095.75 | 5046.054 | 9762.5 | 9667.2918 | 11220 | 11110.5776 | 24455.3571 | 24216.8578 | 50533.6071 | 50040.7813 | 385000 | 381245.3113 | 704001.7188 | 697135.9856 | 240834.7333 | 238486.0075 | 944836.4521 | 935621.9931 | 1329836.4521 | 1316867.3044 | 525000 | 519879.97 | 1905370.0592 | 1886788.0556 | 17184.75 | 17017.1568 | 44767.8 | 44331.2048 | 61952.55 | 61348.3616 | 245272 | 242880 | 4443.3333 | 4400 | 249715.3333 | 247280 | 311667.8833 | 308628.3616 | 156420 | 154894.5236 | 941996 | 932809.2423 | 47795 | 47328.8822 | 6435 | 6372.2431 | 71976.6667 | 71274.7187 | 5720 | 5664.2161 | 141700 | 140318.0795 | 1372042.6667 | 1358661.9055 | 275675.5083 | 272987 | 137854.4167 | 136510 | 17044.5711 | 16878.345 | 7534.7047 | 7461.223 | 292720.0795 | 289865.345 | 145389.1214 | 143971.223 | 458.3601 | 453.89 | 9900 | 9803.4509 | 10358.3601 | 10257.3409 | 0 | 0 | 3580491.1655 | 3545572.647 | 457057.0047 | 452599.5846 | 1009848.4848 | 2448683.7214 | 4590339.6503 | 2905740.7261
353-901F | oh | 2 | 16.0333 | 16.0333 | 2.3892 | 2.3892 | 3.3902 | 14268.1 | 5971.9039 | 27335 | 11441.0464 | 23375 | 9783.591 | 68475 | 28660.1665 | 133453.1 | 55856.7077 | 1078000 | 451196.195 | 1971204.8125 | 825046.4851 | 674337.2533 | 282243.4164 | 2645542.0658 | 1107289.9015 | 3723542.0658 | 1558486.0965 | 1175000 | 491795.4816 | 5031995.1658 | 2106138.2858 | 48117.3 | 20139.4644 | 70096.95 | 29339.0326 | 118214.25 | 49478.497 | 580290 | 242880 | 10512.5 | 4400 | 590802.5 | 247280 | 709016.75 | 296758.497 | 155430 | 65055.1249 | 936034 | 391776.4185 | 47492.5 | 19877.9548 | 15840 | 6629.8216 | 177173.3333 | 74155.7828 | 14080 | 5893.1748 | 348800 | 145990.0119 | 1694849.8333 | 709378.2893 | 652221.7812 | 272987 | 326150.3125 | 136510 | 40325.0039 | 16878.004 | 17826.0462 | 7461.08 | 692546.7851 | 289865.004 | 343976.3587 | 143971.08 | 1084.4361 | 453.89 | 9900 | 4143.6385 | 10984.4361 | 4597.5285 | 0 | 0 | 7430376.2203 | 3109979.1077 | 1052993.1087 | 440729.577 | 2389204.5455 | 6780458.2044 | 9819580.7658 | 7833451.3131
353-904R | oh | 2 | 9.339 | 9.339 | 7.0653 | 7.0653 | 9.6713 | 33020.46 | 4673.5834 | 63261 | 8953.7081 | 57970 | 8204.8412 | 158470.7143 | 22429.309 | 312722.1743 | 44261.4416 | 2494800 | 353103.9807 | 4561931.1375 | 645677.4268 | 1560609.072 | 220882.3455 | 6122540.2095 | 866559.7723 | 8617340.2095 | 1219663.753 | 2950000 | 417531.162 | 11880062.3838 | 1681456.3567 | 111357.18 | 15761.0484 | 45356.85 | 6419.6265 | 156714.03 | 22180.6749 | 1716030 | 242880 | 31087.5 | 4400 | 1747117.5 | 247280 | 1903831.53 | 269460.6749 | 470250 | 66557.2979 | 2831950 | 400822.8388 | 143687.5 | 20336.9522 | 28710 | 4063.4982 | 321126.6667 | 45450.9798 | 25520 | 3611.9984 | 632200 | 89479.0511 | 4453444.1667 | 630322.6163 | 1928746.2187 | 272987 | 964489.6875 | 136510 | 119368.2281 | 16894.9 | 52737.9231 | 7464.314 | 2048114.4469 | 289881.9 | 1017227.6106 | 143974.314 | 3206.8876 | 453.89 | 9900 | 1401.2063 | 13106.8876 | 1855.0963 | 0 | 0 | 18394727.8849 | 2603515.9692 | 2921059.1406 | 413434.9889 | 7065340.9091 | 19342561.0461 | 25460068.794 | 22263620.1867
354-1706R | oh | 2 | 21.9403 | 21.9403 | 17.0706 | 17.0706 | 21.7363 | 72359.65 | 4238.8354 | 138627.5 | 8120.8126 | 114537.5 | 6709.618 | 347266.0714 | 20342.8806 | 672790.7214 | 39412.1466 | 5467000 | 320257.3974 | 9996824.4062 | 585614.9564 | 3419853.2133 | 200335.3374 | 13416677.6196 | 785950.2938 | 18883677.6196 | 1106207.6912 | 5475000 | 320726.0382 | 25031468.341 | 1466345.876 | 244023.45 | 14294.9177 | 118988.1 | 6970.3346 | 363011.55 | 21265.2523 | 4146118 | 242880 | 75110.8333 | 4400 | 4221228.8333 | 247280 | 4584240.3833 | 268545.2523 | 1138500 | 66693.4419 | 6856300 | 401642.728 | 347875 | 20378.5517 | 74250 | 4349.5723 | 830500 | 48650.7716 | 66000 | 3866.2865 | 1635000 | 95778.4607 | 10948425 | 641359.8127 | 4660063.8771 | 272987 | 2330313.6042 | 136510 | 272073.596 | 15938.098 | 124548.7838 | 7296.08 | 4932137.4731 | 288925.098 | 2454862.388 | 143806.08 | 7748.1946 | 453.89 | 9900 | 579.943 | 17648.1946 | 1033.833 | 0 | 0 | 40929679.0087 | 2397664.6197 | 7039102.7713 | 412351.3323 | 17070643.9394 | 43472693.2715 | 58000322.9481 | 50511796.0428
354-24AE | oh | 2 | 13.9604 | 13.9604 | 3.4697 | 3.4697 | 4.8179 | 15491.08 | 4464.6781 | 29678 | 8553.4847 | 23842.5 | 6871.6376 | 74344.2857 | 21426.7374 | 143355.8657 | 41316.5377 | 1170400 | 337320.524 | 2140165.225 | 616816.1784 | 732137.5893 | 211009.0869 | 2872302.8143 | 827825.2653 | 4042702.8143 | 1165145.7893 | 1025000 | 295414.8472 | 5211058.68 | 1501877.1742 | 52241.64 | 15056.5425 | 82467 | 23767.7817 | 134708.64 | 38824.3242 | 842720 | 242880 | 15266.6667 | 4400 | 857986.6667 | 247280 | 992695.3067 | 286104.3242 | 218790 | 63057.3799 | 1317602 | 379745.5546 | 66852.5 | 19267.5328 | 12870 | 3709.2576 | 143953.3333 | 41488.7336 | 11440 | 3297.1179 | 283400 | 81678.6026 | 2054907.8333 | 592244.179 | 947182.1667 | 272987 | 473648.3333 | 136510 | 55223.3882 | 15915.911 | 25302.0192 | 7292.285 | 1002405.5548 | 288902.911 | 498950.3525 | 143802.285 | 1574.8608 | 453.89 | 9900 | 2853.2751 | 11474.8608 | 3307.1651 | 0 | 0 | 8279846.929 | 2386331.4293 | 1491645.6592 | 429906.6092 | 3469696.9697 | 9635771.3288 | 11749543.8987 | 11127416.9879
355-41R | oh | 2 | 7.2148 | 7.2148 | 4.728 | 4.728 | 5.7904 | 26701.73 | 5647.5378 | 51155.5 | 10819.6219 | 42542.5 | 8997.933 | 128146.0714 | 27103.4793 | 248545.8014 | 52568.572 | 2017400 | 426689.3126 | 3688969.0063 | 780233.7908 | 1261974.0027 | 266913.2645 | 4950943.0089 | 1047147.0552 | 6968343.0089 | 1473836.3679 | 2175000 | 460022.4323 | 9391888.8103 | 1986427.3722 | 90048.09 | 19045.5822 | 55370.7 | 11711.1559 | 145418.79 | 30756.7382 | 1148344 | 242880 | 20803.3333 | 4400 | 1169147.3333 | 247280 | 1314566.1233 | 278036.7382 | 484110 | 102391.4757 | 2915418 | 616624.2205 | 147922.5 | 31286.2842 | 43065 | 9108.4442 | 481690 | 101879.6347 | 38280 | 8096.3948 | 948300 | 200569.7805 | 5058785.5 | 1069956.2346 | 1290690.8083 | 272987 | 645423.4167 | 136510 | 75530.6623 | 15975.08 | 34531.0369 | 7303.472 | 1366221.4707 | 288962.08 | 679954.4536 | 143813.472 | 2146.0057 | 453.89 | 9900 | 2093.8952 | 12046.0057 | 2547.7852 | 0 | 0 | 15828941.7867 | 3347893.4719 | 1994520.5769 | 421850.2102 | 4728030.303 | 11580792.545 | 20556972.0897 | 13575313.122
355-6R | oh | 2 | 3.4479 | 3.4479 | 1.2307 | 1.2307 | 1.56 | 7337.88 | 5962.451 | 14058 | 11422.9363 | 7947.5 | 6457.8024 | 35215.7143 | 28614.8002 | 64559.0943 | 52457.9898 | 554400 | 450481.9945 | 1013762.475 | 823740.5152 | 346802.016 | 281796.652 | 1360564.491 | 1105537.1672 | 1914964.491 | 1556019.1617 | 375000 | 304709.1413 | 2354523.5853 | 1913186.2928 | 24746.04 | 20107.5856 | 30630.6 | 24889.1302 | 55376.64 | 44996.7158 | 298908 | 242880 | 5415 | 4400 | 304323 | 247280 | 359699.64 | 292276.7158 | 228690 | 185823.8227 | 1377222 | 1119072.3546 | 69877.5 | 56779.5014 | 12375 | 10055.4017 | 138416.6667 | 112471.5297 | 11000 | 8938.1348 | 272500 | 221421.976 | 2110081.1667 | 1714562.7208 | 335960.1375 | 272987 | 168000.375 | 136510 | 19633.2061 | 15953.113 | 8983.2007 | 7299.369 | 355593.3436 | 288940.113 | 176983.5757 | 143809.369 | 558.5942 | 453.89 | 9900 | 8044.3213 | 10458.5942 | 8498.2113 | 0 | 0 | 4830656.6897 | 3925187.3379 | 536683.2157 | 436086.0848 | 1230681.8182 | 3119966.7569 | 6061338.5079 | 3656649.9726
356-16R | oh | 2 | 7.9983 | 7.9983 | 4.3428 | 4.3428 | 4.8525 | 24663.43 | 5679.15 | 47250.5 | 10880.1849 | 37867.5 | 8719.5988 | 118363.9286 | 27255.1916 | 228145.3586 | 52534.1253 | 1863400 | 429077.7148 | 3407368.3188 | 784601.1654 | 1165640.1093 | 268407.3169 | 4573008.4281 | 1053008.4823 | 6436408.4281 | 1482086.1971 | 1575000 | 362668.9926 | 8239553.7867 | 1897289.315 | 83174.19 | 19152.1903 | 57137.85 | 13156.9057 | 140312.04 | 32309.096 | 1054780 | 242880 | 19108.3333 | 4400 | 1073888.3333 | 247280 | 1214200.3733 | 279589.096 | 323730 | 74544.0209 | 1949574 | 448920.6594 | 98917.5 | 22777.3397 | 32670 | 7522.7911 | 365420 | 84143.8116 | 29040 | 6686.9254 | 719400 | 165653.3799 | 3518751.5 | 810248.928 | 1185528.7708 | 272987 | 592836.0417 | 136510 | 69405.5272 | 15981.735 | 31721.3142 | 7304.341 | 1254934.298 | 288968.735 | 624557.3559 | 143814.341 | 1971.1549 | 453.89 | 9900 | 2279.6337 | 11871.1549 | 2733.5237 | 0 | 0 | 13025110.7395 | 2999240.5017 | 1838757.7292 | 423403.437 | 4342803.0303 | 9704946.8077 | 17367913.7698 | 11543704.5369
356-19R | oh | 3 | 26.7619 | 26.7619 | 18.8011 | 18.8011 | 23.7526 | 87850.73 | 4672.6287 | 168305.5 | 8951.8791 | 164092.5 | 8727.7969 | 421610.3571 | 22424.7274 | 841859.0871 | 44777.0321 | 6637400 | 353031.8525 | 12136989.6312 | 645545.5349 | 4151990.8027 | 220837.2261 | 16288980.4339 | 866382.7611 | 22926380.4339 | 1219414.6136 | 7200000 | 382955.5757 | 30968239.5211 | 1647147.2214 | 296265.09 | 15757.8289 | 166701.15 | 8866.5465 | 462966.24 | 24624.3754 | 4566420 | 242880 | 82725 | 4400 | 4649145 | 247280 | 5112111.24 | 271904.3754 | 1049400 | 55815.7752 | 6319720 | 336135.0015 | 320650 | 17054.8202 | 69795 | 3712.2756 | 780670 | 41522.4902 | 62040 | 3299.8005 | 1536900 | 81745.0589 | 10139175 | 539285.2221 | 5132465.8125 | 272987 | 2566543.125 | 136510 | 308511.5128 | 16409.195 | 138739.5452 | 7379.317 | 5440977.3253 | 289396.195 | 2705282.6702 | 143889.317 | 8533.6478 | 453.89 | 9900 | 526.5639 | 18433.6478 | 980.4539 | 0 | 0 | 46566825.4942 | 2476809.0925 | 7817393.9102 | 415793.6924 | 18801136.3636 | 47505147.1706 | 65367961.8578 | 55322541.0808
356-30AE | oh | 3 | 25.1741 | 25.1741 | 14.6992 | 14.6992 | 17.535 | 82143.49 | 5588.2805 | 157371.5 | 10706.096 | 143990 | 9795.7429 | 394220.3571 | 26819.0935 | 777725.3471 | 52909.2129 | 6206200 | 422212.2352 | 11348507.7063 | 772047.115 | 3882255.9013 | 264112.6522 | 15230763.6076 | 1036159.7671 | 21436963.6076 | 1458372.0024 | 5600000 | 380972.0146 | 27814688.9547 | 1892253.2299 | 277018.17 | 18845.7447 | 176125.95 | 11981.9746 | 453144.12 | 30827.7193 | 3570152 | 242880 | 64676.6667 | 4400 | 3634828.6667 | 247280 | 4087972.7867 | 278107.7193 | 957330 | 65127.8462 | 5765254 | 392214.3627 | 292517.5 | 19900.1752 | 57915 | 3939.999 | 647790 | 44069.6181 | 51480 | 3502.2213 | 1275300 | 86759.5733 | 9047586.5 | 615513.7958 | 4012702.0917 | 272987 | 2006593.5833 | 136510 | 234438.2027 | 15948.999 | 107286.1397 | 7298.753 | 4247140.2944 | 288935.999 | 2113879.7231 | 143808.753 | 6671.8391 | 453.89 | 9900 | 673.5041 | 16571.8391 | 1127.3941 | 0 | 0 | 41125987.5883 | 2797830.4188 | 6201852.5097 | 421916.4723 | 14699242.4242 | 35069956.6417 | 55825230.0125 | 41271809.1514
357-1299R | oh | 3 | 2.7741 | 2.7741 | 2.6642 | 2.6642 | 3.7325 | 9172.35 | 3442.81 | 17572.5 | 6595.7774 | 17765 | 6668.0316 | 44019.6429 | 16522.6213 | 88529.4929 | 33229.2402 | 693000 | 260115.1631 | 1267203.0938 | 475640.3167 | 433502.52 | 162713.6778 | 1700705.6138 | 638353.9945 | 2393705.6138 | 898469.1576 | 100000 | 37534.6556 | 2582235.1066 | 969233.0535 | 30932.55 | 11610.4261 | 7068.6 | 2653.1747 | 38001.15 | 14263.6008 | 647082 | 242880 | 11722.5 | 4400 | 658804.5 | 247280 | 696805.65 | 261543.6008 | 46530 | 17464.8752 | 280214 | 105177.3598 | 14217.5 | 5336.4897 | 5940 | 2229.5585 | 66440 | 24938.0252 | 5280 | 1981.8298 | 130800 | 49095.3295 | 549421.5 | 206223.4677 | 727293.2062 | 272987 | 363690.5625 | 136510 | 55907.7676 | 20984.788 | 21803.0587 | 8183.703 | 783200.9738 | 293971.788 | 385493.6212 | 144693.703 | 1209.2558 | 453.89 | 9900 | 3715.9309 | 11109.2558 | 4169.8209 | 0 | 0 | 3925966.8362 | 1473598.13 | 1082299.2712 | 406237.3038 | 2664204.5455 | 7464994.3368 | 6590171.3817 | 8547293.608
357-2049F | oh | 3 | 6.4667 | 6.4667 | 5.6208 | 5.6208 | 6.3694 | 28740.03 | 5113.1262 | 55060.5 | 9795.7895 | 50490 | 8982.6538 | 137928.2143 | 24538.7483 | 272218.7443 | 48430.3177 | 2171400 | 386312.8243 | 3970569.6938 | 706402.3176 | 1358307.896 | 241655.9637 | 5328877.5898 | 948058.2813 | 7500277.5898 | 1334371.1057 | 2450000 | 435878.4285 | 10222496.334 | 1818679.8519 | 96921.99 | 17243.3489 | 49480.2 | 8803.0007 | 146402.19 | 26046.3496 | 1365188 | 242880 | 24731.6667 | 4400 | 1389919.6667 | 247280 | 1536321.8567 | 273326.3496 | 399960 | 71156.7087 | 2408648 | 428521.5122 | 122210 | 21742.3277 | 48510 | 8630.3929 | 542593.3333 | 96532.5426 | 43120 | 7671.4603 | 1068200 | 190042.9948 | 4633241.3333 | 824297.9392 | 1534414.4292 | 272987 | 767299.9583 | 136510 | 105225.6367 | 18720.647 | 43759.3454 | 7785.206 | 1639640.0658 | 291707.647 | 811059.3037 | 144295.206 | 2551.24 | 453.89 | 9900 | 1761.3047 | 12451.24 | 2215.1947 | 0 | 0 | 16507828.9733 | 2936900.6328 | 2347381.1604 | 417621.5556 | 5620833.3333 | 12738763.0002 | 22128662.3066 | 15086144.1606
357-45R | oh | 3 | 18.0269 | 18.0269 | 9.6792 | 9.6792 | 0.080347 | 49530.69 | 5117.2474 | 94891.5 | 9803.6849 | 95837.5 | 9901.4206 | 237706.0714 | 24558.5265 | 477965.7614 | 49380.8794 | 3742200 | 386624.1929 | 6842896.7062 | 706971.6786 | 2340913.608 | 241850.7387 | 9183810.3142 | 948822.4173 | 12926010.3142 | 1335446.6102 | 4850000 | 501076.1946 | 18253976.0757 | 1885903.6841 | 167035.77 | 17257.247 | 126645.75 | 13084.365 | 293681.52 | 30341.6121 | 2350876 | 242880 | 42588.3333 | 4400 | 2393464.3333 | 247280 | 2687145.8533 | 277621.6121 | 735570 | 75995.1786 | 4429766 | 457659.8536 | 224757.5 | 23220.749 | 72270 | 7466.5519 | 808353.3333 | 83514.7654 | 64240 | 6636.935 | 1591400 | 164414.9806 | 7926356.8333 | 818909.0142 | 2642286.6708 | 272987 | 1321303.0417 | 136510 | 174666.3603 | 18045.599 | 74210.9161 | 7667.077 | 2816953.0312 | 291032.599 | 1395513.9578 | 144177.077 | 4393.277 | 453.89 | 9900 | 1022.8153 | 14293.277 | 1476.7053 | 0 | 0 | 29011579.2171 | 2997322.0026 | 4082659.8111 | 421798.6891 | 9679166.6667 | 160694.4714 | 38690745.8838 | 4243354.2825
357-50R | oh | 3 | 15.7551 | 15.7551 | 8.6547 | 8.6547 | 10.7992 | 47288.56 | 5463.8947 | 90596 | 10467.7961 | 88357.5 | 10209.1516 | 226945.7143 | 26222.1452 | 453187.7743 | 52362.9877 | 3572800 | 412814.4955 | 6533135.95 | 754862.6347 | 2234946.3253 | 258233.9453 | 8768082.2753 | 1013096.5799 | 12340882.2753 | 1425911.0754 | 4325000 | 499726.4591 | 17119070.0496 | 1978000.5222 | 159474.48 | 18426.2699 | 115453.8 | 13339.9581 | 274928.28 | 31766.2279 | 2102062 | 242880 | 38080.8333 | 4400 | 2140142.8333 | 247280 | 2415071.1133 | 279046.2279 | 925650 | 106953.0166 | 5574470 | 644094.8334 | 282837.5 | 32680.0884 | 75240 | 8693.5072 | 841573.3333 | 97238.4883 | 66880 | 7727.562 | 1656800 | 191432.7855 | 9423450.8333 | 1088820.2814 | 2362630.1021 | 272987 | 1181457.8542 | 136510 | 148232.119 | 17127.286 | 64953.9062 | 7505.014 | 2510862.2211 | 290114.286 | 1246411.7604 | 144015.014 | 3928.2976 | 453.89 | 9900 | 1143.8825 | 13828.2976 | 1597.7725 | 0 | 0 | 29067211.4016 | 3358532.8621 | 3661482.8737 | 423061.2419 | 8654734.8485 | 21598437.3268 | 37721946.2501 | 25259920.2005
357-750R | oh | 2 | 12.9038 | 12.9038 | 7.1746 | 7.1746 | 8.066 | 35262.59 | 4914.9062 | 67556.5 | 9416.0372 | 65450 | 9122.4328 | 169231.0714 | 23587.4573 | 337500.1614 | 47040.8334 | 2664200 | 371336.677 | 4871691.8937 | 679017.2958 | 1666576.3547 | 232287.7132 | 6538268.2484 | 911305.009 | 9202468.2484 | 1282641.6861 | 3325000 | 463439.1004 | 12864968.4098 | 1793121.6199 | 118918.47 | 16574.8778 | 95426.1 | 13300.507 | 214344.57 | 29875.3849 | 1742572 | 242880 | 31568.3333 | 4400 | 1774140.3333 | 247280 | 1988484.9033 | 277155.3849 | 612810 | 85413.5684 | 3690478 | 514379.49 | 187247.5 | 26098.5904 | 55935 | 7796.2304 | 625643.3333 | 87202.2808 | 49720 | 6929.9826 | 1231700 | 171674.5684 | 6453533.8333 | 899494.7109 | 1958578.3208 | 272987 | 979407.5417 | 136510 | 129750.1906 | 18084.605 | 55060.3821 | 7674.326 | 2088328.5115 | 291071.605 | 1034467.9238 | 144184.326 | 3256.4888 | 453.89 | 9900 | 1379.8638 | 13156.4888 | 1833.7538 | 0 | 0 | 21419987.2435 | 2985521.6896 | 3022952.8271 | 421339.7109 | 7174621.2121 | 16132097.2386 | 28594608.4556 | 19155050.0657
358-682F | oh | 3 | 11.6621 | 11.6621 | 10.4532 | 10.4532 | 13.5028 | 46269.41 | 4426.331 | 88643.5 | 8480.0188 | 61710 | 5903.4443 | 222054.6429 | 21242.7031 | 418677.5529 | 40052.4972 | 3495800 | 334423.2783 | 6392335.6063 | 611518.3447 | 2186779.3787 | 209196.73 | 8579114.9849 | 820715.0747 | 12074914.9849 | 1155138.3531 | 2950000 | 282209.7005 | 15443592.5378 | 1477400.5508 | 156037.53 | 14927.2219 | 60083.1 | 5747.808 | 216120.63 | 20675.0299 | 2538878 | 242880 | 45994.1667 | 4400 | 2584872.1667 | 247280 | 2800992.7967 | 267955.0299 | 322740 | 30874.6979 | 1943612 | 185934.2917 | 98615 | 9433.9355 | 53955 | 5161.5676 | 603496.6667 | 57733.0893 | 47960 | 4588.0601 | 1188100 | 113658.7611 | 4258478.6667 | 407384.4031 | 2853593.0854 | 272987 | 1426969.0208 | 136510 | 301786.8151 | 28870.226 | 100073.8779 | 9573.498 | 3155379.9005 | 301857.226 | 1527042.8987 | 146083.498 | 4744.6119 | 453.89 | 9900 | 947.0766 | 14644.6119 | 1400.9666 | 0 | 0 | 22872095.7168 | 2188043.1465 | 4328035.6954 | 414038.5279 | 10453219.697 | 27005647.0076 | 33325315.4138 | 31333682.703
387-15 | oh | 3 | 12.7566 | 4.2057 | 3.0775 | 6.3288 | 9.0618 | 22421.3 | 3542.7479 | 42955 | 6787.2396 | 30387.5 | 4801.4723 | 37172.1429 | 5873.5011 | 132935.9429 | 21004.961 | 1694000 | 267665.7888 | 3097607.5625 | 489447.2088 | 1059672.8267 | 167436.9322 | 4157280.3892 | 656884.141 | 5851280.3892 | 924549.9298 | 275000 | 43452.2384 | 6259216.332 | 989007.1293 | 75612.9 | 11947.4537 | 46534.95 | 7352.9009 | 122147.85 | 19300.3546 | 1537136 | 242880 | 27846.6667 | 4400 | 1564982.6667 | 247280 | 1687130.5167 | 266580.3546 | 306900 | 48492.6981 | 1848220 | 292033.8042 | 93775 | 14817.2133 | 17325 | 2737.491 | 193783.3333 | 30619.344 | 15400 | 2433.3254 | 381500 | 60280.1053 | 2856903.3333 | 451413.9813 | 840107.1521 | 132743.7683 | 420104.3542 | 66379.9075 | 46972.3722 | 7422.0172 | 22086.5887 | 3489.8608 | 887079.5243 | 140165.7855 | 442190.9428 | 69869.7683 | 2872.5735 | 453.89 | 9900 | 1564.2806 | 12772.5735 | 2018.1706 | 0 | 0 | 10015971.7632 | 1582605.0667 | 2129321.4595 | 336450.1229 | 6328787.8788 | 18123663.459 | 16344759.642 | 20252984.9185
393-14R | oh | 2 | 9.4062 | 3.268 | 1.5102 | 2.068 | 2.5699 | 11006.82 | 5322.4663 | 21087 | 10196.8459 | 19167.5 | 9268.651 | 40106.7857 | 19394.068 | 91368.1057 | 44182.0312 | 831600 | 402129.1327 | 1520643.7125 | 735323.6379 | 520203.024 | 251549.7726 | 2040846.7365 | 986873.4105 | 2872446.7365 | 1389002.5432 | 875000 | 423115.6699 | 3838814.8422 | 1856300.2442 | 37119.06 | 17949.3211 | 60672.15 | 29338.6713 | 97791.21 | 47287.9924 | 502274 | 242880 | 9099.1667 | 4400 | 511373.1667 | 247280 | 609164.3767 | 294567.9924 | 117810 | 56968.2938 | 709478 | 343075.7249 | 35997.5 | 17406.9787 | 1980 | 957.4503 | 22146.6667 | 10709.2591 | 1760 | 851.0669 | 43600 | 21083.2494 | 932772.1667 | 451052.0231 | 412272.4125 | 199358.7634 | 206161.125 | 99691.4314 | 25181.4601 | 12176.7661 | 11214.9658 | 5423.1175 | 437453.8726 | 211535.5296 | 217376.0908 | 105114.5489 | 938.6411 | 453.89 | 9900 | 4787.2516 | 10838.6411 | 5241.1416 | 0 | 0 | 5219879.5225 | 2524128.9385 | 826540.4675 | 399682.5413 | 2067992.4242 | 5139761.1093 | 7287871.9468 | 5966301.5768
396-699R | oh | 2 | 24.5655 | 22.1294 | 18.8928 | 20.5477 | 26.7259 | 102526.49 | 4989.6754 | 196421.5 | 9559.2811 | 212245 | 10329.3662 | 448022.1429 | 21803.9755 | 959215.1329 | 46682.2982 | 7746200 | 376985.7317 | 14164514.5813 | 689347.0209 | 4845594.8347 | 235821.4498 | 19010109.4159 | 925168.4706 | 26756309.4159 | 1302154.2023 | 11725000 | 570622.7187 | 39440524.5488 | 1919459.2193 | 345757.17 | 16827.0274 | 129001.95 | 6278.1615 | 474759.12 | 23105.1889 | 4990632 | 242880 | 90410 | 4400 | 5081042 | 247280 | 5555801.12 | 270385.1889 | 1771110 | 86194.9342 | 10666018 | 519085.0481 | 541172.5 | 26337.341 | 63360 | 3083.5527 | 708693.3333 | 34490.108 | 56320 | 2740.9357 | 1395200 | 67900.4535 | 15201873.8333 | 739832.3733 | 5157489.6208 | 251000.4903 | 2579056.5417 | 125515.4163 | 314728.4421 | 15316.9466 | 140238.5374 | 6825.0145 | 5472218.0629 | 266317.437 | 2719295.0791 | 132340.4308 | 9326.4079 | 453.89 | 9900 | 481.8051 | 19226.4079 | 935.6951 | 0 | 0 | 60133842.8529 | 2926544.7246 | 8275096.1991 | 402725.6197 | 20547727.2727 | 53451867.0838 | 80681570.1257 | 61726963.2829
411-1873R | oh | 2 | 7.2172 | 7.2172 | 6.7498 | 6.7498 | 8.1257 | 39746.85 | 5888.5874 | 76147.5 | 11281.4276 | 81345 | 12051.4493 | 190751.7857 | 28260.3167 | 387991.1357 | 57481.7811 | 3003000 | 444901.3721 | 5491213.4062 | 813535.9237 | 1878510.92 | 278305.7229 | 7369724.3262 | 1091841.6466 | 10372724.3262 | 1536743.0187 | 3725000 | 551867.3363 | 14485715.462 | 2146092.1361 | 134041.05 | 19858.4905 | 53603.55 | 7941.4895 | 187644.6 | 27799.98 | 1639394 | 242880 | 29699.1667 | 4400 | 1669093.1667 | 247280 | 1856737.7667 | 275079.98 | 530640 | 78615.5392 | 3195632 | 473440.2469 | 162140 | 24021.4147 | 15345 | 2273.3971 | 171636.6667 | 25428.3678 | 13640 | 2020.7974 | 337900 | 50060.6639 | 4426933.6667 | 655860.4271 | 1842610.5479 | 272987 | 921416.6458 | 136510 | 95833.568 | 14197.964 | 47176.755 | 6989.345 | 1938444.1159 | 287184.964 | 968593.4008 | 143499.345 | 3063.6715 | 453.89 | 9900 | 1466.7078 | 12963.6715 | 1920.5978 | 0 | 0 | 20864056.9161 | 3091058.125 | 2825331.1675 | 418579.325 | 6749810.6061 | 16251345.8628 | 27613867.5221 | 19076677.0303
411-30R | oh | 3 | 28.2934 | 28.2934 | 17.7117 | 17.7117 | 20.6931 | 100895.85 | 5696.5513 | 193297.5 | 10913.5225 | 203830 | 11508.1845 | 484216.0714 | 27338.7033 | 982239.4214 | 55456.9617 | 7623000 | 430392.4378 | 13939234.0312 | 787005.2363 | 4768527.72 | 269229.735 | 18707761.7512 | 1056234.9713 | 26330761.7512 | 1486627.4091 | 8950000 | 505314.4849 | 36263001.1727 | 2047398.8557 | 340258.05 | 19210.8739 | 197331.75 | 11141.2952 | 537589.8 | 30352.169 | 4301828 | 242880 | 77931.6667 | 4400 | 4379759.6667 | 247280 | 4917349.4667 | 277632.169 | 1248390 | 70483.7486 | 7518082 | 424468.797 | 381452.5 | 21536.701 | 56430 | 3186.0219 | 631180 | 35636.2454 | 50160 | 2832.0195 | 1242600 | 70156.8468 | 11128294.5 | 628300.3802 | 4835075.4292 | 272987 | 2417829.9583 | 136510 | 251432.6896 | 14195.819 | 123787.6335 | 6989.015 | 5086508.1188 | 287182.819 | 2541617.5918 | 143499.015 | 8039.1828 | 453.89 | 9900 | 558.9512 | 17939.1828 | 1012.8412 | 0 | 0 | 52495742.9742 | 2963894.8962 | 7458967.0585 | 421131.184 | 17711742.4242 | 41386128.0605 | 70207485.3985 | 48845095.1189
411-47R | oh | 2 | 17.3881 | 5.2898 | 2.8362 | 10.8545 | 13.3524 | 54422.61 | 5013.8083 | 104263.5 | 9605.5151 | 112667.5 | 10379.7529 | 45976.0714 | 4235.6515 | 317329.6814 | 29234.7278 | 4111800 | 378809.0452 | 7518738.3563 | 692681.0881 | 2572114.952 | 236962.014 | 10090853.3083 | 929643.1021 | 14202653.3083 | 1308452.1473 | 525000 | 48366.8342 | 15044982.9897 | 1386053.7093 | 183533.13 | 16908.4123 | 111919.5 | 10310.8417 | 295452.63 | 27219.254 | 2636352 | 242880 | 47760 | 4400 | 2684112 | 247280 | 2979564.63 | 274499.254 | 654390 | 60287.1859 | 3940882 | 363062.8308 | 199952.5 | 18421.0846 | 19305 | 1778.5176 | 215930 | 19893.0486 | 17160 | 1580.9045 | 425100 | 39163.3166 | 5472719.5 | 504186.8886 | 774238.6979 | 71328.5233 | 387166.1458 | 35668.5729 | 40266.1215 | 3709.6092 | 19822.8755 | 1826.2281 | 814504.8194 | 75038.1324 | 406989.0213 | 37494.801 | 4926.7696 | 453.89 | 9900 | 912.0603 | 14826.7696 | 1365.9503 | 0 | 0 | 21347034.0787 | 1966644.6806 | 3386553.6513 | 311994.055 | 10854545.4545 | 26704865.517 | 32201579.5333 | 30091419.1683
441-23R | oh | 3 | 7.1263 | 7.1263 | 5.1261 | 5.1261 | 4.4175 | 16917.89 | 3300.3199 | 32411.5 | 6322.7932 | 12155 | 2371.1816 | 81191.7857 | 15838.7877 | 142676.1757 | 27833.0824 | 1278200 | 249349.5899 | 2337285.7062 | 455954.649 | 799571.3147 | 155979.3298 | 3136857.0209 | 611933.9788 | 4415057.0209 | 861283.5687 | 550000 | 107293.2831 | 5107733.1966 | 996409.9342 | 57053.37 | 11129.8971 | 8835.75 | 1723.6666 | 65889.12 | 12853.5636 | 1245036 | 242880 | 22555 | 4400 | 1267591 | 247280 | 1333480.12 | 260133.5636 | 362340 | 70684.8149 | 2182092 | 425679.663 | 110715 | 21598.1379 | 9405 | 1834.7151 | 105196.6667 | 20521.6286 | 8360 | 1630.8579 | 207100 | 40400.798 | 2985208.6667 | 582350.6155 | 1399368.5875 | 272987 | 699768.875 | 136510 | 154725.4956 | 30183.648 | 50261.3928 | 9804.927 | 1554094.0831 | 303170.648 | 750030.2678 | 146314.927 | 2326.702 | 453.89 | 9900 | 1931.2791 | 12226.702 | 2385.1691 | 0 | 0 | 9659262.6484 | 1884316.3668 | 2083510.3878 | 406448.4906 | 5126136.3636 | 8834945.1342 | 14785399.0121 | 10918455.522
441-279R | oh | 3 | 4.4066 | 4.4066 | 2.1595 | 2.1595 | 1.5458 | 10191.5 | 4719.4457 | 19525 | 9041.5717 | 2337.5 | 1082.4417 | 48910.7143 | 22649.4099 | 80964.7143 | 37492.8689 | 770000 | 356569.023 | 1408003.4375 | 652013.5196 | 481669.4667 | 223049.8846 | 1889672.9042 | 875063.4041 | 2659672.9042 | 1231632.4271 | 75000 | 34730.749 | 2815637.6185 | 1303856.045 | 34369.5 | 15915.713 | 6479.55 | 3000.5283 | 40849.05 | 18916.2414 | 524492 | 242880 | 9501.6667 | 4400 | 533993.6667 | 247280 | 574842.7167 | 266196.2414 | 48510 | 22463.8484 | 292138 | 135282.2873 | 14822.5 | 6863.9537 | 3465 | 1604.5606 | 38756.6667 | 17947.3075 | 3080 | 1426.2761 | 76300 | 35332.7486 | 477072.1667 | 220920.9823 | 589507.1542 | 272987 | 294789.2083 | 136510 | 65290.1562 | 30234.347 | 21191.9947 | 9813.518 | 654797.3103 | 303221.347 | 315981.2031 | 146323.518 | 980.1617 | 453.89 | 9900 | 4584.4589 | 10880.1617 | 5038.3489 | 0 | 0 | 3958387.2571 | 1833036.7232 | 890823.9197 | 412519.7594 | 2159469.697 | 3091665.6934 | 6117856.9541 | 3982489.6131
441-27R | oh | 3 | 7.5343 | 7.5343 | 7.3795 | 7.3795 | 6.9611 | 24459.6 | 3314.5131 | 46860 | 6349.9846 | 22440 | 3040.8377 | 117385.7143 | 15906.9031 | 211145.3143 | 28612.2385 | 1848000 | 250421.9279 | 3379208.25 | 457915.5005 | 1156006.72 | 156650.1253 | 4535214.97 | 614565.6257 | 6383214.97 | 864987.5537 | 1025000 | 138897.4438 | 7619360.2843 | 1032497.2359 | 82486.8 | 11177.7616 | 16493.4 | 2235.0157 | 98980.2 | 13412.7773 | 1792344 | 242880 | 32470 | 4400 | 1824814 | 247280 | 1923794.2 | 260692.7773 | 119790 | 16232.7071 | 721402 | 97756.9695 | 36602.5 | 4959.9938 | 17325 | 2347.7056 | 193783.3333 | 26259.5216 | 15400 | 2086.8494 | 381500 | 51696.951 | 1485802.8333 | 201340.6981 | 2014519.975 | 272987 | 1007381.75 | 136510 | 221984.0773 | 30080.996 | 72224.1574 | 9787.074 | 2236504.0523 | 303067.996 | 1079605.9074 | 146297.074 | 3349.5019 | 453.89 | 9900 | 1341.546 | 13249.5019 | 1795.436 | 0 | 0 | 11354916.6718 | 1538701.3661 | 3003400.1074 | 406989.8513 | 7379545.4545 | 13922236.6005 | 18734462.1264 | 16925636.7079
441-30R | oh | 3 | 6.2754 | 6.2754 | 5.7333 | 5.7333 | 5.2852 | 19975.34 | 3484.0709 | 38269 | 6674.8256 | 16362.5 | 2853.9244 | 95865 | 16720.6395 | 170471.84 | 29733.4605 | 1509200 | 263232.5581 | 2759686.7375 | 481340.71 | 944072.1547 | 164663.7479 | 3703758.8922 | 646004.4579 | 5212958.8922 | 909237.0161 | 800000 | 139534.8837 | 6183430.7322 | 1078505.3603 | 67364.22 | 11749.5733 | 12370.05 | 2157.5669 | 79734.27 | 13907.1401 | 1392512 | 242880 | 25226.6667 | 4400 | 1417738.6667 | 247280 | 1497472.9367 | 261187.1401 | 65340 | 11396.5116 | 393492 | 68632.3256 | 19965 | 3482.2674 | 15840 | 2762.7907 | 177173.3333 | 30902.3256 | 14080 | 2455.814 | 348800 | 60837.2093 | 1034690.3333 | 180469.2442 | 1565125.4667 | 272987 | 782657.3333 | 136510 | 171988.7283 | 29998.034 | 56028.4897 | 9772.411 | 1737114.1949 | 302985.034 | 838685.8231 | 146282.411 | 2602.3027 | 453.89 | 9900 | 1726.7442 | 12502.3027 | 2180.6342 | 0 | 0 | 8967737.5631 | 1564140.2726 | 2336158.7597 | 407469.5511 | 5733333.3333 | 10570357.4818 | 14701070.8964 | 12906516.2415
442-16R | oh | 3 | 10.7023 | 10.7023 | 10.6841 | 10.6841 | 10.2939 | 40154.51 | 3758.346 | 76928.5 | 7200.285 | 27582.5 | 2581.6422 | 192708.2143 | 18036.9314 | 337373.7243 | 31577.2046 | 3033800 | 283954.9032 | 5547533.5438 | 519233.0907 | 1897777.6987 | 177626.5023 | 7445311.2424 | 696859.593 | 10479111.2424 | 980814.4962 | 1325000 | 124016.1668 | 12141484.9667 | 1136407.8675 | 135415.83 | 12674.5299 | 12370.05 | 1157.8009 | 147785.88 | 13832.3308 | 2594952 | 242880 | 47010 | 4400 | 2641962 | 247280 | 2789747.88 | 261112.3308 | 873180 | 81727.1219 | 5258484 | 492178.8896 | 266805 | 24972.1761 | 13860 | 1297.2559 | 155026.6667 | 14510.0475 | 12320 | 1153.1164 | 305200 | 28565.8371 | 6884875.6667 | 644404.4444 | 2916617.925 | 272987 | 1458485.25 | 136510 | 285692.5802 | 26739.999 | 98267.1184 | 9197.518 | 3202310.5052 | 299726.999 | 1556752.3684 | 145707.518 | 4849.402 | 453.89 | 9900 | 926.6114 | 14749.402 | 1380.5014 | 0 | 0 | 22243420.5406 | 2081919.8124 | 4346500.2484 | 406819.8488 | 10684090.9091 | 20587796.9295 | 32927511.4497 | 24934297.178
442-509R | oh | 3 | 4.625 | 4.625 | 3.7778 | 3.7778 | 5.6038 | 18344.7 | 4855.8689 | 35145 | 9302.9328 | 7480 | 1979.9669 | 88039.2857 | 23304.1274 | 149008.9857 | 39442.8959 | 1386000 | 366876.222 | 2534406.1875 | 670861.0152 | 867005.04 | 229497.4989 | 3401411.2275 | 900358.5141 | 4787411.2275 | 1267234.7361 | 400000 | 105880.5835 | 5336420.2132 | 1412558.2156 | 61865.1 | 16375.7822 | 15904.35 | 4209.9046 | 77769.45 | 20585.6869 | 917562 | 242880 | 16622.5 | 4400 | 934184.5 | 247280 | 1011953.95 | 267865.6869 | 519750 | 137578.5832 | 3130050 | 828528.8013 | 158812.5 | 42037.9004 | 16335 | 4323.8983 | 182710 | 48363.6035 | 14520 | 3843.4652 | 359700 | 95213.1148 | 4381877.5 | 1159889.3668 | 1031301.4562 | 272987 | 515713.0625 | 136510 | 93517.5617 | 24754.235 | 33422.3621 | 8846.948 | 1124819.0179 | 297741.235 | 549135.4246 | 145356.948 | 1714.7242 | 453.89 | 9900 | 2620.5444 | 11614.7242 | 3074.4344 | 0 | 0 | 10854731.4553 | 2873263.2518 | 1561089.3746 | 413222.6349 | 3777840.9091 | 11207635.6976 | 14632572.3644 | 12768725.0721
442-525 | oh | 3 | 4.7371 | 4.7371 | 2.8098 | 2.8098 | 3.9257 | 14675.76 | 5222.972 | 28116 | 10006.2335 | 9350 | 3327.5816 | 70431.4286 | 25065.9169 | 122573.1886 | 43622.7039 | 1108800 | 394612.0248 | 2027524.95 | 721578.0356 | 693604.032 | 246847.4851 | 2721128.982 | 968425.5207 | 3829928.982 | 1363037.5455 | 500000 | 177945.5379 | 4452502.1706 | 1584605.7873 | 49492.08 | 17613.7896 | 17671.5 | 6289.1291 | 67163.58 | 23902.9187 | 682456 | 242880 | 12363.3333 | 4400 | 694819.3333 | 247280 | 761982.9133 | 271182.9187 | 442530 | 157492.4778 | 2665014 | 948454.6994 | 135217.5 | 48122.7015 | 12870 | 4580.3181 | 143953.3333 | 51231.7067 | 11440 | 4071.3939 | 283400 | 100859.5309 | 3694424.8333 | 1314812.8283 | 767052.1083 | 272987 | 383572.4167 | 136510 | 69127.3529 | 24601.808 | 24783.4453 | 8820.207 | 836179.4613 | 297588.808 | 408355.8619 | 145330.207 | 1275.3621 | 453.89 | 9900 | 3523.3217 | 11175.3621 | 3977.2117 | 0 | 0 | 8994281.8273 | 3200984.6352 | 1170338.7753 | 416513.1257 | 2809848.4848 | 7851320.7703 | 11804130.3121 | 9021659.5456
442-728R | oh | 3 | 19.9375 | 19.9375 | 15.4341 | 15.4341 | 19.1336 | 83366.47 | 5401.45 | 159714.5 | 10348.1637 | 16830 | 1090.4432 | 400089.6429 | 25922.4625 | 660000.6129 | 42762.5195 | 6298600 | 408096.5984 | 11517468.1188 | 746235.6019 | 3940056.2373 | 255282.6895 | 15457524.3561 | 1001518.2914 | 21756124.3561 | 1409614.8898 | 800000 | 51833.3088 | 23216124.9689 | 1504210.7181 | 281142.51 | 18215.6832 | 141372 | 9159.7232 | 422514.51 | 27375.4063 | 3748632 | 242880 | 67910 | 4400 | 3816542 | 247280 | 4239056.51 | 274655.4063 | 1348380 | 87363.7461 | 8120244 | 526123.8934 | 412005 | 26694.478 | 105930 | 6863.378 | 1184846.6667 | 76768.1539 | 94160 | 6100.7804 | 2332600 | 151132.9701 | 13598165.6667 | 881047.4 | 4213306.175 | 272987 | 2106907.75 | 136510 | 339243.8957 | 21980.167 | 129017.9646 | 8359.285 | 4552550.0707 | 294967.167 | 2235925.7146 | 144869.285 | 7005.3795 | 453.89 | 9900 | 641.4372 | 16905.3795 | 1095.3272 | 0 | 0 | 41383746.0858 | 2681320.6122 | 6474982.2246 | 419524.6913 | 15434090.9091 | 38267223.7764 | 56817836.9949 | 44742206.001
442-729 | oh | 3 | 3.2718 | 3.2718 | 2.7652 | 2.7652 | 4.1182 | 10395.33 | 3759.407 | 19915.5 | 7202.3178 | 467.5 | 169.0685 | 49888.9286 | 18042.0235 | 80667.2586 | 29172.8168 | 785400 | 284035.0685 | 1436163.5063 | 519379.679 | 491302.856 | 177676.6493 | 1927466.3623 | 697056.3283 | 2712866.3622 | 981091.3968 | 25000 | 9041.0959 | 2818533.6208 | 1019305.3094 | 35056.89 | 12678.1082 | 4712.4 | 1704.2104 | 39769.29 | 14382.3186 | 671600 | 242880 | 12166.6667 | 4400 | 683766.6667 | 247280 | 723535.9567 | 261662.3186 | 35640 | 12888.9863 | 214632 | 77620.3397 | 10890 | 3938.3014 | 8415 | 3043.2329 | 94123.3333 | 34039.1233 | 7480 | 2705.0959 | 185300 | 67012.6027 | 556480.3333 | 201247.6822 | 754850.4167 | 272987 | 377470.8333 | 136510 | 91094.9662 | 32943.933 | 71932.4662 | 26013.933 | 845945.3829 | 305930.933 | 449403.2996 | 162523.933 | 1255.0746 | 453.89 | 9900 | 3580.274 | 11155.0746 | 4034.164 | 0 | 0 | 4232114.4117 | 1530518.0886 | 1172939.2562 | 424186.2516 | 2765151.5152 | 8236312.0542 | 6997265.9268 | 9409251.3104
442-758F | oh | 3 | 1.1114 | 1.1114 | 1.1019 | 1.1019 | 1.6412 | 5095.75 | 4624.5376 | 9762.5 | 8859.7456 |  |  | 24455.3571 | 22193.9302 | 39313.6071 | 35678.2134 | 385000 | 349398.4187 | 704001.7188 | 638901.5254 | 240834.7333 | 218564.3506 | 944836.4521 | 857465.8761 | 1329836.4521 | 1206864.2948 | 0 | 0 | 1369150.0592 | 1242542.5082 | 17184.75 | 15595.648 | 1178.1 | 1069.1592 | 18362.85 | 16664.8072 | 267628 | 242880 | 4848.3333 | 4400 | 272476.3333 | 247280 | 290839.1833 | 263944.8072 | 43560 | 39531.9354 | 262328 | 238070.0997 | 13310 | 12079.2025 | 990 | 898.4531 | 11073.3333 | 10049.364 | 880 | 798.625 | 21800 | 19784.1183 | 353941.3333 | 321211.7979 | 300802.7208 | 272987 | 150419.5417 | 136510 | 36266.1636 | 32912.572 | 28630.0386 | 25982.572 | 337068.8844 | 305899.572 | 179049.5803 | 162492.572 | 500.1386 | 453.89 | 9900 | 8984.5308 | 10400.1386 | 9438.4208 | 0 | 0 | 2070560.4156 | 1879092.2988 | 469888.7636 | 426437.3792 | 1101893.9394 | 3282477.8935 | 3172454.355 | 3752366.6571
444-15R | oh | 2 | 8.3812 | 6.9496 | 6.9193 | 8.3509 | 11.5486 | 22421.3 | 2684.8811 | 42955 | 5143.728 | 37867.5 | 4534.5157 | 83148.2143 | 9956.7408 | 186392.0143 | 22319.8656 | 1694000 | 202851.2462 | 3097607.5625 | 370928.8987 | 1059672.8267 | 126892.5345 | 4157280.3892 | 497821.4332 | 5851280.3892 | 700672.6794 | 1800000 | 215544.4175 | 7837672.4035 | 938536.9626 | 75612.9 | 9054.4103 | 9424.8 | 1128.5906 | 85037.7 | 10183.0008 | 2028278 | 242880 | 36744.1667 | 4400 | 2065022.1667 | 247280 | 2150059.8667 | 257463.0008 | 14850 | 1778.2414 | 89430 | 10708.9651 | 4537.5 | 543.3516 | 11880 | 1422.5932 | 132880 | 15911.9679 | 10560 | 1264.5272 | 261600 | 31325.7887 | 525737.5 | 62955.4351 | 1888883.9125 | 226187.9903 | 944556.125 | 113107.6665 | 114746.9005 | 13740.5855 | 51272.8051 | 6139.7594 | 2003630.813 | 239928.5758 | 995828.9301 | 119247.4259 | 3790.4113 | 453.89 | 9900 | 1185.4943 | 13690.4113 | 1639.3843 | 0 | 0 | 10380731.1278 | 1243060.3578 | 3145888.7967 | 376710.4268 | 8350946.9697 | 23097274.8185 | 18731678.0975 | 26243163.6152
444-43R | oh | 2 | 23.9824 | 23.9824 | 20.6062 | 20.6062 | 28.977 | 72971.14 | 3541.214 | 139799 | 6784.3009 | 53762.5 | 2609.0385 | 350200.7143 | 16994.8785 | 616733.3543 | 29929.4318 | 5513200 | 267549.8938 | 10081304.6125 | 489235.286 | 3448753.3813 | 167364.4346 | 13530057.9938 | 656599.7207 | 19043257.9938 | 924149.6145 | 2600000 | 126175.3109 | 22259991.3481 | 1080254.3572 | 246085.62 | 11942.2806 | 59494.05 | 2887.1847 | 305579.67 | 14829.4653 | 5004846 | 242880 | 90667.5 | 4400 | 5095513.5 | 247280 | 5401093.17 | 262109.4653 | 141570 | 6870.2457 | 852566 | 41374.1462 | 43257.5 | 2099.2417 | 64845 | 3146.8608 | 725303.3333 | 35198.2206 | 57640 | 2797.2096 | 1427900 | 69294.5102 | 3313081.8333 | 160780.4347 | 5625238.3687 | 272987 | 2812959.1875 | 136510 | 341619.0465 | 16578.419 | 152673.4166 | 7409.083 | 5966857.4153 | 289565.419 | 2965632.6041 | 143919.083 | 9352.9708 | 453.89 | 9900 | 480.4368 | 19252.9708 | 934.3268 | 0 | 0 | 31559183.5675 | 1531534.5377 | 8366725.7741 | 406028.5483 | 20606250 | 57954030.774 | 52165433.5675 | 66320756.548
444-9R | oh | 2 | 15.1881 | 15.1881 | 14.6246 | 14.6246 | 20.8917 | 74194.12 | 5073.2336 | 142142 | 9719.3628 | 124822.5 | 8535.0929 | 356070 | 24347.2973 | 697228.62 | 47674.9866 | 5605600 | 383298.8163 | 10250265.025 | 700890.9753 | 3506553.7173 | 239770.5668 | 13756818.7423 | 940661.5421 | 19362418.7423 | 1323960.3585 | 7675000 | 524799.9171 | 27734647.3623 | 1896435.2622 | 250209.96 | 17108.8165 | 41822.55 | 2859.7356 | 292032.51 | 19968.5521 | 3552028 | 242880 | 64348.3333 | 4400 | 3616376.3333 | 247280 | 3908408.8433 | 267248.5521 | 558360 | 38179.4504 | 3362568 | 229925.1346 | 170610 | 11665.9432 | 70290 | 4806.2783 | 786206.6667 | 53759.1132 | 62480 | 4272.2474 | 1547800 | 105835.2198 | 6558314.6667 | 448443.3868 | 3992331.4708 | 272987 | 1996407.0417 | 136510 | 242352.2322 | 16571.522 | 108335.4062 | 7407.741 | 4234683.703 | 289558.522 | 2104742.4478 | 143917.741 | 6637.9693 | 453.89 | 9900 | 676.9406 | 16537.9693 | 1130.8306 | 0 | 0 | 38544183.7013 | 2635568.0015 | 6013151.2912 | 411166.2931 | 14624621.2121 | 41783319.0105 | 53168804.9134 | 47796470.3016
445-1311R | oh | 3 | 14.1299 | 14.1299 | 13.2994 | 13.2994 | 9.6439 | 56460.91 | 4245.3626 | 108168.5 | 8133.3174 | 82747.5 | 6221.8823 | 270965.3571 | 20374.2055 | 518342.2671 | 38974.7678 | 4265800 | 320750.5447 | 7800339.0438 | 586516.7137 | 2668448.8453 | 200643.8231 | 10468787.8891 | 787160.5368 | 14734587.8891 | 1107911.0815 | 4125000 | 310163.6263 | 19377930.1562 | 1457049.4756 | 190407.03 | 14316.9297 | 47124 | 3543.3093 | 237531.03 | 17860.2389 | 3230166 | 242880 | 58517.5 | 4400 | 3288683.5 | 247280 | 3526214.53 | 265140.2389 | 350460 | 26351.5017 | 2110548 | 158694.5991 | 107085 | 8051.8477 | 52470 | 3945.2813 | 586886.6667 | 44128.7022 | 46640 | 3506.9167 | 1155400 | 86875.8918 | 4409489.6667 | 331554.7406 | 3630571.9937 | 272987 | 1815505.4375 | 136510 | 374951.6127 | 28193.055 | 125744.0132 | 9454.841 | 4005523.6065 | 301180.055 | 1941249.4507 | 145964.841 | 6036.4791 | 453.89 | 9900 | 744.3927 | 15936.4791 | 1198.2827 | 0 | 0 | 27808879.9085 | 2090982.5539 | 5467463.9807 | 411105.0799 | 13299431.8182 | 19287758.9856 | 41108311.7267 | 24755222.9664
445-1325F | oh | 2 | 18.6034 | 18.6034 | 11.7129 | 11.7129 | 13.0993 | 40154.51 | 3428.2358 | 76928.5 | 6567.8559 | 24310 | 2075.4932 | 192708.2143 | 16452.6772 | 334101.2243 | 28524.2621 | 3033800 | 259014.0353 | 5547533.5438 | 473626.8209 | 1897777.6987 | 162024.8731 | 7445311.2424 | 635651.6939 | 10479111.2424 | 894665.7293 | 1125000 | 96048.1211 | 11938212.4667 | 1019238.1124 | 135415.83 | 11561.2765 | 41822.55 | 3570.6465 | 177238.38 | 15131.923 | 2844824 | 242880 | 51536.6667 | 4400 | 2896360.6667 | 247280 | 3073599.0467 | 262411.923 | 208890 | 17834.2151 | 1257982 | 107401.6066 | 63827.5 | 5449.3435 | 28215 | 2408.8869 | 315590 | 26943.8458 | 25080 | 2141.2328 | 621300 | 53044.1757 | 2520884.5 | 215223.3064 | 3197463.6417 | 272987 | 1598925.0833 | 136510 | 350300.3924 | 29907.284 | 114275.472 | 9756.395 | 3547764.034 | 302894.284 | 1713200.5554 | 146266.395 | 5316.3586 | 453.89 | 9900 | 845.2235 | 15216.3586 | 1299.1135 | 0 | 0 | 18022077.3593 | 1538654.8163 | 4786799.602 | 408678.318 | 11712878.7879 | 26198622.7513 | 29734956.1472 | 30985422.3534
445-17R | oh | 2 | 5.7004 | 5.7004 | 3.4055 | 3.4055 | 4.6934 | 15083.42 | 4429.1451 | 28897 | 8485.4102 | 9350 | 2745.5648 | 72387.8571 | 21256.2085 | 125718.2771 | 36916.3285 | 1139600 | 334635.8934 | 2083845.0875 | 611907.1276 | 712870.8107 | 209329.7303 | 2796715.8982 | 821236.8579 | 3936315.8982 | 1155872.7514 | 475000 | 139480.5628 | 4537034.1753 | 1332269.6427 | 50866.86 | 14936.7121 | 20616.75 | 6053.9703 | 71483.61 | 20990.6824 | 827126 | 242880 | 14984.1667 | 4400 | 842110.1667 | 247280 | 913593.7767 | 268270.6824 | 105930 | 31105.6337 | 637934 | 187325.0387 | 32367.5 | 9504.4992 | 16830 | 4942.0166 | 188246.6667 | 55277.3706 | 14960 | 4392.9036 | 370600 | 108824.2033 | 1366868.1667 | 401371.6656 | 929655.1604 | 272987 | 464883.7708 | 136510 | 102318.1084 | 30045.026 | 33310.2146 | 9781.321 | 1031973.2688 | 303032.026 | 498193.9854 | 146291.321 | 1545.719 | 453.89 | 9900 | 2907.0686 | 11445.719 | 3360.9586 | 0 | 0 | 6947321.3298 | 2040034.2929 | 1411787.7621 | 414562.0034 | 3405492.4242 | 9386801.869 | 10352813.754 | 10798589.631
445-18R | oh | 2 | 27.4678 | 27.4678 | 24.8581 | 24.8581 | 10.783 | 89685.2 | 3607.88 | 171820 | 6912.0205 | 142120 | 5717.241 | 430414.2857 | 17314.8199 | 834039.4857 | 33551.9614 | 6776000 | 272586.7231 | 12390430.25 | 498445.5107 | 4238691.3067 | 170515.1968 | 16629121.5567 | 668960.7075 | 23405121.5567 | 941547.4306 | 7425000 | 298694.8671 | 31664161.0424 | 1273794.2591 | 302451.6 | 12167.1031 | 76576.5 | 3080.5397 | 379028.1 | 15247.6428 | 6037546 | 242880 | 109375.8333 | 4400 | 6146921.8333 | 247280 | 6525949.9333 | 262527.6428 | 458370 | 18439.4298 | 2760406 | 111046.3439 | 140057.5 | 5634.2702 | 76725 | 3086.5136 | 858183.3333 | 34523.2265 | 68200 | 2743.5677 | 1689500 | 67965.6536 | 6051441.8333 | 243439.0053 | 6785950.1396 | 272987 | 3393385.2292 | 136510 | 717690.3118 | 28871.436 | 237988.1414 | 9573.85 | 7503640.4514 | 301858.436 | 3631373.3705 | 146083.85 | 11282.863 | 453.89 | 9900 | 398.2598 | 21182.863 | 852.1498 | 0 | 0 | 45240426.1901 | 1819943.8502 | 10157323.3039 | 408611.4928 | 24858143.9394 | 21566049.4217 | 70098570.1295 | 31723372.7256
445-19R | oh | 2 | 13.5214 | 13.5214 | 11.3089 | 11.3089 | 15.4111 | 45046.43 | 3983.2719 | 86300.5 | 7631.201 | 13557.5 | 1198.8344 | 216185.3571 | 19116.3887 | 361089.7871 | 31929.696 | 3403400 | 300948.7699 | 6223375.1937 | 550307.6656 | 2128979.0427 | 188256.9266 | 8352354.2364 | 738564.5923 | 11755754.2364 | 1039513.3622 | 550000 | 48634.255 | 12666844.0236 | 1120077.3131 | 151913.19 | 13433.0633 | 41233.5 | 3646.1101 | 193146.69 | 17079.1734 | 2746706 | 242880 | 49759.1667 | 4400 | 2796465.1667 | 247280 | 2989611.8567 | 264359.1734 | 189090 | 16720.4569 | 1138742 | 100694.3069 | 57777.5 | 5109.0285 | 38610 | 3414.1247 | 431860 | 38187.617 | 34320 | 3034.7775 | 850200 | 75179.7156 | 2740599.5 | 242340.0271 | 3087183.0979 | 272987 | 1543778.1458 | 136510 | 337955.4277 | 29884.019 | 110283.8534 | 9751.951 | 3425138.5257 | 302871.019 | 1654061.9993 | 146261.951 | 5132.9973 | 453.89 | 9900 | 875.4166 | 15032.9973 | 1329.3066 | 0 | 0 | 18847615.0465 | 1666617.6659 | 4643673.8559 | 410621.1244 | 11308901.5152 | 30822250.4072 | 30156516.5617 | 35465924.2631
445-39R | oh | 2 | 18.4023 | 18.4023 | 8.4979 | 8.4979 | 12.2598 | 40766 | 4797.1758 | 78100 | 9190.4879 | 26180 | 3080.7551 | 195642.8571 | 23022.4495 | 340688.8571 | 40090.8682 | 3080000 | 362441.7749 | 5632013.75 | 662752.2922 | 1926677.8667 | 226723.5538 | 7558691.6167 | 889475.846 | 10638691.6167 | 1251917.621 | 800000 | 94140.7208 | 11779380.4738 | 1386149.21 | 137478 | 16177.8475 | 64206.45 | 7555.5519 | 201684.45 | 23733.3994 | 2063974 | 242880 | 37390.8333 | 4400 | 2101364.8333 | 247280 | 2303049.2833 | 271013.3994 | 218790 | 25746.3104 | 1317602 | 155050.0025 | 66852.5 | 7866.9282 | 46530 | 5475.4597 | 520446.6667 | 61244.0304 | 41360 | 4867.0753 | 1024600 | 120570.7281 | 3236181.1667 | 380820.5344 | 2319820.7771 | 272987 | 1160050.6042 | 136510 | 236129.6559 | 27786.77 | 79719.4066 | 9381.053 | 2555950.433 | 300773.77 | 1239770.0108 | 145891.053 | 3857.1194 | 453.89 | 9900 | 1164.9914 | 13757.1194 | 1618.8814 | 0 | 0 | 17585269.1929 | 2069362.3958 | 3542819.2941 | 416904.4524 | 8497916.6667 | 24519532.1621 | 26083185.8595 | 28062351.4562
445-894R | oh | 2 | 27.3138 | 27.3138 | 26.8623 | 26.8623 | 36.1897 | 104157.13 | 3877.4449 | 199545.5 | 7428.4563 | 28050 | 1044.214 | 499867.5 | 18608.5072 | 831620.13 | 30958.6224 | 7869400 | 292953.2055 | 14389795.1312 | 535687.1694 | 4922661.9493 | 183255.3432 | 19312457.0806 | 718942.5126 | 27181857.0806 | 1011895.7181 | 1175000 | 43741.5834 | 29188477.2106 | 1086595.9239 | 351256.29 | 13076.1756 | 86001.3 | 3201.56 | 437257.59 | 16277.7356 | 6524318 | 242880 | 118194.1667 | 4400 | 6642512.1667 | 247280 | 7079769.7567 | 263557.7356 | 353430 | 13157.096 | 2128434 | 79234.956 | 107992.5 | 4020.2238 | 89100 | 3316.915 | 996600 | 37100.3081 | 79200 | 2948.3689 | 1962000 | 73039.1376 | 5716756.5 | 212817.0054 | 7333061.5854 | 272987 | 3666974.0208 | 136510 | 794402.4962 | 29573.126 | 260453.2566 | 9695.862 | 8127464.0816 | 302560.126 | 3927427.2775 | 146205.862 | 12192.5342 | 453.89 | 9900 | 368.5461 | 22092.5342 | 822.4361 | 0 | 0 | 43054790.3264 | 1602795.4913 | 11007197.0341 | 409763.5976 | 26862310.6061 | 72379410.5968 | 69917100.9324 | 83386607.6309
445-897R | oh | 2 | 1.4839 | 1.4839 | 1.0659 | 1.0659 | 1.6056 | 4688.09 | 4398.2081 | 8981.5 | 8426.1407 | 2805 | 2631.5565 | 22498.9286 | 21107.7368 | 38973.5186 | 36563.6422 | 354200 | 332298.5075 | 647681.5813 | 607633.04 | 221567.9547 | 207867.5907 | 869249.5359 | 815500.6307 | 1223449.5359 | 1147799.1382 | 125000 | 117270.7889 | 1387423.0545 | 1301633.5692 | 15809.97 | 14832.3812 | 4712.4 | 4421.0149 | 20522.37 | 19253.3962 | 258888 | 242880 | 4690 | 4400 | 263578 | 247280 | 284100.37 | 266533.3962 | 28710 | 26934.7548 | 172898 | 162207.0789 | 8772.5 | 8230.064 | 3960 | 3715.1386 | 44293.3333 | 41554.5131 | 3520 | 3302.3454 | 87200 | 81808.1023 | 349353.8333 | 327751.9972 | 290979.325 | 272987 | 145507.25 | 136510 | 39592.5344 | 37144.382 | 11755.2153 | 11028.347 | 330571.8594 | 310131.382 | 157262.4653 | 147538.347 | 483.8055 | 453.89 | 9900 | 9287.8465 | 10383.8055 | 9741.7365 | 0 | 0 | 2077732.5527 | 1949258.6849 | 441362.8353 | 414071.7432 | 1065909.0909 | 3211148.8232 | 3143641.6437 | 3652511.6586
448-1234R | oh | 3 | 2.9873 | 2.9873 | 2.9873 | 2.9873 | 3.745 | 9376.18 | 3138.6693 | 17963 | 6013.1009 |  |  | 44997.8571 | 15062.9992 | 72337.0371 | 24214.7693 | 708400 | 237136.3723 | 1295363.1625 | 433621.8537 | 443135.9093 | 148339.4155 | 1738499.0718 | 581961.2692 | 2446899.0718 | 819097.6415 | 0 | 0 | 2519236.109 | 843312.4108 | 31619.94 | 10584.7514 | 5301.45 | 1774.6564 | 36921.39 | 12359.4078 | 725558 | 242880 | 13144.1667 | 4400 | 738702.1667 | 247280 | 775623.5567 | 259639.4078 | 30690 | 10273.4546 | 184822 | 61869.0268 | 9377.5 | 3139.1111 | 8415 | 2816.915 | 94123.3333 | 31507.7157 | 7480 | 2503.9244 | 185300 | 62029.037 | 520207.8333 | 174139.1847 | 815496.9604 | 272987 | 407797.7708 | 136510 | 141228.5831 | 47276.163 | 120526.5206 | 40346.163 | 956725.5436 | 320263.163 | 528324.2915 | 176856.163 | 1355.9104 | 453.89 | 9900 | 3314.0176 | 11255.9104 | 3767.9076 | 0 | 0 | 4007425.3963 | 1341482.6661 | 1303947.8481 | 436495.5708 | 2987310.6061 | 7490012.7091 | 6994736.0023 | 8793960.5573
448-47R | oh | 3 | 8.8741 | 8.8741 | 8.3023 | 8.3023 | 12.0173 | 31593.65 | 3805.4218 | 60527.5 | 7290.4736 |  |  | 151623.2143 | 18262.8564 | 243744.3643 | 29358.7518 | 2387000 | 287511.6343 | 4364810.6562 | 525736.8433 | 1493175.3467 | 179851.3968 | 5857986.0029 | 705588.2402 | 8244986.0029 | 993099.8744 | 0 | 0 | 8488730.3672 | 1022458.6262 | 106545.45 | 12833.2872 | 25329.15 | 3050.8694 | 131874.6 | 15884.1566 | 2016456 | 242880 | 36530 | 4400 | 2052986 | 247280 | 2184860.6 | 263164.1566 | 124740 | 15024.8015 | 751212 | 90482.6937 | 38115 | 4590.9116 | 33165 | 3994.6893 | 370956.6667 | 44681.3395 | 29480 | 3550.8349 | 730300 | 87963.8653 | 2077968.6667 | 250289.1359 | 2266412.525 | 272987 | 1133343.25 | 136510 | 385209.2153 | 46398.044 | 327674.4653 | 39468.044 | 2651621.7403 | 319385.044 | 1461017.7153 | 175978.044 | 3768.3186 | 453.89 | 9900 | 1192.4446 | 13668.3186 | 1646.3346 | 0 | 0 | 13231989.0927 | 1593779.1407 | 3645878.3153 | 439142.2006 | 8302272.7273 | 24034564.367 | 21534261.82 | 27680442.6823
448-714R | oh | 3 | 13.3053 | 12.8822 | 9.7888 | 10.2119 | 13.3746 | 43619.62 | 4271.4367 | 83567 | 8183.2705 | 10285 | 1007.1552 | 202490.3571 | 19828.8003 | 339961.9771 | 33290.6626 | 3295600 | 322720.5252 | 6026254.7125 | 590118.9726 | 2061545.3173 | 201876.1341 | 8087800.0298 | 791995.1067 | 11383400.0298 | 1114715.6319 | 525000 | 51410.449 | 12248362.007 | 1199416.7436 | 147101.46 | 14404.8612 | 58315.95 | 5710.5699 | 205417.41 | 20115.431 | 2480274 | 242880 | 44932.5 | 4400 | 2525206.5 | 247280 | 2730623.91 | 267395.431 | 212850 | 20843.2649 | 1281830 | 125522.773 | 65037.5 | 6368.7754 | 54945 | 5380.4707 | 614570 | 60181.5612 | 48840 | 4782.6406 | 1209900 | 118479.0519 | 3487972.5 | 341558.5378 | 2672222.1771 | 261676.4609 | 1336272.6042 | 130854.0468 | 263766.1064 | 25829.2075 | 90383.39 | 8850.7632 | 2935988.2834 | 287505.6684 | 1426655.9942 | 139704.81 | 4635.0937 | 453.89 | 9900 | 969.4542 | 14535.0937 | 1423.3442 | 0 | 0 | 18686857.8842 | 1829904.294 | 4157279.9042 | 407100.241 | 10211931.8182 | 26749137.6862 | 28898789.7023 | 30906417.5904
448-724R | oh | 3 | 7.9845 | 7.9845 | 7.9845 | 7.9845 | 11.8572 | 30982.16 | 3880.3028 | 59356 | 7433.9314 | 1402.5 | 175.6535 | 148688.5714 | 18622.2225 | 240429.2314 | 30112.1102 | 2340800 | 293169.1257 | 4280330.45 | 536081.9957 | 1464275.1787 | 183390.4109 | 5744605.6287 | 719472.4066 | 8085405.6287 | 1012641.5323 | 50000 | 6262.1566 | 8375834.8601 | 1049015.7992 | 104483.28 | 13085.8133 | 22972.95 | 2877.2042 | 127456.23 | 15963.0176 | 1939268 | 242880 | 35131.6667 | 4400 | 1974399.6667 | 247280 | 2101855.8967 | 263243.0176 | 242550 | 30377.7219 | 1460690 | 182941.3919 | 74112.5 | 9282.0817 | 31680 | 3967.7025 | 354346.6667 | 44379.4867 | 28160 | 3526.8466 | 697600 | 87369.6096 | 2889139.1667 | 361844.8408 | 2179656.4292 | 272987 | 1089959.9583 | 136510 | 240168.6806 | 30079.478 | 78114.646 | 9783.323 | 2419825.1098 | 303066.478 | 1168074.6044 | 146293.323 | 3624.071 | 453.89 | 9900 | 1239.907 | 13524.071 | 1693.797 | 0 | 0 | 13698323.2075 | 1715620.915 | 3269930.501 | 409536.3406 | 7984469.697 | 23714441.0517 | 21682792.9044 | 26984371.5528
448-735R | oh | 3 | 7.6566 | 7.5566 | 7.5566 | 7.6566 | 11.2809 | 28943.86 | 3780.2355 | 55451 | 7242.2213 |  |  | 137928.2143 | 18014.2225 | 222323.0743 | 29036.6793 | 2186800 | 285608.7268 | 3998729.7625 | 522257.2327 | 1367941.2853 | 178661.043 | 5366671.0478 | 700918.2757 | 7553471.0478 | 986527.0026 | 0 | 0 | 7775794.1221 | 1015563.6818 | 97609.38 | 12748.3495 | 20027.7 | 2615.7334 | 117637.08 | 15364.083 | 1859642 | 242880 | 33689.1667 | 4400 | 1893331.1667 | 247280 | 2010968.2467 | 262644.083 | 189090 | 24696.2476 | 1138742 | 148726.2908 | 57777.5 | 7546.0756 | 32670 | 4266.8909 | 365420 | 47725.9653 | 29040 | 3792.7919 | 719400 | 93957.8005 | 2532139.5 | 330712.0627 | 2062861.4229 | 269421.6319 | 1031555.3958 | 134727.1005 | 317950.393 | 41526.1601 | 265582.9555 | 34686.6699 | 2380811.8159 | 310947.792 | 1297138.3513 | 169413.7704 | 3475.2672 | 453.89 | 9900 | 1292.9973 | 13375.2672 | 1746.8873 | 0 | 0 | 12702120.7053 | 1658970.4238 | 3308106.598 | 432057.8534 | 7656628.7879 | 22561731.2387 | 20358749.4931 | 25869837.8367
448-744R | oh | 3 | 26.8485 | 26.8485 | 25.9697 | 25.9697 | 30.4552 | 100692.02 | 3877.289 | 192907 | 7428.1575 | 33192.5 | 1278.1243 | 483237.8571 | 18607.7588 | 810029.3771 | 31191.3296 | 7607600 | 292941.4236 | 13911073.9625 | 535665.6252 | 4758894.3307 | 183247.9731 | 18669968.2932 | 718913.5982 | 26277568.2932 | 1011855.0218 | 1400000 | 53908.9848 | 28487597.6703 | 1096955.3362 | 339570.66 | 13075.6497 | 126056.7 | 4853.9919 | 465627.36 | 17929.6416 | 6307520 | 242880 | 114266.6667 | 4400 | 6421786.6667 | 247280 | 6887414.0267 | 265209.6416 | 586080 | 22567.8413 | 3529504 | 135908.5554 | 179080 | 6895.7293 | 121275 | 4669.8658 | 1356483.3333 | 52233.3139 | 107800 | 4150.9918 | 2670500 | 102831.3886 | 8550722.3333 | 329257.6861 | 7089389.6667 | 272987 | 3545123.3333 | 136510 | 666732.8593 | 25673.494 | 233982.425 | 9009.825 | 7756122.526 | 298660.494 | 3779105.7583 | 145519.825 | 11787.3858 | 453.89 | 9900 | 381.2135 | 21687.3858 | 835.1035 | 0 | 0 | 44816129.9154 | 1725708.6198 | 10666519.785 | 410729.4666 | 25969696.9697 | 60910408.8212 | 70785826.8851 | 71576928.6062
448-9R | oh | 3 | 16.9231 | 16.9231 | 16.4426 | 16.4426 | 18.1535 | 61964.32 | 3768.5201 | 118712 | 7219.7768 | 15895 | 966.6955 | 297377.1429 | 18085.7587 | 493948.4629 | 30040.751 | 4681600 | 284723.591 | 8560660.9 | 520638.6946 | 2928550.3573 | 178107.3509 | 11489211.2573 | 698746.0456 | 16170811.2573 | 983469.6366 | 825000 | 50174.505 | 17489759.7202 | 1063684.8926 | 208966.56 | 12708.8409 | 54781.65 | 3331.6875 | 263748.21 | 16040.5283 | 3993582 | 242880 | 72347.5 | 4400 | 4065929.5 | 247280 | 4329677.71 | 263320.5283 | 282150 | 17159.6807 | 1699170 | 103339.4105 | 86212.5 | 5243.2358 | 63855 | 3883.5067 | 714230 | 43437.7415 | 56760 | 3452.0059 | 1406100 | 85515.6018 | 4308477.5 | 262031.1828 | 4488619.7687 | 272987 | 2244581.1875 | 136510 | 470857.4256 | 28636.41 | 156739.7735 | 9532.534 | 4959477.1943 | 301623.41 | 2401320.961 | 146042.534 | 7463.1379 | 453.89 | 9900 | 602.0941 | 17363.1379 | 1055.9841 | 0 | 0 | 26775077.5524 | 1628395.4695 | 6730998.671 | 409363.0623 | 16442613.6364 | 36306985.8146 | 43217691.1888 | 43037984.4857
449-13R | oh | 3 | 17.7888 | 17.7888 | 16.5477 | 16.5477 | 6.8069 | 85404.77 | 5161.1178 | 163619.5 | 9887.7325 | 167832.5 | 10142.3294 | 409871.7857 | 24769.0682 | 826728.5557 | 49960.2478 | 6452600 | 389938.7447 | 11799068.8063 | 713032.5882 | 4036390.1307 | 243924.1392 | 15835458.9369 | 956956.7274 | 22288058.9369 | 1346895.4721 | 9675000 | 584672.4351 | 32789787.4926 | 1981528.155 | 288016.41 | 17405.1944 | 92480.85 | 5588.7342 | 380497.26 | 22993.9286 | 4019112 | 242880 | 72810 | 4400 | 4091922 | 247280 | 4472419.26 | 270273.9286 | 990990 | 59886.7738 | 5967962 | 360651.46 | 302802.5 | 18298.7364 | 110880 | 6700.618 | 1240213.3333 | 74947.6537 | 98560 | 5956.1049 | 2441600 | 147548.9631 | 11153007.8333 | 673990.3099 | 4517314.425 | 272987 | 2258930.25 | 136510 | 341737.3755 | 20651.62 | 134456.9528 | 8125.403 | 4859051.8005 | 293638.62 | 2393387.2028 | 144635.403 | 7510.8479 | 453.89 | 9900 | 598.2695 | 17410.8479 | 1052.1595 | 0 | 0 | 48819257.9744 | 2950209.2444 | 6865806.4628 | 414909.3316 | 16547727.2727 | 13613874.3718 | 65366985.2471 | 20479680.8346
449-16R | oh | 3 | 2.5212 | 2.5212 | 2.4038 | 2.4038 | 0.56936 | 11414.48 | 4748.5388 | 21868 | 9097.3085 | 14025 | 5834.5414 | 54780 | 22789.0325 | 102087.48 | 42469.4212 | 862400 | 358767.0974 | 1576963.85 | 656032.8654 | 539469.8027 | 224424.8785 | 2116433.6527 | 880457.7439 | 2978833.6527 | 1239224.8413 | 575000 | 239205.7989 | 3655921.1327 | 1520900.0615 | 38493.84 | 16013.8257 | 12370.05 | 5146.0656 | 50863.89 | 21159.8912 | 583832 | 242880 | 10576.6667 | 4400 | 594408.6667 | 247280 | 645272.5567 | 268439.8912 | 60390 | 25122.849 | 363682 | 151295.3798 | 18452.5 | 7676.4261 | 13860 | 5765.8998 | 155026.6667 | 64492.6568 | 12320 | 5125.2442 | 305200 | 126966.278 | 928931.1667 | 386444.7337 | 656202.8417 | 272987 | 328141.0833 | 136510 | 50465.4016 | 20994.116 | 19674.2923 | 8184.704 | 706668.2432 | 293981.116 | 347815.3756 | 144694.704 | 1091.0553 | 453.89 | 9900 | 4118.4998 | 10991.0553 | 4572.3898 | 0 | 0 | 5302511.5978 | 2205898.301 | 993087.9323 | 413134.5952 | 2403787.8788 | 1138717.0455 | 7706299.4766 | 2131804.9777
449-683 | oh | 3 | 1.6021 | 1.6021 | 1.6021 | 1.6021 | 1.7856 | 5503.41 | 3435.1584 | 10543.5 | 6581.1183 | 5610 | 3501.6905 | 26411.7857 | 16485.9001 | 48068.6957 | 30003.8673 | 415800 | 259537.0611 | 760321.8562 | 474583.2133 | 260101.512 | 162352.0491 | 1020423.3683 | 636935.2624 | 1436223.3683 | 896472.3235 | 275000 | 171651.4954 | 1759292.064 | 1098127.6862 | 18559.53 | 11584.6221 | 3534.3 | 2206.065 | 22093.83 | 13790.6871 | 389114 | 242880 | 7049.1667 | 4400 | 396163.1667 | 247280 | 418256.9967 | 261070.6871 | 36630 | 22863.9792 | 220594 | 137691.9636 | 11192.5 | 6986.2159 | 3960 | 2471.7815 | 44293.3333 | 27647.3342 | 3520 | 2197.1391 | 87200 | 54429.1287 | 407389.8333 | 254287.5423 | 437347.9229 | 272987 | 218700.3958 | 136510 | 39182.1232 | 24456.982 | 14087.8653 | 8793.466 | 476530.0462 | 297443.982 | 232788.2612 | 145303.466 | 727.1696 | 453.89 | 9900 | 6179.4538 | 10627.1696 | 6633.3438 | 0 | 0 | 2653839.1131 | 1656492.5543 | 651045.2578 | 406374.1531 | 1602083.3333 | 3571297.6331 | 4255922.4464 | 4222342.8909
449-693R | oh | 3 | 8.5108 | 8.5108 | 8.4553 | 8.4553 | 1.2514 | 26905.56 | 3182.0929 | 51546 | 6096.2924 | 30855 | 3649.1891 | 129124.2857 | 15271.3966 | 238430.8457 | 28198.9711 | 2032800 | 240417.1669 | 3717129.075 | 439621.0357 | 1271607.392 | 150391.6994 | 4988736.467 | 590012.7351 | 7021536.467 | 830429.902 | 1775000 | 209927.4259 | 9034967.3127 | 1068556.299 | 90735.48 | 10731.192 | 18849.6 | 2229.3228 | 109585.08 | 12960.5148 | 2053624 | 242880 | 37203.3333 | 4400 | 2090827.3333 | 247280 | 2200412.4133 | 260240.5148 | 197010 | 23300.1702 | 1186438 | 140318.803 | 60197.5 | 7119.4965 | 25740 | 3044.2433 | 287906.6667 | 34050.4256 | 22880 | 2705.9941 | 566800 | 67034.8535 | 2346972.1667 | 277573.9862 | 2308187.8083 | 272987 | 1154233.4167 | 136510 | 177448.367 | 20986.636 | 69193.7356 | 8183.472 | 2485636.1753 | 293973.636 | 1223427.1523 | 144693.472 | 3837.7775 | 453.89 | 9900 | 1170.8628 | 13737.7775 | 1624.7528 | 0 | 0 | 13881313.4322 | 1641728.674 | 3423839.5656 | 404933.9868 | 8455303.0303 | 2502738.6364 | 22336616.4625 | 5926578.202
449-6R | oh | 3 | 5.4714 | 5.4714 | 5.3305 | 5.3305 | 1.9218 | 25274.92 | 4741.5732 | 48422 | 9083.9638 | 40205 | 7542.4551 | 121298.5714 | 22755.6034 | 235200.4914 | 44123.5955 | 1909600 | 358240.8243 | 3491848.525 | 655070.5352 | 1194540.2773 | 224095.6711 | 4686388.8023 | 879166.2063 | 6595988.8023 | 1237407.0306 | 2100000 | 393959.8508 | 8931189.2938 | 1675490.4769 | 85236.36 | 15990.3351 | 27096.3 | 5083.264 | 112332.66 | 21073.599 | 1294670 | 242880 | 23454.1667 | 4400 | 1318124.1667 | 247280 | 1430456.8267 | 268353.599 | 262350 | 49216.8414 | 1579930 | 296394.7557 | 80162.5 | 15038.4793 | 33165 | 6221.7516 | 370956.6667 | 69591.4443 | 29480 | 5530.4459 | 730300 | 137004.2281 | 3086344.1667 | 578997.9463 | 1455155.1354 | 272987 | 727665.5208 | 136510 | 111712.0786 | 20957.178 | 43595.3737 | 8178.489 | 1566867.214 | 293944.178 | 771260.8945 | 144688.489 | 2419.4572 | 453.89 | 9900 | 1857.2393 | 12319.4572 | 2311.1293 | 0 | 0 | 13596720.1316 | 2550743.7305 | 2201717.7212 | 413042.088 | 5330492.4242 | 3843532.9545 | 18927212.5559 | 6045250.6757
450-1851F | oh | 2 | 6.4822 | 6.4822 | 5.91 | 5.91 | 7.7705 | 25682.58 | 4345.5864 | 49203 | 8325.3274 | 49087.5 | 8305.7843 | 123255 | 20855.1963 | 247228.08 | 41831.8943 | 1940400 | 328322.7688 | 3548168.6625 | 600363.1001 | 1213807.056 | 205380.5882 | 4761975.7185 | 805743.6883 | 6702375.7185 | 1134066.4571 | 2300000 | 389168.4025 | 9249603.7985 | 1565066.7539 | 86611.14 | 14654.9213 | 35343 | 5980.1647 | 121954.14 | 20635.086 | 1435430 | 242880 | 26004.1667 | 4400 | 1461434.1667 | 247280 | 1583388.3067 | 267915.086 | 509850 | 86268.4826 | 3070430 | 519527.9731 | 155787.5 | 26359.8141 | 17820 | 3015.2091 | 199320 | 33725.6722 | 15840 | 2680.1859 | 392400 | 66395.5135 | 4361447.5 | 737972.8505 | 1613363.5104 | 272987 | 806779.2708 | 136510 | 95039.1182 | 16080.966 | 43271.6484 | 7321.721 | 1708402.6286 | 289067.966 | 850050.9193 | 143831.721 | 2682.5071 | 453.89 | 9900 | 1675.1162 | 12582.5071 | 2129.0062 | 0 | 0 | 15332036.4342 | 2594236.5766 | 2433439.2259 | 411746.807 | 5910037.8788 | 15541088.9959 | 21242074.313 | 17974528.2219
450-1854 | oh | 2 | 1.6924 | 1.6924 | 1.4413 | 1.4413 | 1.5394 | 8357.03 | 5798.3073 | 16010.5 | 11108.4678 | 18232.5 | 12650.1445 | 40106.7857 | 27827.0471 | 82706.8157 | 57383.9668 | 631400 | 438080.4205 | 1154562.8188 | 801063.2961 | 394968.9627 | 274038.9123 | 1549531.7814 | 1075102.2084 | 2180931.7814 | 1513182.6289 | 875000 | 607095.9264 | 3138638.5971 | 2177662.5221 | 28182.99 | 19554.0325 | 12959.1 | 8991.3335 | 41142.09 | 28545.366 | 350060 | 242880 | 6341.6667 | 4400 | 356401.6667 | 247280 | 397543.7567 | 275825.366 | 122760 | 85173.8239 | 739288 | 512935.6951 | 37510 | 26025.3351 | 2475 | 1717.2142 | 27683.3333 | 19207.3587 | 2200 | 1526.4126 | 54500 | 37813.4034 | 986416.3333 | 684399.2431 | 393452.8542 | 272987 | 196750.2083 | 136510 | 23173.5598 | 16078.37 | 10551.915 | 7321.171 | 416626.414 | 289065.37 | 207302.1234 | 143831.171 | 654.1862 | 453.89 | 9900 | 6868.8568 | 10554.1862 | 7322.7468 | 0 | 0 | 4552235.5306 | 3158449.8819 | 604845.88 | 419656.537 | 1441287.8788 | 3078872.1554 | 5993523.4094 | 3683718.0354
452-38AE | oh | 2 | 9.5934 | 8.4544 | 2.7653 | 2.7653 | 3.69 | 12229.8 | 4422.5289 | 23430 | 8472.7347 | 15895 | 5747.9351 | 58692.8571 | 21224.4563 | 110247.6571 | 39867.6549 | 924000 | 334136.0181 | 1689604.125 | 610993.0676 | 578003.36 | 209017.0359 | 2267607.485 | 820010.1035 | 3191607.485 | 1154146.1216 | 550000 | 198890.487 | 3851855.1421 | 1392904.2634 | 41243.4 | 14914.3998 | 36521.1 | 13206.7261 | 77764.5 | 28121.126 | 671646 | 242880 | 12167.5 | 4400 | 683813.5 | 247280 | 761578 | 275401.126 | 338580 | 122436.9838 | 2039004 | 737342.7245 | 103455 | 37411.3006 | 3465 | 1253.0101 | 38756.6667 | 14015.1496 | 3080 | 1113.7867 | 76300 | 27591.5348 | 2602640.6667 | 941164.4901 | 754902.1187 | 272987 | 377496.6875 | 136510 |  |  |  |  | 754902.1187 | 272987 | 377496.6875 | 136510 | 1255.1606 | 453.89 | 9900 | 3580.0288 | 11155.1606 | 4033.9188 | 0 | 0 | 7220553.0881 | 2611089.6723 | 1139074.6875 | 411911.126 | 2765340.9091 | 7379993.3109 | 9985893.9972 | 8519067.9984
454-48F | oh | 2 | 3.5366 | 3.0794 | 3.0267 | 3.4244 | 4.7071 | 9987.67 | 2916.5919 | 19134.5 | 5587.6423 | 14492.5 | 4232.0889 | 40106.7857 | 11711.9534 | 83721.4557 | 24448.2764 | 754600 | 220357.7236 | 1379843.3687 | 402940.8211 | 472036.0773 | 137843.6197 | 1851879.4461 | 540784.4409 | 2606479.4461 | 761142.1644 | 625000 | 182512.0292 | 3315200.9018 | 968102.4701 | 33682.11 | 9835.8244 | 7657.65 | 2236.1812 | 41339.76 | 12072.0056 | 831726 | 242880 | 15067.5 | 4400 | 846793.5 | 247280 | 888133.26 | 259352.0056 | 313830 | 91644.4002 | 1889954 | 551902.9434 | 95892.5 | 28002.4556 | 3960 | 1156.3962 | 44293.3333 | 12934.5058 | 3520 | 1027.9077 | 87200 | 25464.0783 | 2438649.8333 | 712132.6874 | 826250.9937 | 241281.1928 | 413175.4375 | 120655.18 | 48722.8395 | 14228.0069 | 22169.1095 | 6473.8067 | 874973.8333 | 255509.1997 | 435344.547 | 127128.9867 | 1554.3154 | 453.89 | 9900 | 2890.9905 | 11454.3154 | 3344.8805 | 0 | 0 | 6640278.8837 | 1939089.2377 | 1323477.807 | 386480.9923 | 3424431.8182 | 9414223.0775 | 10064710.7019 | 10737700.8846
463-1229 | oh | 2 | 12.5159 | 12.3388 | 11.3227 | 11.4998 | 12.5208 | 44434.94 | 3863.9715 | 85129 | 7402.6437 | 67320 | 5854.0095 | 203468.5714 | 17693.2106 | 400352.5114 | 34813.8352 | 3357200 | 291935.2427 | 6138894.9875 | 533825.747 | 2100078.8747 | 182618.5619 | 8238973.8622 | 716444.3089 | 11596173.8622 | 1008379.5516 | 3375000 | 293483.0943 | 15371526.3736 | 1336676.481 | 149851.02 | 13030.7381 | 11191.95 | 973.2291 | 161042.97 | 14003.9672 | 2793074 | 242880 | 50599.1667 | 4400 | 2843673.1667 | 247280 | 3004716.1367 | 261283.9672 | 60390 | 5251.3908 | 363682 | 31625.0426 | 18452.5 | 1604.5916 | 10395 | 903.9279 | 116270 | 10110.6013 | 9240 | 803.4915 | 228900 | 19904.6756 | 807329.5 | 70203.7214 | 3090957.35 | 268783.3266 | 1545665.5 | 134407.9092 | 177572.305 | 15441.3243 | 82094.2678 | 7138.7496 | 3268529.655 | 284224.6509 | 1627759.7678 | 141546.6588 | 5219.649 | 453.89 | 9900 | 860.8837 | 15119.649 | 1314.7737 | 0 | 0 | 19462505.1777 | 1692419.6271 | 4632475.9045 | 402830.6259 | 11499810.6061 | 25041607.8139 | 30962315.7837 | 29674083.7184
470-40AE | oh | 2 | 12.4506 | 12.0733 | 6.1881 | 6.1881 | 8.2876 | 25682.58 | 4150.3389 | 49203 | 7951.2699 | 50022.5 | 8083.7021 | 123255 | 19918.171 | 248163.08 | 40103.4818 | 1940400 | 313571.2056 | 3548168.6625 | 573388.7472 | 1213807.056 | 196152.8251 | 4761975.7185 | 769541.5724 | 6702375.7185 | 1083112.7779 | 2400000 | 387843.1733 | 9350538.7985 | 1511059.4331 | 86611.14 | 13996.4747 | 50069.25 | 8091.257 | 136680.39 | 22087.7317 | 1502958 | 242880 | 27227.5 | 4400 | 1530185.5 | 247280 | 1666865.89 | 269367.7317 | 417780 | 67513.8004 | 2515964 | 406583.109 | 127655 | 20629.2168 | 12375 | 1999.8164 | 138416.6667 | 22368.3163 | 11000 | 1777.6145 | 272500 | 44036.3603 | 3495690.6667 | 564908.2337 | 1689262.1687 | 272987 | 844733.1875 | 136510 | 98561.2357 | 15927.626 | 45136.5923 | 7294.133 | 1787823.4044 | 288914.626 | 889869.7798 | 143804.133 | 2808.7023 | 453.89 | 9900 | 1599.8531 | 12708.7023 | 2053.7431 | 0 | 0 | 14646761.5718 | 2366936.0359 | 2556735.6698 | 413171.8647 | 6188068.1818 | 16575171.5174 | 20834829.7537 | 19131907.1872
470-47R | oh | 3 | 26.0369 | 26.0369 | 24.3072 | 24.3072 | 32.3938 | 97023.08 | 3991.5372 | 185878 | 7647.0356 | 177650 | 7308.535 | 465630 | 19156.0549 | 926181.08 | 38103.1627 | 7330400 | 301573.234 | 13404192.725 | 551449.5457 | 4585493.3227 | 188647.5569 | 17989686.0477 | 740097.1025 | 25320086.0477 | 1041670.3365 | 7975000 | 328092.1288 | 34221267.1277 | 1407865.628 | 327197.64 | 13460.9367 | 77165.55 | 3174.5968 | 404363.19 | 16635.5335 | 5903732 | 242880 | 106951.6667 | 4400 | 6010683.6667 | 247280 | 6415046.8567 | 263915.5335 | 860310 | 35393.2212 | 5180978 | 213145.8434 | 262872.5 | 10814.5954 | 38610 | 1588.4184 | 431860 | 17766.7545 | 34320 | 1411.9275 | 850200 | 34977.295 | 7659150.5 | 315098.0555 | 6635548.7792 | 272987 | 3318175.4583 | 136510 | 387045.7822 | 15923.094 | 177284.6869 | 7293.506 | 7022594.5614 | 288910.094 | 3495460.1453 | 143803.506 | 11032.7936 | 453.89 | 9900 | 407.2868 | 20932.7936 | 861.1768 | 0 | 0 | 48923944.9827 | 2012734.9543 | 9910507.0019 | 407719.0395 | 24307196.9697 | 64787601.7668 | 73231141.9524 | 74698108.7688
471-36F | oh | 2 | 10.2913 | 2.3337 | 1.0657 | 3.0515 | 3.5273 | 15287.25 | 5009.7244 | 29287.5 | 9597.6912 | 29920 | 9804.9652 | 21520.7143 | 7052.4684 | 96015.4643 | 31464.8493 | 1155000 | 378500.4965 | 2112005.1562 | 692116.8834 | 722504.2 | 236769.003 | 2834509.3563 | 928885.8864 | 3989509.3563 | 1307386.3829 | 350000 | 114697.1202 | 4435524.8205 | 1453548.3523 | 51554.25 | 16894.64 | 63028.35 | 20654.7721 | 114582.6 | 37549.4121 | 741152 | 242880 | 13426.6667 | 4400 | 754578.6667 | 247280 | 869161.2667 | 284829.4121 | 383130 | 125554.0218 | 2307294 | 756114.2205 | 117067.5 | 38363.7289 | 11880 | 3893.148 | 132880 | 43545.5809 | 10560 | 3460.576 | 261600 | 85727.9047 | 3224411.5 | 1056659.1807 | 290927.6229 | 95338.7444 | 145481.3958 | 47675.1347 | 17350.2801 | 5685.7919 | 7840.7908 | 2569.4746 | 308277.903 | 101024.5362 | 153322.1866 | 50244.6093 | 1385.0522 | 453.89 | 9900 | 3244.29 | 11285.0522 | 3698.18 | 0 | 0 | 7979499.2757 | 2614930.2492 | 1022483.4533 | 335074.0214 | 3051515.1515 | 7054554.2589 | 11031014.4273 | 8077037.7121
501-786 | oh | 2 | 9.7466 | 8.336 | 1.0485 | 1.0485 | 1.5358 | 4484.26 | 4276.8954 | 8591 | 8193.7283 | 7480 | 7134.104 | 21520.7143 | 20525.5367 | 42075.9743 | 40130.2645 | 338800 | 323132.948 | 619521.5125 | 590873.1189 | 211934.5653 | 202134.123 | 831456.0778 | 793007.2419 | 1170256.0778 | 1116140.1898 | 400000 | 381502.8902 | 1612332.0521 | 1537773.3445 | 15122.58 | 14423.2699 | 47713.05 | 45506.6662 | 62835.63 | 59929.9361 | 254656 | 242880 | 4613.3333 | 4400 | 259269.3333 | 247280 | 322104.9633 | 307209.9361 | 188100 | 179401.7341 | 1132780 | 1080397.1098 | 57475 | 54817.1965 | 1485 | 1416.3295 | 16610 | 15841.9075 | 1320 | 1258.9595 | 32700 | 31187.8613 | 1430470 | 1364321.0983 | 286222.7333 | 272987 | 143128.6667 | 136510 |  |  |  |  | 286222.7333 | 272987 | 143128.6667 | 136510 | 475.8968 | 453.89 | 9900 | 9442.1965 | 10375.8968 | 9896.0865 | 0 | 0 | 3339400.6822 | 3184977.5293 | 465233.63 | 443719.9361 | 1048484.8485 | 3071612.6284 | 4387885.5307 | 3536846.2584
504-2501R | oh | 2 | 13.5735 | 1.7561 | 1.7106 | 4.6487 | 6.6373 | 20790.66 | 4472.3848 | 39831 | 8568.2493 | 42075 | 9050.9676 | 23477.1429 | 5050.2878 | 126173.8029 | 27141.8896 | 1570800 | 337902.7908 | 2872327.0125 | 617880.8974 | 982605.712 | 211373.3208 | 3854932.7245 | 829254.2182 | 5425732.7245 | 1167157.009 | 325000 | 69912.4058 | 5876906.5274 | 1264211.3043 | 70113.78 | 15082.5324 | 78932.7 | 16979.6152 | 149046.48 | 32062.1477 | 1129070 | 242880 | 20454.1667 | 4400 | 1149524.1667 | 247280 | 1298570.6467 | 279342.1477 | 285120 | 61333.6158 | 1717056 | 369364.6641 | 87120 | 18740.8271 | 7920 | 1703.7116 | 88586.6667 | 19056.3292 | 7040 | 1514.4103 | 174400 | 37516.0725 | 2367242.6667 | 509229.6305 | 466973.2167 | 100452.9877 | 233514.8333 | 50232.5655 |  |  |  |  | 466973.2167 | 100452.9877 | 233514.8333 | 50232.5655 | 2109.9868 | 453.89 | 9900 | 2129.6394 | 12009.9868 | 2583.5294 | 0 | 0 | 8723132.3974 | 1876477.452 | 1532085.48 | 329574.7132 | 4648674.2424 | 13274573.1958 | 13371806.6399 | 14806658.6758
520-1045R | oh | 2 | 8.2299 | 8.2299 | 8.2123 | 8.2123 | 11.746 | 32001.31 | 3896.7486 | 61308.5 | 7465.4385 | 16830 | 2049.3623 | 153579.6429 | 18701.1488 | 263719.4529 | 32112.6983 | 2417800 | 294411.6602 | 4421130.7938 | 538354.0645 | 1512442.1253 | 184167.6719 | 5933572.9191 | 722521.7364 | 8351372.9191 | 1016933.3967 | 775000 | 94370.5173 | 9390092.3719 | 1143416.6123 | 107920.23 | 13141.2747 | 28863.45 | 3514.6564 | 136783.68 | 16655.9311 | 1994606 | 242880 | 36134.1667 | 4400 | 2030740.1667 | 247280 | 2167523.8467 | 263935.9311 | 942480 | 114764.2905 | 5675824 | 691136.0605 | 287980 | 35066.8665 | 28215 | 3435.6957 | 315590 | 38428.8923 | 25080 | 3053.9517 | 621300 | 75654.7128 | 7896469 | 961540.47 | 2241854.0354 | 272987 | 1121062.5208 | 136510 | 173658.6369 | 21146.136 | 67441.3507 | 8212.226 | 2415512.6724 | 294133.136 | 1188503.8715 | 144722.226 | 3727.4857 | 453.89 | 9900 | 1205.5073 | 13627.4857 | 1659.3973 | 0 | 0 | 19715701.53 | 2400749.6155 | 3356027.7182 | 408658.1571 | 8212310.6061 | 23492025.4605 | 27928012.136 | 26848053.1786
520-10R | oh | 2 | 5.5998 | 5.5998 | 4.5294 | 4.5294 | 5.8016 | 23032.79 | 5085.224 | 44126.5 | 9742.3341 | 45815 | 10115.1244 | 110538.2143 | 24404.841 | 223512.5043 | 49347.5234 | 1740200 | 384204.7251 | 3182087.7687 | 702547.4982 | 1088572.9947 | 240337.2533 | 4270660.7634 | 942884.7514 | 6010860.7634 | 1327089.4765 | 2400000 | 529876.6465 | 8634373.2677 | 1906313.6464 | 77675.07 | 17149.2523 | 41822.55 | 9233.6636 | 119497.62 | 26382.9159 | 1100090 | 242880 | 19929.1667 | 4400 | 1120019.1667 | 247280 | 1239516.7867 | 273662.9159 | 409860 | 90489.6843 | 2468268 | 544948.9877 | 125235 | 27649.6258 | 21285 | 4699.3435 | 238076.6667 | 52563.0274 | 18920 | 4177.1942 | 468700 | 103480.4934 | 3750344.6667 | 828008.3563 | 1236455.3229 | 272987 | 618302.3958 | 136510 | 66248.2369 | 14626.414 | 31998.3696 | 7064.662 | 1302703.5598 | 287613.414 | 650300.7655 | 143574.662 | 2055.8294 | 453.89 | 9900 | 2185.7412 | 11955.8294 | 2639.6312 | 0 | 0 | 13699377.3236 | 3024575.0478 | 1889817.5521 | 417237.5779 | 4529356.0606 | 11603130.3952 | 18228733.3842 | 13492947.9473
520-1489R | oh | 2 | 16.6227 | 16.6227 | 16.4032 | 16.4032 | 22.0822 | 68079.22 | 4150.3571 | 130427 | 7951.3048 | 44412.5 | 2707.5477 | 326723.5714 | 19918.2586 | 569642.2914 | 34727.4683 | 5143600 | 313572.5848 | 9405462.9625 | 573391.2693 | 3217552.0373 | 196153.6879 | 12623014.9998 | 769544.9572 | 17766614.9998 | 1083117.542 | 2275000 | 138692.2837 | 20611257.2913 | 1256537.294 | 229588.26 | 13996.5363 | 82467 | 5027.4886 | 312055.26 | 19024.0249 | 3984014 | 242880 | 72174.1667 | 4400 | 4056188.1667 | 247280 | 4368243.4267 | 266304.0249 | 1107810 | 67536.1313 | 6671478 | 406717.591 | 338497.5 | 20636.0401 | 69795 | 4254.9573 | 780670 | 47592.4858 | 62040 | 3782.1843 | 1536900 | 93695.0201 | 10567190.5 | 644214.41 | 4477865.7354 | 272987 | 2239203.5208 | 136510 | 261551.0604 | 15945.105 | 119702.2989 | 7297.488 | 4739416.7958 | 288932.105 | 2358905.8197 | 143807.488 | 7445.2574 | 453.89 | 9900 | 603.54 | 17345.2574 | 1057.43 | 0 | 0 | 35935209.8445 | 2190741.2391 | 6727149.2464 | 410111.5129 | 16403219.697 | 44164380.4872 | 52338429.5414 | 50891529.7336
520-1509R | oh | 2 | 13.4619 | 13.4619 | 13.2937 | 13.2937 | 15.8585 | 56460.91 | 4247.1771 | 108168.5 | 8136.7936 | 76202.5 | 5732.205 | 270965.3571 | 20382.9136 | 511797.2671 | 38499.0892 | 4265800 | 320887.6352 | 7800339.0438 | 586767.394 | 2668448.8453 | 200729.5793 | 10468787.8891 | 787496.9733 | 14734587.8891 | 1108384.6085 | 3800000 | 285848.6131 | 19046385.1562 | 1432732.3108 | 190407.03 | 14323.0488 | 78932.7 | 5937.5797 | 269339.73 | 20260.6285 | 3228786 | 242880 | 58492.5 | 4400 | 3287278.5 | 247280 | 3556618.23 | 267540.6285 | 1204830 | 90631.3117 | 7255754 | 545801.8994 | 368142.5 | 27692.9008 | 49995 | 3760.7898 | 559203.3333 | 42065.1309 | 44440 | 3342.9243 | 1100900 | 82813.3521 | 10583264.8333 | 796108.309 | 3629020.9312 | 272987 | 1814729.8125 | 136510 | 279233.8362 | 21004.896 | 108839.042 | 8187.234 | 3908254.7674 | 293991.896 | 1923568.8545 | 144697.234 | 6033.9002 | 453.89 | 9900 | 744.7109 | 15933.9002 | 1198.6009 | 0 | 0 | 33553838.6572 | 2524031.1167 | 5480187.0845 | 412237.8625 | 13293750 | 31717016.8566 | 46847588.6572 | 37197203.9411
520-1525R | oh | 2 | 8.2225 | 8.2225 | 7.4684 | 7.4684 | 10.9927 | 26497.9 | 3548.0159 | 50765 | 6797.3322 | 35997.5 | 4819.9934 | 127167.8571 | 17027.5223 | 240428.2571 | 32192.8638 | 2002000 | 268063.8044 | 3660808.9375 | 490175.0105 | 1252340.6133 | 167685.9087 | 4913149.5508 | 657860.9192 | 6915149.5508 | 925924.7237 | 1575000 | 210889.3566 | 8730577.808 | 1169006.9441 | 89360.7 | 11965.2194 | 26507.25 | 3549.2679 | 115867.95 | 15514.4873 | 1813918 | 242880 | 32860.8333 | 4400 | 1846778.8333 | 247280 | 1962646.7833 | 262794.4873 | 460350 | 61639.9462 | 2772330 | 371209.454 | 140662.5 | 18834.428 | 18315 | 2452.3419 | 204856.6667 | 27429.8988 | 16280 | 2179.8595 | 403300 | 54001.0651 | 4016094.1667 | 537746.9936 | 2038768.2521 | 272987 | 1019507.3542 | 136510 | 119102.6938 | 15947.613 | 54502.0745 | 7297.719 | 2157870.9459 | 288934.613 | 1074009.4287 | 143807.719 | 3389.819 | 453.89 | 9900 | 1325.5902 | 13289.819 | 1779.4802 | 0 | 0 | 14917832.7396 | 1997468.031 | 3036656.212 | 406602.2063 | 7468371.2121 | 21985457.6975 | 22386203.9517 | 25022113.9095
520-1527R | oh | 3 | 13.2657 | 13.2657 | 10.018 | 10.018 | 13.06 | 41988.98 | 4191.3567 | 80443 | 8029.8523 | 62645 | 6253.2489 | 201512.1429 | 20115.0225 | 386589.1229 | 38589.4805 | 3172400 | 316670.2335 | 5800974.1625 | 579055.5549 | 1984478.2027 | 198091.4058 | 7785452.3652 | 777146.9607 | 10957852.3652 | 1093817.1942 | 3175000 | 316929.7665 | 14519441.488 | 1449336.4412 | 141602.34 | 14134.8021 | 66562.65 | 6644.3103 | 208164.99 | 20779.1123 | 2433170 | 242880 | 44079.1667 | 4400 | 2477249.1667 | 247280 | 2685414.1567 | 268059.1123 | 785070 | 78366.0006 | 4727866 | 471937.4701 | 239882.5 | 23945.1668 | 34650 | 3458.7768 | 387566.6667 | 38687.0593 | 30800 | 3074.4683 | 763000 | 76162.9644 | 6968835.1667 | 695631.9062 | 2734781.6979 | 272987 | 1367556.1458 | 136510 | 210003.5086 | 20962.634 | 81949.4521 | 8180.227 | 2944785.2065 | 293949.634 | 1449505.5979 | 144690.227 | 4547.0666 | 453.89 | 9900 | 988.2219 | 14447.0666 | 1442.1119 | 0 | 0 | 24447508.9278 | 2440360.0934 | 4134919.7546 | 412749.3393 | 10017992.4242 | 26120055.9313 | 34465501.352 | 30254975.6859
520-1902R | oh | 2 | 8.9862 | 8.9862 | 6.5758 | 6.5758 | 7.3758 | 41377.49 | 6292.4294 | 79271.5 | 12055.1129 | 78540 | 11943.871 | 198577.5 | 30198.4217 | 397766.49 | 60489.8349 | 3126200 | 475412.9032 | 5716493.9562 | 869328.574 | 1955578.0347 | 297392.0514 | 7672071.9909 | 1166720.6253 | 10798271.9909 | 1642133.5286 | 3800000 | 577880.1843 | 14996038.4809 | 2280503.5478 | 139540.17 | 21220.3945 | 81877.95 | 12451.4855 | 221418.12 | 33671.88 | 1597120 | 242880 | 28933.3333 | 4400 | 1626053.3333 | 247280 | 1847471.4533 | 280951.88 | 419760 | 63834.47 | 2527888 | 384425.3641 | 128260 | 19504.977 | 10890 | 1656.0829 | 121806.6667 | 18523.5945 | 9680 | 1472.0737 | 239800 | 36467.2811 | 3458084.6667 | 525883.8433 | 1795096.3333 | 272987 | 897656.6667 | 136510 | 96133.7487 | 14619.418 | 46447.982 | 7063.518 | 1891230.082 | 287606.418 | 944104.6487 | 143573.518 | 2984.6706 | 453.89 | 9900 | 1505.53 | 12884.6706 | 1959.42 | 0 | 0 | 20358237.9002 | 3095953.2291 | 2791576.102 | 424525.398 | 6575757.5758 | 14751641.0084 | 26933995.4759 | 17543217.1104
520-1904 | oh | 3 | 8.0419 | 8.0419 | 5.4665 | 5.4665 | 6.9065 | 30574.5 | 5593.0901 | 58575 | 10715.3103 | 58905 | 10775.6782 | 146732.1429 | 26842.1756 | 294786.6429 | 53926.2542 | 2310000 | 422575.6158 | 4224010.3125 | 772711.584 | 1445008.4 | 264339.963 | 5669018.7125 | 1037051.547 | 7979018.7125 | 1459627.1629 | 2725000 | 498492.8802 | 10998805.3554 | 2012046.2972 | 103108.5 | 18861.9645 | 66562.65 | 12176.5164 | 169671.15 | 31038.4808 | 1327698 | 242880 | 24052.5 | 4400 | 1351750.5 | 247280 | 1521421.65 | 278318.4808 | 381150 | 69724.9766 | 2295370 | 419899.3036 | 116462.5 | 21304.854 | 21285 | 3893.7325 | 238076.6667 | 43552.1186 | 18920 | 3461.0955 | 468700 | 85740.7754 | 3539964.1667 | 647576.8562 | 1492277.2312 | 272987 | 746228.8125 | 136510 | 79948.2851 | 14625.193 | 38616.9502 | 7064.321 | 1572225.5164 | 287612.193 | 784845.7627 | 143574.321 | 2481.1794 | 453.89 | 9900 | 1811.0384 | 12381.1794 | 2264.9284 | 0 | 0 | 16123376.2178 | 2949500.2747 | 2306267.4127 | 421892.8018 | 5466477.2727 | 13813059.3075 | 21589853.4905 | 16119326.7202
520-22R | oh | 2 | 3.2506 | 3.2506 | 1.9752 | 1.9752 | 2.1952 | 11618.31 | 5882.1245 | 22258.5 | 11269.0459 | 22440 | 11360.9359 | 55758.2143 | 28229.3002 | 112075.0243 | 56741.4065 | 877800 | 444413.0789 | 1605123.9187 | 812643.0426 | 549103.192 | 278000.2736 | 2154227.1107 | 1090643.3162 | 3032027.1107 | 1535056.3951 | 1050000 | 531594.592 | 4194102.135 | 2123392.3936 | 39181.23 | 19836.6952 | 27685.35 | 14016.5546 | 66866.58 | 33853.2498 | 479734 | 242880 | 8690.8333 | 4400 | 488424.8333 | 247280 | 555291.4133 | 281133.2498 | 149490 | 75683.8815 | 900262 | 455785.1529 | 45677.5 | 23125.6305 | 2475 | 1253.0444 | 27683.3333 | 14015.5336 | 2200 | 1113.8172 | 54500 | 27592.2907 | 1182287.8333 | 598569.3508 | 539201.0271 | 272987 | 269633.1042 | 136510 | 28888.0258 | 14625.446 | 13953.5457 | 7064.409 | 568089.0529 | 287612.446 | 283586.6499 | 143574.409 | 896.5187 | 453.89 | 9900 | 5012.1776 | 10796.5187 | 5466.0676 | 0 | 0 | 5955275.54 | 3015040.258 | 838878.0632 | 424707.6588 | 1975189.3939 | 4390362.794 | 7930464.9339 | 5229240.8572
520-35R | oh | 3 | 16.8116 | 16.8116 | 13.971 | 13.971 | 18.8404 | 56257.08 | 4026.6973 | 107778 | 7714.3959 | 62177.5 | 4450.4616 | 269987.1429 | 19324.7945 | 496199.7229 | 35516.3493 | 4250400 | 304229.6962 | 7772178.975 | 556307.0884 | 2658815.456 | 190309.2929 | 10430994.431 | 746616.3813 | 14681394.431 | 1050846.0775 | 3075000 | 220098.418 | 18252594.1539 | 1306460.8447 | 189719.64 | 13579.5098 | 72453.15 | 5185.9589 | 262172.79 | 18765.4687 | 3393282 | 242880 | 61472.5 | 4400 | 3454754.5 | 247280 | 3716927.29 | 266045.4687 | 1361250 | 97433.8119 | 8197750 | 586768.067 | 415937.5 | 29771.4425 | 52965 | 3791.061 | 592423.3333 | 42403.7198 | 47080 | 3369.832 | 1166300 | 83479.9301 | 11833705.8333 | 847017.8644 | 3813907.5812 | 272987 | 1907184.3125 | 136510 | 292878.6569 | 20963.294 | 114286.9057 | 8180.282 | 4106786.2382 | 293950.294 | 2021471.2182 | 144690.282 | 6341.3075 | 453.89 | 9900 | 708.6095 | 16241.3075 | 1162.4995 | 0 | 0 | 34209327.5329 | 2448591.5026 | 5738398.5082 | 410735.7507 | 13971022.7273 | 37680883.795 | 48180350.2601 | 43419282.3032
520-45 | oh | 2 | 8.9975 | 8.9975 | 8.7233 | 8.7233 | 12.7431 | 36077.91 | 4135.812 | 69118.5 | 7923.4391 | 19167.5 | 2197.2774 | 173143.9286 | 19848.454 | 297507.8386 | 34104.9825 | 2725800 | 312473.6534 | 4984332.1688 | 571381.7897 | 1705109.912 | 195466.2571 | 6689442.0807 | 766848.0468 | 9415242.0807 | 1079321.7001 | 650000 | 74513.1245 | 10362749.9193 | 1187939.8071 | 121668.03 | 13947.4847 | 43000.65 | 4929.4043 | 164668.68 | 18876.889 | 2118714 | 242880 | 38382.5 | 4400 | 2157096.5 | 247280 | 2321765.18 | 266156.889 | 585090 | 67072.1292 | 3523542 | 403923.2671 | 178777.5 | 20494.2617 | 41580 | 4766.5473 | 465080 | 53314.7137 | 36960 | 4236.9309 | 915600 | 104960.3335 | 5746629.5 | 658768.1834 | 2381346.2562 | 272987 | 1190817.0625 | 136510 | 139024.4856 | 15937.152 | 63646.1494 | 7296.113 | 2520370.7418 | 288924.152 | 1254463.2119 | 143806.113 | 3959.4166 | 453.89 | 9900 | 1134.8922 | 13859.4166 | 1588.7822 | 0 | 0 | 18643609.5777 | 2137220.9247 | 3576228.3919 | 409963.002 | 8723295.4545 | 25486235.4399 | 27366905.0323 | 29062463.8317
521-14R | oh | 3 | 18.8417 | 18.8417 | 12.7723 | 12.7723 | 1.4778 | 54014.95 | 4229.0539 | 103482.5 | 8102.073 | 99577.5 | 7796.3344 | 259226.7857 | 20295.9374 | 516301.7357 | 40423.3987 | 4081000 | 319518.3724 | 7462418.2188 | 584263.5932 | 2552848.1733 | 199873.0442 | 10015266.3921 | 784136.6374 | 14096266.3921 | 1103655.0098 | 4475000 | 350366.2623 | 19087568.1278 | 1494444.6709 | 182158.35 | 14261.9308 | 101316.6 | 7932.4957 | 283474.95 | 22194.4265 | 3102148 | 242880 | 56198.3333 | 4400 | 3158346.3333 | 247280 | 3441821.2833 | 269474.4265 | 926640 | 72550.479 | 5580432 | 436915.1066 | 283140 | 22168.2019 | 38610 | 3022.9366 | 431860 | 33812.1059 | 34320 | 2687.0548 | 850200 | 66565.6751 | 8145202 | 637721.56 | 3486685.0958 | 272987 | 1743553.2917 | 136510 | 264925.4061 | 20742.106 | 103984.9001 | 8141.408 | 3751610.502 | 293729.106 | 1847538.1918 | 144651.408 | 5797.2413 | 453.89 | 9900 | 775.112 | 15697.2413 | 1229.002 | 0 | 0 | 31000077.871 | 2427124.3388 | 5289359.4751 | 414125.8345 | 12772348.4848 | 2955670.4545 | 43772426.3559 | 8245029.9297
521-1819R | oh | 2 | 10.2657 | 10.2657 | 5.3453 | 5.3453 | 7.1129 | 28128.54 | 5262.3283 | 53889 | 10081.6327 | 56100 | 10495.2698 | 134993.5714 | 25254.7942 | 273111.1114 | 51094.025 | 2125200 | 397585.5154 | 3886089.4875 | 727015.2887 | 1329407.728 | 248707.5365 | 5215497.2155 | 975722.8253 | 7340697.2155 | 1373308.3406 | 3400000 | 636076.9585 | 11013808.3269 | 2060479.3242 | 94859.82 | 17746.5135 | 50658.3 | 9477.2286 | 145518.12 | 27223.7421 | 1298258 | 242880 | 23519.1667 | 4400 | 1321777.1667 | 247280 | 1467295.2867 | 274503.7421 | 442530 | 82789.1578 | 2665014 | 498574.7057 | 135217.5 | 25296.6871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3242761.5 | 606660.5506 | 1459187.8979 | 272987 | 729682.1458 | 136510 | 78171.4186 | 14624.423 | 37760.1985 | 7064.233 | 1537359.3165 | 287611.423 | 767442.3443 | 143574.233 | 2426.1624 | 453.89 | 9900 | 1852.1064 | 12326.1624 | 2305.9964 | 0 | 0 | 15806255.3059 | 2957057.2942 | 2234737.631 | 418077.9751 | 5345265.1515 | 14225770.6864 | 21151520.4574 | 16460508.3173
521-1856R | oh | 3 | 15.721 | 15.721 | 12.1964 | 12.1964 | 16.1409 | 56460.91 | 4629.3089 | 108168.5 | 8868.8864 | 105655 | 8662.8011 | 270965.3571 | 22216.8282 | 541249.7671 | 44377.8246 | 4265800 | 349758.9018 | 7800339.0438 | 639560.6962 | 2668448.8453 | 218789.849 | 10468787.8891 | 858350.5451 | 14734587.8891 | 1208109.4469 | 4875000 | 399708.0609 | 20150837.6562 | 1652195.3325 | 190407.03 | 15611.7384 | 73042.2 | 5988.832 | 263449.23 | 21600.5704 | 2962262 | 242880 | 53664.1667 | 4400 | 3015926.1667 | 247280 | 3279375.3967 | 268880.5704 | 964260 | 79061.0246 | 5806988 | 476123.0591 | 294635 | 24157.5353 | 60390 | 4951.4605 | 675473.3333 | 55383.0023 | 53680 | 4401.2982 | 1329800 | 109032.1599 | 9185226.3333 | 753109.5399 | 3329459.0604 | 272987 | 1664930.7708 | 136510 | 209840.1735 | 17205.089 | 91704.5478 | 7518.984 | 3539299.234 | 290192.089 | 1756635.3187 | 144028.984 | 5535.8247 | 453.89 | 9900 | 811.7148 | 15435.8247 | 1265.6048 | 0 | 0 | 32890799.0482 | 2696762.5662 | 5036010.7153 | 412909.5544 | 12196401.5152 | 32281710.7119 | 45087200.5634 | 37317721.4272
521-18R | oh | 3 | 18.2392 | 18.2392 | 12.6528 | 12.6528 | 16.6173 | 54014.95 | 4268.9978 | 103482.5 | 8178.5981 | 100980 | 7980.8164 | 259226.7857 | 20487.635 | 517704.2357 | 40916.0472 | 4081000 | 322536.2612 | 7462418.2188 | 589782.0317 | 2552848.1733 | 201760.8687 | 10015266.3921 | 791542.9004 | 14096266.3921 | 1114079.1616 | 4350000 | 343796.3088 | 18963970.6278 | 1498791.5176 | 182158.35 | 14396.6364 | 78932.7 | 6238.3381 | 261091.05 | 20634.9745 | 3073122 | 242880 | 55672.5 | 4400 | 3128794.5 | 247280 | 3389885.55 | 267914.9745 | 726660 | 57430.5806 | 4376108 | 345859.7189 | 222035 | 17548.233 | 46530 | 3677.435 | 520446.6667 | 41132.7915 | 41360 | 3268.8311 | 1024600 | 80977.8616 | 6957739.6667 | 549895.4517 | 3454061.0812 | 272987 | 1727239.3125 | 136510 | 185064.4368 | 14626.315 | 89387.2093 | 7064.596 | 3639125.518 | 287613.315 | 1816626.5218 | 143574.596 | 5742.998 | 453.89 | 9900 | 782.433 | 15642.998 | 1236.323 | 0 | 0 | 29576478.8105 | 2337536.6072 | 5206512.0718 | 411489.5705 | 12652840.9091 | 33234697.0865 | 42229319.7195 | 38441209.1583
521-27R | oh | 2 | 13.4508 | 13.4508 | 10.1674 | 10.1674 | 12.9154 | 51365.16 | 5051.9344 | 98406 | 9678.5575 | 97240 | 9563.8775 | 246510 | 24245.0786 | 493521.16 | 48539.448 | 3880800 | 381689.5909 | 7096337.325 | 697948.3845 | 2427614.112 | 238763.9243 | 9523951.437 | 936712.3088 | 13404751.437 | 1318401.8998 | 5500000 | 540943.2978 | 19398272.597 | 1907884.6456 | 173222.28 | 17036.9875 | 74220.3 | 7299.8134 | 247442.58 | 24336.801 | 2469464 | 242880 | 44736.6667 | 4400 | 2514200.6667 | 247280 | 2761643.2467 | 271616.801 | 885060 | 87048.5955 | 5330028 | 524225.9861 | 270435 | 26598.182 | 28710 | 2823.724 | 321126.6667 | 31583.876 | 25520 | 2509.9769 | 632200 | 62178.9733 | 7493079.6667 | 736969.3138 | 2775574.6417 | 272987 | 1387955.0833 | 136510 | 148703.2261 | 14625.457 | 71827.7381 | 7064.497 | 2924277.8677 | 287612.457 | 1459782.8214 | 143574.497 | 4614.8922 | 453.89 | 9900 | 973.6979 | 14514.8922 | 1427.5879 | 0 | 0 | 29830145.0236 | 2933894.0043 | 4221426.0681 | 415191.298 | 10167424.2424 | 25830845.0644 | 39997569.266 | 30052271.1325
521-32R | oh | 3 | 10.3 | 10.3 | 9.9972 | 9.9972 | 13.5381 | 42396.64 | 4240.8688 | 81224 | 8124.7082 | 80877.5 | 8090.0483 | 203468.5714 | 20352.6391 | 407966.7114 | 40808.2644 | 3203200 | 320411.0259 | 5857294.3 | 585895.8777 | 2003744.9813 | 200431.4389 | 7861039.2813 | 786327.3166 | 11064239.2813 | 1106738.3424 | 3875000 | 387610.1165 | 15347205.9928 | 1535156.7233 | 142977.12 | 14301.775 | 45356.85 | 4536.9739 | 188333.97 | 18838.7489 | 2428110 | 242880 | 43987.5 | 4400 | 2472097.5 | 247280 | 2660431.47 | 266118.7489 | 668250 | 66843.9898 | 4024350 | 402549.3606 | 204187.5 | 20424.5524 | 26235 | 2624.2455 | 293443.3333 | 29352.6722 | 23320 | 2332.6627 | 577700 | 57786.4166 | 5817485.8333 | 581913.8998 | 2729094.4687 | 272987 | 1364712.1875 | 136510 | 172078.7701 | 17212.767 | 75180.5758 | 7520.194 | 2901173.2388 | 290199.767 | 1439892.7633 | 144030.194 | 4537.6105 | 453.89 | 9900 | 990.2813 | 14437.6105 | 1444.1713 | 0 | 0 | 24080302.6755 | 2408714.5615 | 4100324.2333 | 410148.9429 | 9997159.0909 | 27076104.3279 | 34077461.7664 | 31176428.5612
521-700R | oh | 2 | 18.8364 | 18.8364 | 13.3788 | 13.3788 | 18.0506 | 67263.9 | 5027.6528 | 128865 | 9632.0385 | 125757.5 | 9399.7678 | 322810.7143 | 24128.5472 | 644697.1143 | 48188.0063 | 5082000 | 379855.0396 | 9292822.6875 | 694593.7683 | 3179018.48 | 237616.3303 | 12471841.1675 | 932210.0986 | 17553841.1675 | 1312065.1382 | 6750000 | 504530.0113 | 24948538.2818 | 1864783.1558 | 226838.7 | 16955.101 | 110152.35 | 8233.358 | 336991.05 | 25188.459 | 3249440 | 242880 | 58866.6667 | 4400 | 3308306.6667 | 247280 | 3645297.7167 | 272468.459 | 1576080 | 117804.3941 | 9491504 | 709444.2401 | 481580 | 35995.7871 | 40590 | 3033.9071 | 454006.6667 | 33934.8131 | 36080 | 2696.8063 | 893800 | 66807.248 | 12973640.6667 | 969717.1959 | 3652235.1667 | 272987 | 1826338.3333 | 136510 | 195648.5175 | 14623.785 | 94509.1088 | 7064.101 | 3847883.6842 | 287610.785 | 1920847.4422 | 143574.101 | 6072.498 | 453.89 | 9900 | 739.9773 | 15972.498 | 1193.8673 | 0 | 0 | 41786035.1306 | 3123305.0041 | 5566145.1588 | 416042.56 | 13378787.8788 | 36101135.0454 | 55164823.0094 | 41667280.2042
522-34 | oh | 2 | 3.339 | 3.339 | 1.233 | 1.233 | 1.2747 | 8357.03 | 6778.052 | 16010.5 | 12985.4747 | 15427.5 | 12512.6267 | 40106.7857 | 32529.0059 | 79901.8157 | 64805.1593 | 631400 | 512103.2258 | 1154562.8188 | 936419.6134 | 394968.9627 | 320343.4905 | 1549531.7814 | 1256763.1038 | 2180931.7814 | 1768866.3296 | 775000 | 628571.4286 | 3035833.5971 | 2462242.9175 | 28182.99 | 22858.0933 | 19438.65 | 15765.9097 | 47621.64 | 38624.0029 | 299460 | 242880 | 5425 | 4400 | 304885 | 247280 | 352506.64 | 285904.0029 | 62370 | 50585.8065 | 375606 | 304638.9677 | 19057.5 | 15456.7742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 457033.5 | 370681.5484 | 336580.5625 | 272987 | 168310.625 | 136510 | 18030.2316 | 14623.598 | 8709.5934 | 7064.002 | 354610.7941 | 287610.598 | 177020.2184 | 143574.002 | 559.6257 | 453.89 | 9900 | 8029.4931 | 10459.6257 | 8483.3831 | 0 | 0 | 3857937.517 | 3129018.447 | 529526.8584 | 429478.0049 | 1232954.5455 | 2549489.4058 | 5090892.0624 | 3079016.2642
522-36 | oh | 2 | 3.4858 | 3.4858 | 1.3595 | 1.3595 | 1.552 | 9172.35 | 6747.0059 | 17572.5 | 12925.9961 | 18700 | 13755.3636 | 44019.6429 | 32380.0103 | 89464.4929 | 65808.3759 | 693000 | 509757.5926 | 1267203.0938 | 932130.4451 | 433502.52 | 318876.1919 | 1700705.6138 | 1251006.637 | 2393705.6138 | 1760764.2297 | 850000 | 625243.8005 | 3333170.1066 | 2451816.4061 | 30932.55 | 22753.3943 | 30041.55 | 22097.9916 | 60974.1 | 44851.3859 | 330188 | 242880 | 5981.6667 | 4400 | 336169.6667 | 247280 | 397143.7667 | 292131.3859 | 57420 | 42237.0577 | 345796 | 254360.9473 | 17545 | 12905.7676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420761 | 309503.7726 | 371117.5542 | 272987 | 185581.2083 | 136510 | 19878.3943 | 14622.168 | 9603.0275 | 7063.804 | 390995.9485 | 287609.168 | 195184.2358 | 143573.804 | 617.0497 | 453.89 | 9900 | 7282.2513 | 10517.0497 | 7736.1413 | 0 | 0 | 4155444.1048 | 3056665.488 | 592328.0025 | 435705.1899 | 1359469.697 | 3103914.7347 | 5514913.8017 | 3696242.7371
522-38R | oh | 2 | 22.1362 | 22.1362 | 12.9818 | 12.9818 | 14.7805 | 72971.14 | 5621.0262 | 139799 | 10768.8305 | 127627.5 | 9831.25 | 350200.7143 | 26976.2455 | 690598.3543 | 53197.3522 | 5513200 | 424686.2745 | 10081304.6125 | 776571.0836 | 3448753.3813 | 265660.2745 | 13530057.9938 | 1042231.3581 | 19043257.9938 | 1466917.6326 | 6450000 | 496848.7395 | 26183856.3481 | 2016963.7243 | 246085.62 | 18956.1752 | 172591.65 | 13294.875 | 418677.27 | 32251.0502 | 3153024 | 242880 | 57120 | 4400 | 3210144 | 247280 | 3628821.27 | 279531.0502 | 1644390 | 126668.6975 | 9902882 | 762827.0448 | 502452.5 | 38704.3242 | 1980 | 152.521 | 22146.6667 | 1705.9757 | 1760 | 135.5742 | 43600 | 3358.5434 | 12119211.1667 | 933552.6809 | 3543867.6 | 272987 | 1772148 | 136510 | 189763.9212 | 14617.669 | 91692.4512 | 7063.144 | 3733631.5212 | 287604.669 | 1863840.4512 | 143573.144 | 5892.3175 | 453.89 | 9900 | 762.605 | 15792.3175 | 1216.495 | 0 | 0 | 42052491.3534 | 3239337.5692 | 5492661.7212 | 423104.1942 | 12981818.1818 | 29560958.0167 | 55034309.5353 | 35053619.7379
523-31AE | oh | 2 | 9.7805 | 9.7805 | 2.7023 | 2.7023 | 2.7722 | 20383 | 7542.91 | 39050 | 14450.799 | 40205 | 14878.217 | 97821.4286 | 36199.6876 | 197459.4286 | 73071.6136 | 1540000 | 569890.6644 | 2816006.875 | 1042088.3305 | 963338.9333 | 356492.12 | 3779345.8083 | 1398580.4505 | 5319345.8083 | 1968471.1149 | 1675000 | 619848.6123 | 7191805.2369 | 2661391.3408 | 68739 | 25437.4769 | 75987.45 | 28119.8301 | 144726.45 | 53557.307 | 656328 | 242880 | 11890 | 4400 | 668218 | 247280 | 812944.45 | 300837.307 | 145530 | 53854.6678 | 876414 | 324324.7771 | 44467.5 | 16455.5929 | 990 | 366.3583 | 11073.3333 | 4097.7853 | 880 | 325.6518 | 21800 | 8067.2834 | 1101154.8333 | 407492.1166 | 737685.325 | 272987 | 368887.25 | 136510 | 39489.8706 | 14613.577 | 19084.6687 | 7062.451 | 777175.1956 | 287600.577 | 387971.9187 | 143572.451 | 1226.5346 | 453.89 | 9900 | 3663.5828 | 11126.5346 | 4117.4728 | 0 | 0 | 9081261.8004 | 3360601.5073 | 1200916.3687 | 444409.758 | 2702272.7273 | 5544307.027 | 11783534.5277 | 6745223.3957
524-1782F | oh | 3 | 8.3818 | 8.3818 | 7.6273 | 7.6273 | 10.1528 | 35262.59 | 4623.224 | 67556.5 | 8857.2288 | 69657.5 | 9132.6877 | 169231.0714 | 22187.6256 | 341707.6614 | 44800.7661 | 2664200 | 349299.1657 | 4871691.8937 | 638720.0337 | 1666576.3547 | 218502.2634 | 6538268.2484 | 857222.2972 | 9202468.2484 | 1206521.4628 | 3650000 | 478545.888 | 13194175.9098 | 1729868.1169 | 118918.47 | 15591.2178 | 53014.5 | 6950.6496 | 171932.97 | 22541.8673 | 1852512 | 242880 | 33560 | 4400 | 1886072 | 247280 | 2058004.97 | 269821.8673 | 431640 | 56591.6567 | 2599432 | 340807.5328 | 131890 | 17291.8951 | 25245 | 3309.8331 | 282370 | 37021.0965 | 22440 | 2942.0739 | 555900 | 72883.1943 | 4048917 | 530847.2825 | 2082146.3 | 272987 | 1041199 | 136510 | 106963.5227 | 14023.823 | 53075.0561 | 6958.589 | 2189109.8227 | 287010.823 | 1094274.0561 | 143468.589 | 3461.9428 | 453.89 | 9900 | 1297.9738 | 13361.9428 | 1751.8638 | 0 | 0 | 19445564.6754 | 2549478.0862 | 3152279.0261 | 413290.4563 | 7627272.7273 | 20305587.807 | 27072837.4026 | 23457866.8331
524-27R | oh | 3 | 13.4561 | 13.4561 | 11.4695 | 11.4695 | 14.0614 | 59314.53 | 5171.4975 | 113635.5 | 9907.618 | 106122.5 | 9252.5768 | 284660.3571 | 24818.8822 | 563732.8871 | 49150.5745 | 4481400 | 390722.9644 | 8194580.0062 | 714466.5935 | 2803316.296 | 244414.7037 | 10997896.3022 | 958881.2972 | 15479296.3022 | 1349604.2616 | 5325000 | 464274.5092 | 21368029.1894 | 1863029.3453 | 200030.49 | 17440.1986 | 97782.3 | 8525.414 | 297812.79 | 25965.6126 | 2785714 | 242880 | 50465.8333 | 4400 | 2836179.8333 | 247280 | 3133992.6233 | 273245.6126 | 738540 | 64391.6049 | 4447652 | 387780.5538 | 225665 | 19675.2126 | 59895 | 5222.1074 | 669936.6667 | 58410.2379 | 53240 | 4641.8732 | 1318900 | 114991.8592 | 7513828.6667 | 655113.449 | 3131026.4646 | 272987 | 1565702.4792 | 136510 | 160840.5406 | 14023.317 | 79810.8323 | 6958.523 | 3291867.0052 | 287010.317 | 1645513.3114 | 143468.523 | 5205.8948 | 453.89 | 9900 | 863.1582 | 15105.8948 | 1317.0482 | 0 | 0 | 32188830.756 | 2806470.1595 | 4779505.9348 | 416714.1356 | 11469507.5758 | 28122766.1427 | 43658338.3318 | 32902272.0774
524-46R | oh | 3 | 12.2722 | 12.2722 | 11.0532 | 11.0532 | 14.7147 | 45657.92 | 4130.7349 | 87472 | 7913.7122 | 81345 | 7359.3941 | 219120 | 19824.088 | 433594.92 | 39227.9292 | 3449600 | 312090.0601 | 6307855.4 | 570680.3604 | 2157879.2107 | 195226.3024 | 8465734.6107 | 765906.6627 | 11915334.6107 | 1077996.7229 | 4025000 | 364147.2901 | 16373929.5307 | 1481371.9423 | 153975.36 | 13930.3628 | 60672.15 | 5489.0929 | 214647.51 | 19419.4557 | 2684606 | 242880 | 48634.1667 | 4400 | 2733240.1667 | 247280 | 2947887.6767 | 266699.4557 | 556380 | 50336.4644 | 3350644 | 303137.3746 | 170005 | 15380.5864 | 48015 | 4343.9831 | 537056.6667 | 48588.2559 | 42680 | 3861.3183 | 1057300 | 95655.3863 | 5762080.6667 | 521303.369 | 3017385.2854 | 272987 | 1508875.0208 | 136510 | 201811.1221 | 18258.13 | 85166.9368 | 7705.17 | 3219196.4076 | 291245.13 | 1594041.9576 | 144215.17 | 5016.9459 | 453.89 | 9900 | 895.6666 | 14916.9459 | 1349.5566 | 0 | 0 | 25370123.5508 | 2295269.9979 | 4541929.6343 | 410914.6257 | 11053219.697 | 29429476.0254 | 36423343.2478 | 33971405.6597
524-50R | oh | 3 | 9.9782 | 9.9782 | 9.3718 | 9.3718 | 12.2822 | 41785.15 | 4458.6139 | 80052.5 | 8541.8669 | 75735 | 8081.1754 | 200533.9286 | 21397.6344 | 398106.5786 | 42479.2906 | 3157000 | 336862.3568 | 5772814.0938 | 615978.3848 | 1974844.8133 | 210722.4828 | 7747658.9071 | 826700.8676 | 10904658.9071 | 1163563.2243 | 3650000 | 389467.0897 | 14952765.4857 | 1595509.6046 | 140914.95 | 15036.0919 | 56548.8 | 6033.9443 | 197463.75 | 21070.0362 | 2276218 | 242880 | 41235.8333 | 4400 | 2317453.8333 | 247280 | 2514917.5833 | 268350.0362 | 487080 | 51973.0493 | 2933304 | 312993.2526 | 148830 | 15880.654 | 46035 | 4912.087 | 514910 | 54942.6025 | 40920 | 4366.2995 | 1013700 | 108165.1476 | 5184779 | 553233.0926 | 2558374.1896 | 272987 | 1279341.7292 | 136510 | 171113.6573 | 18258.394 | 72211.3666 | 7705.192 | 2729487.8468 | 291245.394 | 1351553.0958 | 144215.192 | 4253.7574 | 453.89 | 9900 | 1056.3628 | 14153.7574 | 1510.2528 | 0 | 0 | 22881186.0899 | 2441498.344 | 3866470.6791 | 412565.2282 | 9371780.303 | 24564373.3639 | 32252966.3929 | 28430844.043
524-69R | oh | 3 | 33.3411 | 33.3411 | 30.7532 | 30.7532 | 0.31972 | 129635.88 | 4215.3596 | 248358 | 8075.8373 | 222062.5 | 7220.7887 | 622144.2857 | 20230.2163 | 1222200.6657 | 39742.2019 | 9794400 | 318483.7261 | 17909803.725 | 582371.6639 | 6126835.616 | 199225.8266 | 24036639.341 | 781597.4905 | 33831039.341 | 1100081.2167 | 10800000 | 351182.7414 | 45853240.0067 | 1491006.16 | 437180.04 | 14215.7486 | 167290.2 | 5439.7621 | 604470.24 | 19655.5107 | 7469342 | 242880 | 135314.1667 | 4400 | 7604656.1667 | 247280 | 8209126.4067 | 266935.5107 | 1665180 | 54146.5257 | 10028084 | 326082.4102 | 508805 | 16544.7717 | 150480 | 4893.1462 | 1683146.6667 | 54730.7463 | 133760 | 4349.4633 | 3313600 | 107748.0678 | 17483055.6667 | 568495.1312 | 8395229.1854 | 272987 | 4198122.0208 | 136510 | 560352.5402 | 18220.939 | 236747.6957 | 7698.306 | 8955581.7256 | 291207.939 | 4434869.7165 | 144208.306 | 13958.5789 | 453.89 | 9900 | 321.9175 | 23858.5789 | 775.8075 | 0 | 0 | 72315735.9778 | 2351485.0377 | 12643996.1232 | 411143.8167 | 30753219.697 | 639433.0084 | 103068955.6748 | 13283429.1316
540-241R | oh | 2 | 7.5598 | 6.6576 | 1.2638 | 1.2638 | 1.8921 | 3872.77 | 3064.3227 | 7419.5 | 5870.6669 | 467.5 | 369.9086 | 18586.0714 | 14706.1977 | 30345.8414 | 24011.0959 | 292600 | 231519.2567 | 535041.3063 | 423350.5315 | 183034.3973 | 144825.6583 | 718075.7036 | 568176.1899 | 1010675.7036 | 799695.4466 | 0 | 0 | 1041021.545 | 823706.5424 | 13060.41 | 10334.0274 | 50069.25 | 39617.2097 | 63129.66 | 49951.237 | 306958 | 242880 | 5560.8333 | 4400 | 312518.8333 | 247280 | 375648.4933 | 297231.237 | 60390 | 47783.4857 | 363682 | 287762.7694 | 18452.5 | 14600.5095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 442524.5 | 350146.7646 | 345008.0021 | 272987 | 172524.8542 | 136510 | 20502.8064 | 16222.811 | 11744.4939 | 9292.811 | 365510.8085 | 289209.811 | 184269.3481 | 145802.811 | 573.6379 | 453.89 | 9900 | 7833.3583 | 10473.6379 | 8287.2483 | 0 | 0 | 1859530.4914 | 1471350.3663 | 559917.8414 | 443034.048 | 1263825.7576 | 3784175.3524 | 3123356.2489 | 4344093.1938
597-595 | oh | 2 | 43.1902 | 40.4116 | 17.4087 | 17.4087 | 21.3882 | 73378.8 | 4215.0619 | 140580 | 8075.2671 | 131835 | 7572.9324 | 352157.1429 | 20228.7878 | 697950.9429 | 40092.0492 | 5544000 | 318461.2372 | 10137624.75 | 582330.5411 | 3468020.16 | 199211.7588 | 13605644.91 | 781542.2999 | 19149644.91 | 1100003.5371 | 6275000 | 360451.707 | 26122595.8529 | 1500547.2933 | 247460.4 | 14214.7448 | 179660.25 | 10320.1345 | 427120.65 | 24534.8793 | 4228228 | 242880 | 76598.3333 | 4400 | 4304826.3333 | 247280 | 4731946.9833 | 271814.8793 | 1986930 | 114134.2327 | 11965734 | 687341.7124 | 607117.5 | 34874.3489 | 57420 | 3298.3485 | 642253.3333 | 36892.6391 | 51040 | 2931.8654 | 1264400 | 72630.3009 | 16574894.8333 | 952103.4479 | 4752352.0958 | 272987 | 2376463.2917 | 136510 | 288128.6522 | 16550.831 | 128898.7179 | 7404.265 | 5040480.7481 | 289537.831 | 2505362.0095 | 143914.265 | 7901.6403 | 453.89 | 9900 | 568.6808 | 17801.6403 | 1022.5708 | 0 | 0 | 47755773.0746 | 2743211.1429 | 7237308.9929 | 415729.1443 | 17408712.1212 | 42776330.5981 | 65164485.1958 | 50013639.5909
599-19R | oh | 2 | 32.5496 | 32.5496 | 27.9549 | 27.9549 | 36.6728 | 129024.39 | 4615.4441 | 247186.5 | 8842.3241 | 238425 | 8528.9088 | 619209.6429 | 22150.2887 | 1233845.5329 | 44136.9657 | 9748200 | 348711.3725 | 17825323.5188 | 637645.2093 | 6097935.448 | 218134.5725 | 23923258.9667 | 855779.7817 | 33671458.9667 | 1204491.1542 | 10450000 | 373816.073 | 45355304.4996 | 1622444.1929 | 435117.87 | 15564.9812 | 154920.15 | 5541.7839 | 590038.02 | 21106.7651 | 6789692 | 242880 | 123001.6667 | 4400 | 6912693.6667 | 247280 | 7502731.6867 | 268386.7651 | 2478960 | 88677.0423 | 14928848 | 534032.8548 | 757460 | 27095.7629 | 99000 | 3541.4154 | 1107333.3333 | 39611.3874 | 88000 | 3147.9248 | 2180000 | 77982.6832 | 21639601.3333 | 774089.0709 | 7631330.9042 | 272987 | 3816126.7083 | 136510 | 425344.6834 | 15215.376 | 200394.3153 | 7168.48 | 8056675.5876 | 288202.376 | 4016521.0237 | 143678.48 | 12688.4606 | 453.89 | 9900 | 354.1415 | 22588.4606 | 808.0315 | 0 | 0 | 75074169.8811 | 2685543.6713 | 11519252.7103 | 412065.2451 | 27954924.2424 | 73345638.1282 | 103029094.1235 | 84864890.8385
67-24R | oh | 3 | 14.0055 | 14.0055 | 13.6102 | 13.6102 | 17.1035 | 57072.4 | 4193.3466 | 109340 | 8033.6645 | 100512.5 | 7385.0714 | 273900 | 20124.5721 | 540824.9 | 39736.6546 | 4312000 | 316820.5728 | 7884819.25 | 579330.4617 | 2697349.0133 | 198185.4498 | 10582168.2633 | 777515.9115 | 14894168.2633 | 1094336.4842 | 4525000 | 332470.5686 | 19959993.1633 | 1466543.7074 | 192469.2 | 14141.5126 | 65384.55 | 4804.0748 | 257853.75 | 18945.5874 | 3305652 | 242880 | 59885 | 4400 | 3365537 | 247280 | 3623390.75 | 266225.5874 | 582120 | 42770.7773 | 3505656 | 257575.1257 | 177870 | 13068.8486 | 71775 | 5273.6077 | 802816.6667 | 58986.2793 | 63800 | 4687.6513 | 1580500 | 116125.908 | 6784537.6667 | 498488.1979 | 3715415.1125 | 272987 | 1857932.125 | 136510 | 259561.8012 | 19071.085 | 106801.6038 | 7847.158 | 3974976.9137 | 292058.085 | 1964733.7288 | 144357.158 | 6177.5461 | 453.89 | 9900 | 727.3942 | 16077.5461 | 1181.2842 | 0 | 0 | 30735585.2897 | 2258271.2745 | 5588124.4788 | 410582.7454 | 13610227.2727 | 34207066.8946 | 44345812.5625 | 39795191.3735
67-34R | oh | 3 | 20.7557 | 20.7557 | 20.3064 | 20.3064 | 25.6646 | 90908.18 | 4476.8154 | 174163 | 8576.7375 | 167365 | 8241.9668 | 436283.5714 | 21484.9863 | 868719.7514 | 42780.506 | 6868400 | 338237.5347 | 12559390.6625 | 618493.0021 | 4296491.6427 | 211582.7181 | 16855882.3052 | 830075.7202 | 23724282.3052 | 1168313.255 | 7125000 | 350873.9204 | 31718002.0566 | 1561967.6813 | 306575.94 | 15097.474 | 107796.15 | 5308.4713 | 414372.09 | 20405.9452 | 4932028 | 242880 | 89348.3333 | 4400 | 5021376.3333 | 247280 | 5435748.4233 | 267685.9452 | 1255320 | 61818.814 | 7559816 | 372286.6355 | 383570 | 18889.0821 | 116325 | 5728.4784 | 1301116.6667 | 64074.092 | 103400 | 5091.9808 | 2561500 | 126142.2522 | 13281047.6667 | 654031.335 | 5543393.9708 | 272987 | 2772032.0417 | 136510 | 387148.3387 | 19065.299 | 159329.0752 | 7846.234 | 5930542.3095 | 292052.299 | 2931361.1169 | 144356.234 | 9216.8898 | 453.89 | 9900 | 487.5301 | 19116.8898 | 941.4201 | 0 | 0 | 50948708.9225 | 2508992.7355 | 8367109.5402 | 412042.1792 | 20306439.3939 | 51329120.5846 | 71255148.3165 | 59696230.1248
67-37R | oh | 3 | 8.7947 | 8.7947 | 8.2782 | 8.2782 | 11.7501 | 33020.46 | 3988.8359 | 63261 | 7641.8605 | 64982.5 | 7849.8158 | 158470.7143 | 19143.0912 | 319734.6743 | 38623.6034 | 2494800 | 301369.1459 | 4561931.1375 | 551076.3551 | 1560609.072 | 188519.8906 | 6122540.2095 | 739596.2458 | 8617340.2095 | 1040965.3917 | 2750000 | 332197.0304 | 11687074.8838 | 1411786.0254 | 111357.18 | 13451.8271 | 32986.8 | 3984.7698 | 144343.98 | 17436.5969 | 2010614 | 242880 | 36424.1667 | 4400 | 2047038.1667 | 247280 | 2191382.1467 | 264716.5969 | 209880 | 25353.2774 | 1263944 | 152683.0703 | 64130 | 7746.8347 | 35640 | 4305.2735 | 398640 | 48155.2815 | 31680 | 3826.9098 | 784800 | 94802.9925 | 2788714 | 336873.6398 | 2259846.3604 | 272987 | 1130059.7708 | 136510 | 158165.9338 | 19106.274 | 65013.4951 | 7853.56 | 2418012.2942 | 292093.274 | 1195073.2659 | 144363.56 | 3757.4011 | 453.89 | 9900 | 1195.9093 | 13657.4011 | 1649.7993 | 0 | 0 | 16907458.5791 | 2042402.7385 | 3386455.4126 | 409080.1569 | 8278219.697 | 23500122.7899 | 25185678.2761 | 26886578.2025
67-45R | oh | 3 | 10.8966 | 10.8966 | 10.2424 | 10.2424 | 12.9696 | 40562.17 | 3960.2119 | 77709.5 | 7587.0222 | 74332.5 | 7257.3151 | 194664.6429 | 19005.7196 | 387268.8129 | 37810.2687 | 3064600 | 299206.5089 | 5603853.6813 | 547121.8091 | 1917044.4773 | 187167.0644 | 7520898.1586 | 734288.8735 | 10585498.1586 | 1033495.3823 | 3100000 | 302662.7219 | 14072766.9714 | 1373968.373 | 136790.61 | 13355.2962 | 47124 | 4600.8639 | 183914.61 | 17956.1601 | 2487680 | 242880 | 45066.6667 | 4400 | 2532746.6667 | 247280 | 2716661.2767 | 265236.1601 | 315810 | 30833.5207 | 1901878 | 185686.3136 | 96497.5 | 9421.3536 | 48015 | 4687.855 | 537056.6667 | 52434.5266 | 42680 | 4166.9822 | 1057300 | 103227.5148 | 3999237.1667 | 390458.0666 | 2796048.6667 | 272987 | 1398193.3333 | 136510 | 195626.5133 | 19099.63 | 80426.1987 | 7852.262 | 2991675.18 | 292086.63 | 1478619.532 | 144362.262 | 4648.9339 | 453.89 | 9900 | 966.568 | 14548.9339 | 1420.458 | 0 | 0 | 21078228.252 | 2057933.5276 | 4195280.8087 | 409598.4221 | 10242424.2424 | 25939221.1138 | 31320652.4945 | 30134501.9225
73-1130R | oh | 3 | 12.3602 | 12.3602 | 12.0396 | 12.0396 | 16.5975 | 47696.22 | 3961.6172 | 91377 | 7589.7145 | 21037.5 | 1747.3611 | 228902.1429 | 19012.4638 | 389012.8629 | 32311.1566 | 3603600 | 299312.6839 | 6589456.0875 | 547315.9581 | 2254213.104 | 187233.4816 | 8843669.1915 | 734549.4397 | 12447269.1915 | 1033862.1235 | 925000 | 76829.9014 | 13761282.0544 | 1143003.1815 | 160849.26 | 13360.0354 | 55959.75 | 4647.9806 | 216809.01 | 18008.0161 | 2924174 | 242880 | 52974.1667 | 4400 | 2977148.1667 | 247280 | 3193957.1767 | 265288.0161 | 270270 | 22448.4513 | 1627626 | 135189.5622 | 82582.5 | 6859.249 | 59895 | 4974.8399 | 669936.6667 | 55644.506 | 53240 | 4422.0799 | 1318900 | 109546.9804 | 4082450.1667 | 339085.6688 | 3286649.7354 | 272987 | 1643523.5208 | 136510 | 234044.1063 | 19439.552 | 95253.9086 | 7911.728 | 3520693.8417 | 292426.552 | 1738777.4294 | 144421.728 | 5464.6465 | 453.89 | 9900 | 822.2876 | 15364.6465 | 1276.1776 | 0 | 0 | 21379790.7092 | 1775791.5799 | 4932734.6061 | 409709.7441 | 12039583.3333 | 33195041.8445 | 33419374.0425 | 38127776.4506
73-1163 | oh | 3 | 13.4284 | 13.4284 | 11.278 | 11.278 | 7.9236 | 49734.52 | 4409.8587 | 95282 | 8448.4611 | 45347.5 | 4020.8706 | 238684.2857 | 21163.65 | 429048.3057 | 38042.8403 | 3757600 | 333178.7466 | 6871056.775 | 609242.624 | 2350546.9973 | 208418.2197 | 9221603.7723 | 817660.8437 | 12979203.7723 | 1150839.5902 | 1975000 | 175119.2315 | 15383252.078 | 1364001.6621 | 167723.16 | 14871.6713 | 45945.9 | 4073.9295 | 213669.06 | 18945.6008 | 2739208 | 242880 | 49623.3333 | 4400 | 2788831.3333 | 247280 | 3002500.3933 | 266225.6008 | 799920 | 70927.2788 | 4817296 | 427139.8348 | 244420 | 21672.2241 | 59895 | 5310.7678 | 669936.6667 | 59401.9211 | 53240 | 4720.6825 | 1318900 | 116944.1795 | 7963607.6667 | 706116.8886 | 3078755.6583 | 272987 | 1539563.9167 | 136510 | 219535.8597 | 19465.798 | 89281.3089 | 7916.392 | 3298291.518 | 292452.798 | 1628845.2255 | 144426.392 | 5118.9852 | 453.89 | 9900 | 877.8129 | 15018.9852 | 1331.7029 | 0 | 0 | 26660170.2479 | 2363903.0515 | 4631345.6189 | 410651.9928 | 11278030.303 | 15847185.7239 | 37938200.551 | 20478531.3428
73-1164 | oh | 3 | 1.9093 | 1.9093 | 1.2322 | 1.2322 | 0.34441 | 6930.22 | 5624.2794 | 13277 | 10775.063 | 4207.5 | 3414.6326 | 33259.2857 | 26991.8581 | 57674.0057 | 46805.8331 | 523600 | 424932.0627 | 957442.3375 | 777020.526 | 327535.2373 | 265814.026 | 1284977.5748 | 1042834.552 | 1808577.5748 | 1467766.6147 | 175000 | 142022.7482 | 2041251.5805 | 1656595.196 | 23371.26 | 18967.1461 | 8835.75 | 7170.7286 | 32207.01 | 26137.8747 | 299276 | 242880 | 5421.6667 | 4400 | 304697.6667 | 247280 | 336904.6767 | 273417.8747 | 227700 | 184791.8844 | 1371260 | 1112857.7928 | 69575 | 56464.1869 | 9900 | 8034.4298 | 110733.3333 | 89866.5847 | 8800 | 7141.7153 | 218000 | 176919.7664 | 2015968.3333 | 1636076.3603 | 336373.7542 | 272987 | 168207.2083 | 136510 | 24042.6113 | 19511.987 | 9764.9367 | 7924.818 | 360416.3654 | 292498.987 | 177972.1451 | 144434.818 | 559.2819 | 453.89 | 9900 | 8034.4298 | 10459.2819 | 8488.3198 | 0 | 0 | 4428095.5612 | 3593658.8631 | 514876.8217 | 417852.6927 | 1232196.9697 | 688825 | 5660292.5309 | 1203701.8217
73-23R | oh | 3 | 8.6273 | 8.6273 | 8.2208 | 8.2208 | 11.2258 | 32408.97 | 3942.2974 | 62089.5 | 7552.7015 | 6077.5 | 739.2803 | 155536.0714 | 18919.7451 | 256112.0414 | 31154.0243 | 2448600 | 297853.0157 | 4477450.9313 | 544646.8441 | 1531708.904 | 186320.3938 | 6009159.8352 | 730967.2379 | 8457759.8352 | 1028820.2537 | 225000 | 27369.4881 | 8938871.8767 | 1087343.766 | 109295.01 | 13294.8821 | 32397.75 | 3940.9326 | 141692.76 | 17235.8147 | 1996676 | 242880 | 36171.6667 | 4400 | 2032847.6667 | 247280 | 2174540.4267 | 264515.8147 | 243540 | 29624.7339 | 1466652 | 178406.7309 | 74415 | 9052.002 | 35640 | 4335.3269 | 398640 | 48491.4344 | 31680 | 3853.6239 | 784800 | 95464.7745 | 3035367 | 369228.6265 | 2244180.6292 | 272987 | 1122225.9583 | 136510 | 160534.6494 | 19527.783 | 65169.3163 | 7927.337 | 2404715.2786 | 292514.783 | 1187395.2746 | 144437.337 | 3731.354 | 453.89 | 9900 | 1204.2575 | 13631.354 | 1658.1475 | 0 | 0 | 14392585.5093 | 1750745.323 | 3361935.7013 | 408953.1517 | 8220833.3333 | 22451676.4918 | 22613418.8426 | 25813612.1931
73-678R | oh | 3 | 15.8364 | 15.8364 | 14.1729 | 14.1729 | 1.7812 | 55237.93 | 3897.4285 | 105825.5 | 7466.7411 | 86487.5 | 6102.3078 | 265096.0714 | 18704.4119 | 512647.0014 | 36170.8894 | 4173400 | 294463.031 | 7631378.6312 | 538447.9999 | 2610648.5093 | 184199.8066 | 10242027.1406 | 722647.8065 | 14415427.1406 | 1017110.8375 | 4600000 | 324562.6929 | 19528074.142 | 1377844.4198 | 186282.69 | 13143.5677 | 62439.3 | 4405.5364 | 248721.99 | 17549.1041 | 3442318 | 242880 | 62360.8333 | 4400 | 3504678.8333 | 247280 | 3753400.8233 | 264829.1041 | 538560 | 37999.2356 | 3243328 | 228839.8412 | 164560 | 11610.8776 | 59400 | 4191.0922 | 664400 | 46878.142 | 52800 | 3725.4153 | 1308000 | 92288.6962 | 6031048 | 425533.3 | 3869022.0021 | 272987 | 1934744.8542 | 136510 | 276445.1065 | 19505.167 | 112301.1036 | 7923.641 | 4145467.1085 | 292492.167 | 2047045.9578 | 144433.641 | 6432.9451 | 453.89 | 9900 | 698.5154 | 16332.9451 | 1152.4054 | 0 | 0 | 29720922.1957 | 2097022.2922 | 5800446.7811 | 409262.7451 | 14172916.6667 | 3562482.9545 | 43893838.8624 | 9362929.7356
73-683R | oh | 3 | 14.3095 | 14.3095 | 10.907 | 10.907 | 1.4771 | 46269.41 | 4242.1727 | 88643.5 | 8127.2062 | 48620 | 4457.6846 | 222054.6429 | 20358.8969 | 405587.5529 | 37185.9605 | 3495800 | 320509.5418 | 6392335.6063 | 586076.0215 | 2186779.3787 | 200493.065 | 8579114.9849 | 786569.0865 | 12074914.9849 | 1107078.6282 | 2175000 | 199413.0824 | 14655502.5378 | 1343677.6711 | 156037.53 | 14306.1723 | 51247.35 | 4698.571 | 207284.88 | 19004.7434 | 2649094 | 242880 | 47990.8333 | 4400 | 2697084.8333 | 247280 | 2904369.7133 | 266284.7434 | 480150 | 44022.157 | 2891570 | 265111.2122 | 146712.5 | 13451.2146 | 55935 | 5128.3544 | 625643.3333 | 57361.5934 | 49720 | 4558.5372 | 1231700 | 112927.3993 | 5481430.8333 | 502560.4681 | 2977471.2771 | 272987 | 1488915.6042 | 136510 | 212928.7288 | 19522.195 | 86448.6476 | 7925.973 | 3190400.0058 | 292509.195 | 1575364.2517 | 144435.973 | 4950.5817 | 453.89 | 9900 | 907.6733 | 14850.5817 | 1361.5633 | 0 | 0 | 23342183.9586 | 2140108.8976 | 4479733.9651 | 410720.7164 | 10907007.5758 | 2954103.5407 | 34249191.5344 | 7433837.5058
75-2259F | oh | 3 | 6.4811 | 6.4811 | 4.3316 | 4.3316 | 5.737 | 21198.32 | 4893.845 | 40612 | 9375.688 | 40672.5 | 9389.655 | 101734.2857 | 23486.3814 | 204217.1057 | 47145.5694 | 1601600 | 369745.4418 | 2928647.15 | 676107.6014 | 1001872.4907 | 231292.3244 | 3930519.6407 | 907399.9258 | 5532119.6407 | 1277145.3676 | 2225000 | 513663.5914 | 7961336.7464 | 1837954.5285 | 71488.56 | 16503.8519 | 28274.4 | 6527.4291 | 99762.96 | 23031.281 | 1052066 | 242880 | 19059.1667 | 4400 | 1071125.1667 | 247280 | 1170888.1267 | 270311.281 | 405900 | 93706.0907 | 2444420 | 564318.9017 | 124025 | 28632.4166 | 21285 | 4913.856 | 238076.6667 | 54962.3891 | 18920 | 4367.872 | 468700 | 108204.1013 | 3721326.6667 | 859105.6272 | 1182478.3479 | 272987 | 591310.6458 | 136510 | 60744.6136 | 14023.504 | 30142.0721 | 6958.6 | 1243222.9615 | 287010.504 | 621452.7179 | 143468.6 | 1966.083 | 453.89 | 9900 | 2285.5144 | 11866.083 | 2739.4044 | 0 | 0 | 12937752.4576 | 2986810.0641 | 1792340.8446 | 413779.881 | 4331628.7879 | 11473981.3673 | 17269381.2455 | 13266322.2119
75-32R | oh | 3 | 4.6873 | 4.6873 | 2.4445 | 2.4445 | 3.312 | 13452.78 | 5503.2679 | 25773 | 10543.2277 | 25712.5 | 10518.4783 | 64562.1429 | 26411.1036 | 129500.4229 | 52976.0775 | 1016400 | 415789.2616 | 1858564.5375 | 760302.2203 | 635803.696 | 260094.7947 | 2494368.2335 | 1020397.015 | 3510768.2335 | 1436186.2767 | 1400000 | 572712.4816 | 5040268.6564 | 2061874.8358 | 45367.74 | 18559.0507 | 28863.45 | 11807.4701 | 74231.19 | 30366.5207 | 593722 | 242880 | 10755.8333 | 4400 | 604477.8333 | 247280 | 678709.0233 | 277646.5207 | 203940 | 83427.8454 | 1228172 | 502421.0243 | 62315 | 25491.8416 | 11880 | 4859.8745 | 132880 | 54358.5961 | 10560 | 4319.8884 | 261600 | 107015.418 | 1911347 | 781894.4883 | 667318.7896 | 272987 | 333699.7292 | 136510 | 34280.1584 | 14023.339 | 17010.3235 | 6958.589 | 701598.948 | 287010.339 | 350710.0527 | 143468.589 | 1109.5375 | 453.89 | 9900 | 4049.8954 | 11009.5375 | 4503.7854 | 0 | 0 | 7664224.1419 | 3135283.4485 | 1029419.076 | 421115.1097 | 2444507.5758 | 6624070.3256 | 10108731.7177 | 7653489.4016
75-41 | oh | 3 | 2.9212 | 2.9212 | 2.6098 | 2.6098 | 3.5837 | 12229.8 | 4686.0192 | 23430 | 8977.5327 | 25245 | 9672.9753 | 58692.8571 | 22488.9903 | 119597.6571 | 45825.5174 | 924000 | 354043.5414 | 1689604.125 | 647395.4848 | 578003.36 | 221470.0828 | 2267607.485 | 868865.5675 | 3191607.485 | 1222909.1089 | 1375000 | 526850.508 | 4686205.1421 | 1795585.1343 | 41243.4 | 15802.9864 | 7068.6 | 2708.4331 | 48312 | 18511.4194 | 633880 | 242880 | 11483.3333 | 4400 | 645363.3333 | 247280 | 693675.3333 | 265791.4194 | 94050 | 36036.5747 | 566390 | 217020.2612 | 28737.5 | 11011.1756 | 5445 | 2086.328 | 60903.3333 | 23335.9652 | 4840 | 1854.5138 | 119900 | 45941.3643 | 880265.8333 | 337286.1829 | 712454.7083 | 272987 | 356270.4167 | 136510 | 36598.8762 | 14023.372 | 18160.9204 | 6958.611 | 749053.5845 | 287010.372 | 374431.337 | 143468.611 | 1184.5841 | 453.89 | 9900 | 3793.3237 | 11084.5841 | 4247.2137 | 0 | 0 | 6326609.1441 | 2424128.9028 | 1068106.6704 | 409260.0304 | 2609848.4848 | 7167473.9646 | 8936457.629 | 8235580.635
75-996R | oh | 2 | 11.6598 | 11.3888 | 10.6383 | 10.9093 | 10.4953 | 51365.16 | 4708.3913 | 98406 | 9020.3934 | 80410 | 7370.7887 | 240640.7143 | 22058.3492 | 470821.8743 | 43157.9225 | 3880800 | 355733.8241 | 7096337.325 | 650486.295 | 2427614.112 | 222527.4303 | 9523951.437 | 873013.7252 | 13404751.437 | 1228747.5493 | 4825000 | 442283.9881 | 18700573.3113 | 1714189.46 | 173222.28 | 15878.4333 | 51836.4 | 4751.5875 | 225058.68 | 20630.0208 | 2649646 | 242880 | 48000.8333 | 4400 | 2697646.8333 | 247280 | 2922705.5133 | 267910.0208 | 830610 | 76137.9282 | 5002118 | 458519.5229 | 253797.5 | 23264.3669 | 32670 | 2994.698 | 365420 | 33496.2518 | 29040 | 2661.9538 | 719400 | 65943.8551 | 7233055.5 | 663018.5768 | 2904106.0208 | 266205.097 | 1452228.5417 | 133118.6386 | 149182.137 | 13674.7918 | 74027.8472 | 6785.7682 | 3053288.1579 | 279879.8888 | 1526256.3889 | 139904.4068 | 4951.6132 | 453.89 | 9900 | 907.4842 | 14851.6132 | 1361.3742 | 0 | 0 | 29001768.5824 | 2658449.2998 | 4448961.9022 | 407814.4276 | 10909280.303 | 20990687.9124 | 39911048.8854 | 25439649.8146
770-259R | oh | 2 | 1.5089 | 1.3913 | 1.3913 | 1.5089 | 2.2313 | 5095.75 | 3377.1256 | 9762.5 | 6469.9385 | 11687.5 | 7745.701 | 21520.7143 | 14262.5043 | 48066.4643 | 31855.2694 | 385000 | 255152.5041 | 704001.7188 | 466565.718 | 240834.7333 | 159609.3124 | 944836.4521 | 626175.0304 | 1329836.4521 | 881327.5345 | 525000 | 347935.2328 | 1902902.9164 | 1261118.0367 | 17184.75 | 11388.9143 | 1767.15 | 1171.15 | 18951.9 | 12560.0643 | 366482 | 242880 | 6639.1667 | 4400 | 373121.1667 | 247280 | 392073.0667 | 259840.0643 | 19800 | 13122.1288 | 119240 | 79024.3755 | 6050 | 4009.5393 | 990 | 656.1064 | 11073.3333 | 7338.672 | 880 | 583.2057 | 21800 | 14447.5963 | 179833.3333 | 119181.6242 | 379803.5042 | 251708.6108 | 189924.7083 | 125869.5193 | 19511.1137 | 12930.6741 | 9681.5689 | 6416.3027 | 399314.6179 | 264639.2849 | 199606.2772 | 132285.822 | 684.8753 | 453.89 | 9900 | 6561.0644 | 10584.8753 | 7014.9544 | 0 | 0 | 2492635.7429 | 1651953.9002 | 591679.3439 | 392125.8862 | 1508901.5152 | 4462592.378 | 4001537.2581 | 5054271.7219
78-26R | oh | 3 | 6.6301 | 6.6301 | 6.3703 | 6.3703 | 7.3173 | 29351.52 | 4607.5821 | 56232 | 8827.2621 | 15895 | 2495.1866 | 140862.8571 | 22112.5579 | 242341.3771 | 38042.5887 | 2217600 | 348117.3777 | 4055049.9 | 636559.0448 | 1387208.064 | 217763.0022 | 5442257.964 | 854322.047 | 7659857.964 | 1202439.4247 | 675000 | 105961.0525 | 8577199.3411 | 1346443.0659 | 98984.16 | 15538.4678 | 34753.95 | 5455.652 | 133738.11 | 20994.1198 | 1547210 | 242880 | 28029.1667 | 4400 | 1575239.1667 | 247280 | 1708977.2767 | 268274.1198 | 481140 | 75529.0382 | 2897532 | 454852.6523 | 147015 | 23078.3172 | 44055 | 6915.7247 | 492763.3333 | 77353.6614 | 39160 | 6147.3108 | 970100 | 152285.6548 | 5071765.3333 | 796162.3594 | 1738999.5729 | 272987 | 869604.8958 | 136510 | 152097.1196 | 23876.105 | 55366.9939 | 8691.474 | 1891096.6926 | 296863.105 | 924971.8898 | 145201.474 | 2891.3996 | 453.89 | 9900 | 1554.0954 | 12791.3996 | 2007.9854 | 0 | 0 | 15552852.7667 | 2441476.5158 | 2633949.1664 | 413475.5938 | 6370265.1515 | 14634515.3676 | 21923117.9182 | 17268464.534
78-35R | oh | 3 | 1.532 | 1.532 | 1.532 | 1.532 | 1.5849 | 6114.9 | 3991.4293 | 11715 | 7646.829 |  |  | 29346.4286 | 19155.5375 | 47176.3286 | 30793.7959 | 462000 | 301565.0884 | 844802.0625 | 551434.6508 | 289001.68 | 188642.4614 | 1133803.7425 | 740077.1122 | 1595803.7425 | 1041642.2006 | 0 | 0 | 1642980.0711 | 1072435.9964 | 20621.7 | 13460.5731 | 0 | 0 | 20621.7 | 13460.5731 | 372094 | 242880 | 6740.8333 | 4400 | 378834.8333 | 247280 | 399456.5333 | 260740.5731 | 0 | 0 | 0 | 0 | 0 | 0 | 990 | 646.2109 | 11073.3333 | 7227.9886 | 880 | 574.4097 | 21800 | 14229.6946 | 34743.3333 | 22678.3039 | 418218.1521 | 272987 | 209134.3542 | 136510 |  |  |  |  | 418218.1521 | 272987 | 209134.3542 | 136510 | 695.3629 | 453.89 | 9900 | 6462.109 | 10595.3629 | 6915.999 | 0 | 0 | 2106536.9194 | 1375017.2994 | 608590.8875 | 397250.5731 | 1532007.5758 | 3169899.6076 | 3638544.4952 | 3778490.4951
78-782R | oh | 3 | 1.7807 | 1.7807 | 1.7152 | 1.7152 | 1.2654 | 6930.22 | 4040.5876 | 13277 | 7741.0071 | 7480 | 4361.1307 | 33259.2857 | 19391.4563 | 60946.5057 | 35534.1818 | 523600 | 305279.1519 | 957442.3375 | 558226.0978 | 327535.2373 | 190965.7744 | 1284977.5748 | 749191.8723 | 1808577.5748 | 1054471.0242 | 225000 | 131183.7456 | 2094524.0805 | 1221188.9516 | 23371.26 | 13626.353 | 8835.75 | 5151.5857 | 32207.01 | 18777.9387 | 416576 | 242880 | 7546.6667 | 4400 | 424122.6667 | 247280 | 456329.6767 | 266057.9387 | 33660 | 19625.0883 | 202708 | 118186.6431 | 10285 | 5996.5548 | 7920 | 4617.6678 | 88586.6667 | 51649.47 | 7040 | 4104.5936 | 174400 | 101681.9788 | 524599.6667 | 305861.9965 | 468214.0667 | 272987 | 234135.3333 | 136510 | 41392.4479 | 24133.406 | 14985.1519 | 8736.926 | 509606.5145 | 297120.406 | 249120.4852 | 145246.926 | 778.4901 | 453.89 | 9900 | 5772.0848 | 10678.4901 | 6225.9748 | 0 | 0 | 3139408.7519 | 1830397.3288 | 705450.1619 | 411304.8647 | 1715151.5152 | 2530883.5925 | 4854560.267 | 3236333.7544
788-34R | oh | 2 | 24.1536 | 15.7254 | 6.2949 | 12.3557 | 15.4566 | 64614.11 | 5229.5058 | 123788.5 | 10018.751 | 124355 | 10064.6004 | 139884.6429 | 11321.4831 | 452642.2529 | 36634.3403 | 4881800 | 395105.6746 | 8926741.7937 | 722480.7117 | 3053784.4187 | 247156.2851 | 11980526.2124 | 969636.9969 | 16862326.2124 | 1364742.6715 | 1775000 | 143658.6039 | 19089968.4653 | 1545035.6157 | 217902.63 | 17635.824 | 150796.8 | 12204.6523 | 368699.43 | 29840.4763 | 3000948 | 242880 | 54365 | 4400 | 3055313 | 247280 | 3424012.43 | 277120.4763 | 1045440 | 84612.085 | 6295872 | 509552.7784 | 319440 | 25853.6926 | 41085 | 3325.1908 | 459543.3333 | 37192.8753 | 36520 | 2955.7252 | 904700 | 73221.374 | 9102600.3333 | 736713.7215 | 1718422.1437 | 139079.5076 | 859314.9375 | 69548.1601 | 99937.3578 | 8088.3726 | 45862.6284 | 3711.8654 | 1818359.5016 | 147167.8802 | 905177.5659 | 73260.0256 | 5608.1204 | 453.89 | 9900 | 801.2508 | 15508.1204 | 1255.1408 | 0 | 0 | 30026436.4206 | 2430172.3581 | 4329189.9959 | 350380.5018 | 12355681.8182 | 30913100.866 | 42382118.2388 | 35242290.8619
79-658R | oh | 3 | 9.486 | 9.486 | 9.3078 | 9.3078 | 13.1471 | 37912.38 | 4073.199 | 72633 | 7803.4844 | 15895 | 1707.7139 | 181947.8571 | 19547.9639 | 308388.2371 | 33132.3612 | 2864400 | 307743.0461 | 5237772.7875 | 562731.5153 | 1791810.416 | 192507.0505 | 7029583.2035 | 755238.5658 | 9893983.2035 | 1062981.6119 | 75000 | 8057.7882 | 10277371.4406 | 1104171.7612 | 127854.54 | 13736.3307 | 16493.4 | 1772.0043 | 144347.94 | 15508.335 | 2260670 | 242880 | 40954.1667 | 4400 | 2301624.1667 | 247280 | 2445972.1067 | 262788.335 | 535590 | 57542.2769 | 3225442 | 346532.3789 | 163652.5 | 17582.3624 | 20295 | 2180.4375 | 227003.3333 | 24388.597 | 18040 | 1938.1666 | 446900 | 48013.6738 | 4636922.8333 | 498177.8932 | 2540898.8854 | 272987 | 1270603.0208 | 136510 | 252026.0033 | 27076.962 | 86158.1472 | 9256.588 | 2792924.8887 | 300063.962 | 1356761.168 | 145766.588 | 4224.7015 | 453.89 | 9900 | 1063.628 | 14124.7015 | 1517.518 | 0 | 0 | 17721343.8642 | 1903931.1345 | 3802733.2747 | 408554.923 | 9307765.1515 | 26294108.8021 | 27029109.0157 | 30096842.0768
79-660R | oh | 3 | 7.2746 | 7.2746 | 7.2462 | 7.2462 | 9.0056 | 32612.8 | 4500.6687 | 62480 | 8622.436 | 46282.5 | 6387.1302 | 156514.2857 | 21599.4623 | 297889.5857 | 41109.6971 | 2464000 | 340039.7282 | 4505611 | 621788.4496 | 1541342.2933 | 212710.0708 | 6046953.2933 | 834498.5204 | 8510953.2933 | 1174538.2485 | 725000 | 100052.2739 | 9533842.879 | 1315700.2196 | 109982.4 | 15177.9162 | 8246.7 | 1138.0705 | 118229.1 | 16315.9866 | 1759960 | 242880 | 31883.3333 | 4400 | 1791843.3333 | 247280 | 1910072.4333 | 263595.9866 | 700920 | 96729.1584 | 4221096 | 582524.4872 | 214170 | 29556.1317 | 10395 | 1434.5426 | 116270 | 16045.6247 | 9240 | 1275.149 | 228900 | 31588.9179 | 5500991 | 759154.0115 | 1978121.7083 | 272987 | 989180.4167 | 136510 | 196182.3745 | 27073.783 | 67068.7438 | 9255.697 | 2174304.0829 | 300060.783 | 1056249.1605 | 145765.697 | 3288.9832 | 453.89 | 9900 | 1366.2311 | 13188.9832 | 1820.1211 | 0 | 0 | 17222326.9451 | 2376735.1351 | 2966321.5938 | 409361.6836 | 7246212.1212 | 18011204.8859 | 24468539.0664 | 20977526.4796
79-668R | oh | 3 | 11.8225 | 11.8225 | 7.4994 | 7.4994 | 8.625 | 42192.81 | 5626.1342 | 80833.5 | 10778.6166 | 34127.5 | 4550.6781 | 202490.3571 | 27000.7598 | 359644.1671 | 47956.1887 | 3187800 | 425072.2024 | 5829134.2313 | 777276.7821 | 1994111.592 | 265901.6897 | 7823245.8233 | 1043178.4718 | 11011045.8232 | 1468250.6742 | 425000 | 56670.9599 | 11795689.9904 | 1572877.8228 | 142289.73 | 18973.4014 | 57137.85 | 7618.9572 | 199427.58 | 26592.3586 | 1821462 | 242880 | 32997.5 | 4400 | 1854459.5 | 247280 | 2053887.08 | 273872.3586 | 392040 | 52275.9603 | 2360952 | 314817.4498 | 119790 | 15973.2101 | 42075 | 5610.425 | 470616.6667 | 62753.643 | 37400 | 4987.0445 | 926500 | 123542.6926 | 4349373.6667 | 579960.4253 | 2047247.3937 | 272987 | 1023747.4375 | 136510 | 197707.7385 | 26363.029 | 68472.4523 | 9130.352 | 2244955.1323 | 299350.029 | 1092219.8898 | 145640.352 | 3403.9171 | 453.89 | 9900 | 1320.1 | 13303.9171 | 1773.99 | 0 | 0 | 18403322.7064 | 2453962.2671 | 3146106.9698 | 419512.7106 | 7499431.8182 | 17249929.6057 | 25902754.5246 | 20396036.5755
79-676R | oh | 3 | 3.2491 | 3.2491 | 3.1771 | 3.1771 | 2.7499 | 16510.23 | 5196.6626 | 31630.5 | 9955.8295 | 1402.5 | 441.4426 | 79235.3571 | 24939.6534 | 128778.5871 | 40533.5881 | 1247400 | 392624.2623 | 2280965.5688 | 717943.261 | 780304.536 | 245604.0507 | 3061270.1047 | 963547.3117 | 4308670.1047 | 1356171.574 | 50000 | 15737.7049 | 4487448.6919 | 1412442.867 | 55678.59 | 17525.0644 | 17082.45 | 5376.7711 | 72761.04 | 22901.8355 | 771650 | 242880 | 13979.1667 | 4400 | 785629.1667 | 247280 | 858390.2067 | 270181.8355 | 285120 | 89742.6885 | 1717056 | 540450.4131 | 87120 | 27421.377 | 16830 | 5297.3115 | 188246.6667 | 59251.4098 | 14960 | 4708.7213 | 370600 | 116647.8689 | 2679932.6667 | 843519.7902 | 867302.4479 | 272987 | 433703.6458 | 136510 | 80383.4585 | 25301.023 | 28414.159 | 8943.473 | 947685.9064 | 298288.023 | 462117.8048 | 145453.473 | 1442.0464 | 453.89 | 9900 | 3116.0656 | 11342.0464 | 3569.9556 | 0 | 0 | 8126409.3113 | 2557820.6357 | 1320508.0115 | 415635.3085 | 3177083.3333 | 5499724.5811 | 11303492.6447 | 6820232.5926
79-679R | oh | 3 | 6.4354 | 6.4354 | 6.085 | 6.085 | 0 | 26701.73 | 4388.0959 | 51155.5 | 8406.7677 | 15895 | 2612.1448 | 128146.0714 | 21059.2069 | 221898.3014 | 36466.2153 | 2017400 | 331534.5015 | 3688969.0063 | 606235.9972 | 1261974.0027 | 207389.6708 | 4950943.0089 | 813625.668 | 6968343.0089 | 1145160.1695 | 775000 | 127361.5737 | 7965241.3103 | 1308987.9585 | 90048.09 | 14798.2793 | 31808.7 | 5227.3627 | 121856.79 | 20025.642 | 1477934 | 242880 | 26774.1667 | 4400 | 1504708.1667 | 247280 | 1626564.9567 | 267305.642 | 355410 | 58407.196 | 2140358 | 351741.1136 | 108597.5 | 17846.6432 | 29205 | 4799.4771 | 326663.3333 | 53683.0402 | 25960 | 4266.2019 | 643100 | 105685.4555 | 3629293.8333 | 596429.1276 | 1661136.2354 | 272987 | 830668.5208 | 136510 | 153188.7962 | 25174.666 | 54289.8439 | 8921.858 | 1814325.0316 | 298161.666 | 884958.3647 | 145431.858 | 2761.9378 | 453.89 | 9900 | 1626.9414 | 12661.9378 | 2080.8314 | 0 | 0 | 13421522.1131 | 2205659.5835 | 2511523.3214 | 412737.5 | 6085037.8788 | 0 | 19506559.9919 | 2511523.3214
79-685R | oh | 3 | 3.8049 | 3.8049 | 3.8049 | 3.8049 | 5.2582 | 13452.78 | 3535.6236 | 25773 | 6773.5908 |  |  | 64562.1429 | 16968.0495 | 103787.9229 | 27277.2639 | 1016400 | 267127.5261 | 1858564.5375 | 488462.9546 | 635803.696 | 167100.2247 | 2494368.2335 | 655563.1793 | 3510768.2335 | 922690.7055 | 0 | 0 | 3614556.1564 | 949967.9694 | 45367.74 | 11923.4279 | 2356.2 | 619.2502 | 47723.94 | 12542.6781 | 924140 | 242880 | 16741.6667 | 4400 | 940881.6667 | 247280 | 988605.6067 | 259822.6781 | 53460 | 14050.214 | 321948 | 84613.5112 | 16335 | 4293.121 | 1485 | 390.2837 | 16610 | 4365.3957 | 1320 | 346.9189 | 32700 | 8594.1264 | 443858 | 116653.5709 | 1038694.8542 | 272987 | 519410.2083 | 136510 | 139222.4862 | 36590.081 | 112854.3612 | 29660.081 | 1177917.3404 | 309577.081 | 632264.5696 | 166170.081 | 1727.0171 | 453.89 | 9900 | 2601.8915 | 11627.0171 | 3055.7815 | 0 | 0 | 5247958.5138 | 1379254.4028 | 1620870.1762 | 425992.7591 | 3804924.2424 | 10516312.6972 | 9052882.7562 | 12137182.8734
79-714R | oh | 3 | 4.6886 | 4.6886 | 4.585 | 4.585 | 6.1166 | 22013.64 | 4801.1904 | 42174 | 9198.1792 | 3740 | 815.6966 | 105647.1429 | 23041.7165 | 173574.7829 | 37856.7827 | 1663200 | 362745.0948 | 3041287.425 | 663306.9356 | 1040406.048 | 226913.294 | 4081693.473 | 890220.2296 | 5744893.473 | 1252965.3244 | 200000 | 43620.1413 | 6118468.2559 | 1334442.2484 | 74238.12 | 16191.3864 | 24151.05 | 5267.3611 | 98389.17 | 21458.7475 | 1113614 | 242880 | 20174.1667 | 4400 | 1133788.1667 | 247280 | 1232177.3367 | 268738.7475 | 320760 | 69957.9826 | 1931688 | 421302.5172 | 98010 | 21376.0502 | 27225 | 5937.7917 | 304516.6667 | 66415.3001 | 24200 | 5278.0371 | 599500 | 130751.3735 | 3305899.6667 | 721019.0524 | 1251655.7354 | 272987 | 625903.5208 | 136510 | 114301.5326 | 24929.245 | 40712.2249 | 8879.365 | 1365957.268 | 297916.245 | 666615.7457 | 145389.365 | 2081.1028 | 453.89 | 9900 | 2159.197 | 11981.1028 | 2613.087 | 0 | 0 | 10802306.2934 | 2355990.6328 | 1898793.0824 | 414128.1125 | 4585037.8788 | 12233226.2212 | 15387344.1722 | 14132019.3036
79-785 | oh | 3 | 10.5134 | 10.5134 | 10.1106 | 10.1106 | 12.1084 | 48919.2 | 4838.4043 | 93720 | 9269.474 | 21505 | 2126.9744 | 234771.4286 | 23220.3121 | 398915.6286 | 39455.1648 | 3696000 | 365556.7211 | 6758416.5 | 668448.2077 | 2312013.44 | 228672.0921 | 9070429.94 | 897120.2998 | 12766429.94 | 1262677.0209 | 975000 | 96433.3883 | 14140345.5686 | 1398565.574 | 164973.6 | 16316.8854 | 59494.05 | 5884.3208 | 224467.65 | 22201.2062 | 2455664 | 242880 | 44486.6667 | 4400 | 2500150.6667 | 247280 | 2724618.3167 | 269481.2062 | 710820 | 70304.3908 | 4280716 | 423388.6648 | 217195 | 21481.8972 | 56925 | 5630.2263 | 636716.6667 | 62975.1236 | 50600 | 5004.6456 | 1253500 | 123978.7202 | 7206472.6667 | 712763.6685 | 2760064.0167 | 272987 | 1380198.8333 | 136510 | 244532.7523 | 24185.766 | 88456.6207 | 8748.894 | 3004596.769 | 297172.766 | 1468655.454 | 145258.894 | 4589.103 | 453.89 | 9900 | 979.1698 | 14489.103 | 1433.0598 | 0 | 0 | 24365904.1072 | 2409935.0683 | 4193273.7707 | 414740.1002 | 10110606.0606 | 24216794.1155 | 34476510.1678 | 28410067.8862
79-799R | oh | 3 | 6.6937 | 6.6937 | 6.6937 | 6.6937 | 0 | 22625.13 | 3380.0381 | 43345.5 | 6475.5182 | 5142.5 | 768.254 | 108581.7857 | 16221.3685 | 179694.9157 | 26845.1788 | 1709400 | 255372.549 | 3125767.6313 | 466968.0868 | 1069306.216 | 159746.9604 | 4195073.8472 | 626715.0472 | 5904473.8472 | 882087.5962 | 150000 | 22408.9636 | 6234168.763 | 931341.7386 | 76300.29 | 11398.7361 | 10013.85 | 1496 | 86314.14 | 12894.7361 | 1625778 | 242880 | 29452.5 | 4400 | 1655230.5 | 247280 | 1741544.64 | 260174.7361 | 29700 | 4436.9748 | 178860 | 26720.4482 | 9075 | 1355.7423 | 8415 | 1257.1429 | 94123.3333 | 14061.3757 | 7480 | 1117.4603 | 185300 | 27682.5397 | 512953.3333 | 76631.6838 | 1827306.7312 | 272987 | 913763.8125 | 136510 | 245307.5899 | 36647.259 | 73235.6293 | 10940.897 | 2072614.3212 | 309634.259 | 986999.4418 | 147450.897 | 3038.2262 | 453.89 | 9900 | 1478.9916 | 12938.2262 | 1932.8816 | 0 | 0 | 8832674.6437 | 1319540.563 | 2728544.0818 | 407625.6331 | 6693750 | 0 | 15526424.6437 | 2728544.0818
79-808R | oh | 3 | 10.3098 | 10.3098 | 10.2572 | 10.2572 | 5.6475 | 39339.19 | 3835.2768 | 75366.5 | 7347.6702 | 57970 | 5651.6415 | 188795.3571 | 18406.1355 | 361471.0471 | 35240.724 | 2972200 | 289767.2735 | 5434893.2687 | 529861.4509 | 1859244.1413 | 181262.4001 | 7294137.4101 | 711123.8511 | 10266337.4101 | 1000891.1246 | 1650000 | 160862.6611 | 12277808.4572 | 1196994.5097 | 132666.27 | 12933.9692 | 32397.75 | 3158.5384 | 165064.02 | 16092.5076 | 2491268 | 242880 | 45131.6667 | 4400 | 2536399.6667 | 247280 | 2701463.6867 | 263372.5076 | 392040 | 38220.9683 | 2360952 | 230175.1645 | 119790 | 11678.6292 | 30690 | 2992.0455 | 343273.3333 | 33466.583 | 27280 | 2659.596 | 675800 | 65885.4463 | 3949825.3333 | 385078.4327 | 2800081.4292 | 272987 | 1400209.9583 | 136510 | 268626.6136 | 26189.086 | 93345.0364 | 9100.443 | 3068708.0427 | 299176.086 | 1493554.9947 | 145610.443 | 4655.6391 | 453.89 | 9900 | 965.176 | 14555.6391 | 1419.066 | 0 | 0 | 19310897.4724 | 1882668.0944 | 4195018.6814 | 408982.9506 | 10257196.9697 | 11294989.3967 | 29568094.4421 | 15490008.0781
791-419F | oh | 2 | 12.3977 | 6.5 | 2.6167 | 4.9756 | 5.7282 | 22625.13 | 4547.2455 | 43345.5 | 8711.6684 | 45347.5 | 9114.0345 | 47932.5 | 9633.5731 | 159250.63 | 32006.5215 | 1709400 | 343558.753 | 3125767.6313 | 628223.2535 | 1069306.216 | 214911.3783 | 4195073.8472 | 843134.6319 | 5904473.8472 | 1186693.3849 | 1000000 | 200982.0715 | 7063724.4773 | 1419681.9778 | 76300.29 | 15334.9903 | 68918.85 | 13851.4532 | 145219.14 | 29186.4436 | 1208466 | 242880 | 21892.5 | 4400 | 1230358.5 | 247280 | 1375577.64 | 276466.4436 | 436590 | 87746.7626 | 2629242 | 528430.5036 | 133402.5 | 26811.5108 | 5940 | 1193.8335 | 66440 | 13353.2488 | 5280 | 1061.1853 | 130800 | 26288.455 | 3407694.5 | 684885.4996 | 714315.9833 | 143564.706 | 357201.1667 | 71791.0304 | 43345.5125 | 8711.6709 | 19381.2575 | 3895.2853 | 757661.4958 | 152276.3769 | 376582.4242 | 75686.3157 | 2258.3606 | 453.89 | 9900 | 1989.7225 | 12158.3606 | 2443.6125 | 0 | 0 | 11241238.8337 | 2259287.4669 | 1752160.0642 | 352152.7593 | 4975568.1818 | 11456464.8045 | 16216807.0155 | 13208624.8687
835-11F | oh | 2 | 16.4133 | 16.4133 | 1.0576 | 1.0576 | 1.6197 | 3465.11 | 3276.465 | 6638.5 | 6277.0917 | 7480 | 7072.7794 | 16629.6429 | 15724.3041 | 34213.2529 | 32350.6402 | 261800 | 247547.2779 | 478721.1688 | 452658.9848 | 163767.6187 | 154851.903 | 642488.7874 | 607510.8878 | 904288.7874 | 855058.1658 | 300000 | 283667.6218 | 1238502.0403 | 1171076.4278 | 11685.63 | 11049.4496 | 100727.55 | 95243.8152 | 112413.18 | 106293.2648 | 256864 | 242880 | 4653.3333 | 4400 | 261517.3333 | 247280 | 373930.5133 | 353573.2648 | 140580 | 132926.6476 | 846604 | 800513.8109 | 42955 | 40616.4756 | 990 | 936.1032 | 11073.3333 | 10470.4871 | 880 | 832.0917 | 21800 | 20613.1805 | 1064882.3333 | 1006908.7966 | 288704.4333 | 272987 | 144369.6667 | 136510 |  |  |  |  | 288704.4333 | 272987 | 144369.6667 | 136510 | 480.0231 | 453.89 | 9900 | 9361.0315 | 10380.0231 | 9814.9215 | 0 | 0 | 2602468.83 | 2460787.1458 | 518300.18 | 490083.2648 | 1057575.7576 | 3239492.978 | 3660044.5876 | 3757793.158
840-308F | oh | 2 | 1.1646 | 1.1646 | 1.0854 | 1.0854 | 1.6631 | 3261.28 | 3004.6342 | 6248 | 5756.3148 | 6545 | 6029.9424 | 15651.4286 | 14419.7423 | 31705.7086 | 29210.6336 | 246400 | 227009.5969 | 450561.1 | 415104.2764 | 154134.2293 | 142004.6643 | 604695.3293 | 557108.9407 | 851095.3293 | 784118.5376 | 350000 | 322456.8138 | 1232801.0379 | 1135785.985 | 10998.24 | 10132.7355 | 1178.1 | 1085.3896 | 12176.34 | 11218.1251 | 263626 | 242880 | 4775.8333 | 4400 | 268401.8333 | 247280 | 280578.1733 | 258498.1251 | 12870 | 11857.1977 | 77506 | 71406.6795 | 3932.5 | 3623.0326 | 2475 | 2280.2303 | 27683.3333 | 25504.7985 | 2200 | 2026.8714 | 54500 | 50211.1324 | 181166.8333 | 166909.9424 | 296304.6396 | 272987 | 148170.2292 | 136510 | 17035.887 | 15695.251 | 7872.4478 | 7252.927 | 313340.5266 | 288682.251 | 156042.677 | 143762.927 | 492.6598 | 453.89 | 9900 | 9120.9213 | 10392.6598 | 9574.8113 | 0 | 0 | 1737701.0576 | 1600952.9897 | 436620.8503 | 402261.0521 | 1085416.6667 | 3326148.1233 | 2823117.7243 | 3762768.9736
840-374 | oh | 2 | 1.2581 | 1.2581 | 1.2013 | 1.2013 | 1.7785 | 7541.71 | 6277.8226 | 14448.5 | 12027.1291 | 16362.5 | 13620.3689 | 36193.9286 | 30128.3214 | 74546.6386 | 62053.6421 | 569800 | 474309.3174 | 1041922.5437 | 867310.5835 | 356435.4053 | 296701.709 | 1398357.9491 | 1164012.2925 | 1968157.9491 | 1638321.6098 | 800000 | 665930.9475 | 2842704.5877 | 2366306.1994 | 25433.43 | 21171.1352 | 6479.55 | 5393.6661 | 31912.98 | 26564.8013 | 291778 | 242880 | 5285.8333 | 4400 | 297063.8333 | 247280 | 328976.8133 | 273844.8013 | 238590 | 198605.581 | 1436842 | 1196046.9431 | 72902.5 | 60685.0386 | 6930 | 5768.6268 | 77513.3333 | 64523.1594 | 6160 | 5127.6683 | 152600 | 127026.3282 | 1991537.8333 | 1657783.3454 | 327946.3146 | 272987 | 163992.9792 | 136510 | 18854.2239 | 15694.514 | 8713.0619 | 7252.872 | 346800.5385 | 288681.514 | 172706.0411 | 143762.872 | 545.2697 | 453.89 | 9900 | 8240.8955 | 10445.2697 | 8694.7855 | 0 | 0 | 5191488.2292 | 4321465.8443 | 501682.8544 | 417607.6733 | 1201325.7576 | 3556958.1997 | 6392813.9868 | 4058641.0541
859-42R | oh | 2 | 26.6004 | 14.9384 | 7.0809 | 13.8547 | 16.4472 | 71136.67 | 5134.4664 | 136284.5 | 9836.6733 | 143522.5 | 10359.094 | 155536.0714 | 11226.2034 | 506479.7414 | 36556.437 | 5374600 | 387925.1432 | 9827863.9938 | 709350.5651 | 3362052.8773 | 242664.5413 | 13189916.8711 | 952015.1064 | 18564516.8711 | 1339940.2496 | 3350000 | 241794.5949 | 22420996.6125 | 1618291.2815 | 239899.11 | 17315.3159 | 179660.25 | 12967.4261 | 419559.36 | 30282.7419 | 3365038 | 242880 | 60960.8333 | 4400 | 3425998.8333 | 247280 | 3845558.1933 | 277562.7419 | 1310760 | 94607.3681 | 7893688 | 569746.5947 | 400510 | 28907.8069 | 58905 | 4251.6151 | 658863.3333 | 47555.1023 | 52360 | 3779.2134 | 1297100 | 93621.4236 | 11672186.3333 | 842469.1242 | 1932985.7896 | 139518.0645 | 966609.7292 | 69767.465 |  |  |  |  | 1932985.7896 | 139518.0645 | 966609.7292 | 69767.465 | 6288.5256 | 453.89 | 9900 | 714.5572 | 16188.5256 | 1168.4472 | 0 | 0 | 36042357.261 | 2601446.9173 | 4812167.9225 | 347330.207 | 13854734.8485 | 32894411.2407 | 49897092.1095 | 37706579.1632
907-1562AE | oh | 3 | 17.7017 | 17.7017 | 4.1759 | 4.1759 | 5.3591 | 25071.09 | 6003.6897 | 48031.5 | 11501.942 | 41607.5 | 9963.6083 | 120320.3571 | 28812.7119 | 235030.4471 | 56281.9521 | 1894200 | 453597.7142 | 3463688.4562 | 829437.8452 | 1184906.888 | 283745.6741 | 4648595.3443 | 1113183.5193 | 6542795.3443 | 1566781.2335 | 1725000 | 413079.9583 | 8502825.7914 | 2036143.1438 | 84548.97 | 20246.658 | 85412.25 | 20453.3847 | 169961.22 | 40700.0427 | 1014254 | 242880 | 18374.1667 | 4400 | 1032628.1667 | 247280 | 1202589.3867 | 287980.0427 | 499950 | 119721.3479 | 3010810 | 720988.5618 | 152762.5 | 36581.523 | 30690 | 7349.2313 | 343273.3333 | 82202.5126 | 27280 | 6532.65 | 675800 | 161831.557 | 4740565.8333 | 1135207.3836 | 1139979.2354 | 272987 | 570058.5208 | 136510 | 63081.0406 | 15105.805 | 29857.194 | 7149.802 | 1203060.276 | 288092.805 | 599915.7148 | 143659.802 | 1895.4206 | 453.89 | 9900 | 2370.7198 | 11795.4206 | 2824.6098 | 0 | 0 | 14458247.3213 | 3462267.9422 | 1802505.1015 | 431639.8447 | 4175946.9697 | 10718222.5591 | 18634194.291 | 12520727.6606
907-1702R | oh | 3 | 6.1907 | 6.1907 | 5.2799 | 5.2799 | 7.0761 | 24051.94 | 4555.357 | 46079 | 8727.2086 | 33660 | 6375.0915 | 115429.2857 | 21861.9208 | 219220.2257 | 41519.5779 | 1817200 | 344171.6048 | 3322888.1125 | 629343.8996 | 1136739.9413 | 215294.7446 | 4459628.0538 | 844638.6442 | 6276828.0538 | 1188810.2491 | 1200000 | 227275.9882 | 7696048.2795 | 1457605.8152 | 81112.02 | 15362.3454 | 30630.6 | 5801.3332 | 111742.62 | 21163.6787 | 1282388 | 242880 | 23231.6667 | 4400 | 1305619.6667 | 247280 | 1417362.2867 | 268443.6787 | 780120 | 147752.12 | 4698056 | 889796.1002 | 238370 | 45146.4811 | 23265 | 4406.3132 | 260223.3333 | 49285.4294 | 20680 | 3916.7229 | 512300 | 97027.9073 | 6533014.3333 | 1237331.074 | 1441350.6792 | 272987 | 720762.4583 | 136510 | 79855.3694 | 15124.34 | 37767.8367 | 7153.102 | 1521206.0486 | 288111.34 | 758530.295 | 143663.102 | 2396.5048 | 453.89 | 9900 | 1875.0269 | 12296.5048 | 2328.9169 | 0 | 0 | 15762565.1663 | 2985377.1461 | 2175892.5817 | 412106.7807 | 5279924.2424 | 14152197.9477 | 21042489.4087 | 16328090.5293
907-1716R | oh | 3 | 38.6892 | 38.6892 | 12.8004 | 12.8004 | 17.1278 | 57683.89 | 4506.4205 | 110511.5 | 8633.4554 | 98642.5 | 7706.2173 | 276834.6429 | 21627.0665 | 543672.5329 | 42473.1597 | 4358200 | 340474.2994 | 7969299.4562 | 622583.096 | 2726249.1813 | 212981.9146 | 10695548.6376 | 835565.0106 | 15053748.6376 | 1176039.31 | 4550000 | 355458.231 | 20147421.1704 | 1573970.7007 | 194531.37 | 15197.3136 | 191441.25 | 14955.9051 | 385972.62 | 30153.2186 | 3108956 | 242880 | 56321.6667 | 4400 | 3165277.6667 | 247280 | 3551250.2867 | 277433.2186 | 1800810 | 140684.118 | 10844878 | 847231.0218 | 550247.5 | 42986.8138 | 57915 | 4524.4755 | 647790 | 50607.0961 | 51480 | 4021.756 | 1275300 | 99629.8642 | 15228420.5 | 1189685.1454 | 3494337.0042 | 272987 | 1747379.7083 | 136510 | 193370.4454 | 15106.619 | 91520.8779 | 7149.857 | 3687707.4496 | 288093.619 | 1838900.5862 | 143659.857 | 5809.9639 | 453.89 | 9900 | 773.4146 | 15709.9639 | 1227.3046 | 0 | 0 | 39079259.0839 | 3052976.7698 | 5390150.8729 | 421093.0756 | 12800378.7879 | 34255581.0526 | 51879637.8718 | 39645731.9255
907-2820R | oh | 3 | 2.4583 | 2.4583 | 2.4583 | 2.4583 | 3.5427 | 6318.73 | 2570.3308 | 12105.5 | 4924.2712 | 1870 | 760.678 | 30324.6429 | 12335.4479 | 50618.8729 | 20590.7279 | 477400 | 194196.6102 | 872962.1312 | 355103.2398 | 298635.0693 | 121478.6723 | 1171597.2006 | 476581.9121 | 1648997.2006 | 670778.5223 | 125000 | 50847.4576 | 1824616.0734 | 742216.7078 | 21309.09 | 8668.1044 | 1767.15 | 718.8407 | 23076.24 | 9386.9451 | 597080 | 242880 | 10816.6667 | 4400 | 607896.6667 | 247280 | 630972.9067 | 256666.9451 | 106920 | 43492.8814 | 643896 | 261923.7966 | 32670 | 13289.4915 | 2475 | 1006.7797 | 27683.3333 | 11261.0169 | 2200 | 894.9153 | 54500 | 22169.4915 | 870344.3333 | 354038.3729 | 671093.0417 | 272987 | 335587.0833 | 136510 | 39600.655 | 16108.741 | 18011.7511 | 7326.814 | 710693.6966 | 289095.741 | 353598.8344 | 143836.814 | 1115.8129 | 453.89 | 9900 | 4027.1186 | 11015.8129 | 4481.0086 | 0 | 0 | 3416669.9163 | 1389831.8304 | 984571.7411 | 400503.7591 | 2458333.3333 | 7085432.4537 | 5875003.2496 | 8070004.1948
908-1172R | oh | 2 | 15.8231 | 15.8231 | 10.1765 | 10.1765 | 12.3363 | 49326.86 | 4847.1269 | 94501 | 9286.1848 | 70592.5 | 6936.8049 | 236727.8571 | 23262.1731 | 451148.2171 | 44332.2896 | 3726800 | 366215.7374 | 6814736.6375 | 669653.2689 | 2331280.2187 | 229084.3362 | 9146016.8562 | 898737.6052 | 12872816.8562 | 1264953.3425 | 3400000 | 334102.5832 | 16723965.0733 | 1643388.2153 | 166348.38 | 16346.301 | 85412.25 | 8393.0745 | 251760.63 | 24739.3755 | 2471672 | 242880 | 44776.6667 | 4400 | 2516448.6667 | 247280 | 2768209.2967 | 272019.3755 | 1323630 | 130067.1183 | 7971194 | 783293.0902 | 404442.5 | 39742.7306 | 48015 | 4718.2163 | 537056.6667 | 52774.1234 | 42680 | 4193.9701 | 1057300 | 103896.0768 | 11384318.1667 | 1118685.3257 | 2778056.3417 | 272987 | 1389196.0833 | 136510 | 193886.9966 | 19052.396 | 79813.6247 | 7842.923 | 2971943.3382 | 292039.396 | 1469009.7081 | 144352.923 | 4619.0185 | 453.89 | 9900 | 972.8281 | 14519.0185 | 1426.7181 | 0 | 0 | 31094745.5967 | 3055539.6551 | 4237219.0047 | 416372.2985 | 10176515.1515 | 24672535.005 | 41271260.7482 | 28909754.0097
908-1236 | oh | 2 | 7.4777 | 7.4777 | 5.4265 | 5.4265 | 1.0261 | 26701.73 | 4920.6036 | 51155.5 | 9426.9524 | 50957.5 | 9390.4649 | 128146.0714 | 23614.8003 | 256960.8014 | 47352.8211 | 2017400 | 371767.1367 | 3688969.0063 | 679804.4239 | 1261974.0027 | 232556.985 | 4950943.0089 | 912361.4089 | 6968343.0089 | 1284128.5455 | 2575000 | 474521.8484 | 9800303.8103 | 1806003.2151 | 90048.09 | 16594.0917 | 43000.65 | 7924.1739 | 133048.74 | 24518.2656 | 1317992 | 242880 | 23876.6667 | 4400 | 1341868.6667 | 247280 | 1474917.4067 | 271798.2656 | 733590 | 135186.2069 | 4417842 | 814121.3793 | 224152.5 | 41306.8966 | 20790 | 3831.188 | 232540 | 42852.5478 | 18480 | 3405.5005 | 457800 | 84363.5348 | 6105194.5 | 1125067.2539 | 1481368.0917 | 272987 | 740773.5833 | 136510 | 103441.8381 | 19062.296 | 42568.5749 | 7844.551 | 1584809.9297 | 292049.296 | 783342.1582 | 144354.551 | 2463.041 | 453.89 | 9900 | 1824.3753 | 12363.041 | 2278.2653 | 0 | 0 | 17502671.281 | 3225398.0303 | 2258259.5649 | 416152.8166 | 5426515.1515 | 2052129.5455 | 22929186.4326 | 4310389.1103
908-1368R | oh | 2 | 20.7674 | 20.7674 | 18.6854 | 18.6854 | 25.1881 | 78882.21 | 4221.5922 | 151123.5 | 8087.7779 | 131835 | 7055.5023 | 378568.9286 | 20260.1277 | 740409.6386 | 39625.0002 | 5959800 | 318954.6215 | 10897946.6062 | 583232.7317 | 3728121.672 | 199520.3927 | 14626068.2782 | 782753.1245 | 20585868.2783 | 1101707.746 | 6700000 | 358568.4023 | 28026277.9168 | 1499901.1484 | 266019.93 | 14236.7674 | 90124.65 | 4823.2615 | 356144.58 | 19060.0288 | 4538314 | 242880 | 82215.8333 | 4400 | 4620529.8333 | 247280 | 4976674.4133 | 266340.0288 | 1006830 | 53883.1977 | 6063354 | 324496.5905 | 307642.5 | 16464.3104 | 72765 | 3894.2134 | 813890 | 43557.498 | 64680 | 3461.523 | 1602300 | 85751.3658 | 9931461.5 | 531508.6989 | 5100875.8396 | 272987 | 2550746.2292 | 136510 | 354916.2977 | 18994.294 | 146363.093 | 7833.012 | 5455792.1373 | 291981.294 | 2697109.3221 | 144343.012 | 8481.1238 | 453.89 | 9900 | 529.825 | 18381.1238 | 983.715 | 0 | 0 | 43431912.6779 | 2324374.8562 | 7673783.7355 | 410683.0408 | 18685416.6667 | 50376229.9155 | 62117329.3445 | 58050013.651
908-1370R | oh | 2 | 7.979 | 7.979 | 5.8532 | 5.8532 | 7.7464 | 27109.39 | 4631.5347 | 51936.5 | 8873.1506 | 50957.5 | 8705.8923 | 130102.5 | 22227.5101 | 260105.89 | 44438.0877 | 2048200 | 349927.0668 | 3745289.1437 | 639868.1986 | 1281240.7813 | 218895.0437 | 5026529.9251 | 858763.2423 | 7074729.9251 | 1208690.3092 | 2425000 | 414301.8929 | 9759835.8151 | 1667430.2897 | 91422.87 | 15619.2446 | 43589.7 | 7447.132 | 135012.57 | 23066.3766 | 1421630 | 242880 | 25754.1667 | 4400 | 1447384.1667 | 247280 | 1582396.7367 | 270346.3766 | 574200 | 98099.8544 | 3457960 | 590779.1231 | 175450 | 29974.9555 | 23265 | 3974.7355 | 260223.3333 | 44458.1524 | 20680 | 3533.0982 | 512300 | 87524.4782 | 5024078.3333 | 858344.3973 | 1597852.8854 | 272987 | 799023.0208 | 136510 | 111147.6434 | 18989.146 | 45840.0988 | 7831.604 | 1709000.5288 | 291976.146 | 844863.1196 | 144341.604 | 2656.7179 | 453.89 | 9900 | 1691.3768 | 12556.7179 | 2145.2668 | 0 | 0 | 16505471.3951 | 2819896.0999 | 2427259.8563 | 414687.9806 | 5853219.697 | 15492861.2611 | 22358691.0921 | 17920121.1174
908-1372R | oh | 2 | 7.5133 | 7.5133 | 3.7273 | 3.7273 | 0.96306 | 18344.7 | 4921.7488 | 35145 | 9429.1463 | 32725 | 8779.878 | 88039.2857 | 23620.2962 | 174253.9857 | 46751.0693 | 1386000 | 371853.6585 | 2534406.1875 | 679962.6357 | 867005.04 | 232611.1083 | 3401411.2275 | 912573.744 | 4787411.2275 | 1284427.4025 | 1800000 | 482926.8293 | 6761665.2132 | 1814105.3011 | 61865.1 | 16597.9537 | 41233.5 | 11062.6463 | 103098.6 | 27660.6 | 905280 | 242880 | 16400 | 4400 | 921680 | 247280 | 1024778.6 | 274940.6 | 348480 | 93494.6341 | 2098624 | 563045.4634 | 106480 | 28567.8049 | 18810 | 5046.5854 | 210393.3333 | 56446.9919 | 16720 | 4485.8537 | 414200 | 111126.8293 | 3213707.3333 | 862214.1626 | 1017497 | 272987 | 508810 | 136510 | 70637.137 | 18951.427 | 29166.088 | 7825.048 | 1088134.137 | 291938.427 | 537976.088 | 144335.048 | 1691.7718 | 453.89 | 9900 | 2656.0976 | 11591.7718 | 3109.9876 | 0 | 0 | 11075098.4554 | 2971367.8783 | 1562754.688 | 419275.648 | 3727272.7273 | 1926121.5909 | 14802371.1826 | 3488876.2789
908-2038R | oh | 2 | 25.3426 | 25.3426 | 17.9265 | 17.9265 | 5.3935 | 86627.75 | 4832.3809 | 165962.5 | 9257.9343 | 100980 | 5632.9967 | 415741.0714 | 23191.4049 | 769311.3214 | 42914.7168 | 6545000 | 365101.6355 | 11968029.2188 | 667616.0491 | 4094190.4667 | 228387.4156 | 16062219.6854 | 896003.4647 | 22607219.6854 | 1261105.1001 | 5000000 | 278916.4518 | 28376531.0068 | 1582936.2688 | 292140.75 | 16296.5723 | 132536.25 | 7393.3081 | 424677 | 23689.8804 | 4353992 | 242880 | 78876.6667 | 4400 | 4432868.6667 | 247280 | 4857545.6667 | 270969.8804 | 1138500 | 63509.2761 | 6856300 | 382466.9738 | 347875 | 19405.6121 | 106425 | 5936.7367 | 1190383.3333 | 66403.4991 | 94600 | 5277.0993 | 2343500 | 130728.141 | 12077583.3333 | 673727.338 | 4893705.5917 | 272987 | 2447148.5833 | 136510 | 337749.4923 | 18840.778 | 139930.7561 | 7805.798 | 5231455.0839 | 291827.778 | 2587079.3394 | 144315.798 | 8136.666 | 453.89 | 9900 | 552.2546 | 18036.666 | 1006.1446 | 0 | 0 | 45703606.0901 | 2549497.5294 | 7444625.0061 | 415285.6784 | 17926515.1515 | 10787076.4813 | 63630121.2416 | 18231701.4874
908-2040 | oh | 2 | 15.3686 | 15.3686 | 5.3208 | 5.3208 | 6.3967 | 25682.58 | 4826.7966 | 49203 | 9247.2357 | 45815 | 8610.4933 | 123255 | 23164.6045 | 243955.58 | 45849.1301 | 1940400 | 364679.7181 | 3548168.6625 | 666844.5411 | 1213807.056 | 228123.4874 | 4761975.7185 | 894968.0285 | 6702375.7185 | 1259647.7466 | 2650000 | 498042.2866 | 9596331.2985 | 1803539.1634 | 86611.14 | 16277.7397 | 80110.8 | 15056.0626 | 166721.94 | 31333.8023 | 1292324 | 242880 | 23411.6667 | 4400 | 1315735.6667 | 247280 | 1482457.6067 | 278613.8023 | 585090 | 109962.0987 | 3523542 | 662216.1942 | 178777.5 | 33599.5301 | 33165 | 6233.0462 | 370956.6667 | 69717.776 | 29480 | 5540.4855 | 730300 | 137252.9366 | 5451311.1667 | 1024522.0673 | 1452518.3292 | 272987 | 726346.9583 | 136510 | 100296.8091 | 18849.831 | 41540.4907 | 7807.14 | 1552815.1383 | 291836.831 | 767887.4491 | 144317.14 | 2415.073 | 453.89 | 9900 | 1860.6108 | 12315.073 | 2314.5008 | 0 | 0 | 16612772.6765 | 3122212.5625 | 2250345.0557 | 422930.9423 | 5320833.3333 | 12793484.8318 | 21933606.0098 | 15043829.8876
908-2055F | oh | 3 | 12.6886 | 12.6886 | 11.539 | 11.539 | 13.7765 | 57480.06 | 4981.3662 | 110121 | 9543.3621 | 97240 | 8427.0623 | 275856.4286 | 23906.4101 | 540697.4886 | 46858.2008 | 4342800 | 376357.9424 | 7941139.3875 | 688199.0606 | 2716615.792 | 235428.7395 | 10657755.1795 | 923627.8001 | 15000555.1795 | 1299985.7425 | 4300000 | 372648.7871 | 19841252.6681 | 1719492.7303 | 193843.98 | 16799.0056 | 64795.5 | 5615.3406 | 258639.48 | 22414.3462 | 2802596 | 242880 | 50771.6667 | 4400 | 2853367.6667 | 247280 | 3112007.1467 | 269694.3462 | 755370 | 65462.2591 | 4549006 | 394228.2717 | 230807.5 | 20002.357 | 66825 | 5791.2221 | 747450 | 64775.8921 | 59400 | 5147.753 | 1471500 | 127523.8814 | 7880358.5 | 682931.6364 | 3150001.1292 | 272987 | 1575190.9583 | 136510 | 217486.5268 | 18847.928 | 90081.1219 | 7806.656 | 3367487.6559 | 291834.928 | 1665272.0802 | 144316.656 | 5237.4436 | 453.89 | 9900 | 857.9588 | 15137.4436 | 1311.8488 | 0 | 0 | 31104236.2676 | 2695571.1436 | 4777279.2269 | 414011.0022 | 11539015.1515 | 27552916.3424 | 42643251.4191 | 32330195.5692
908-30 | oh | 2 | 1.7795 | 1.7795 | 1.5403 | 1.5403 | 1.883 | 8560.86 | 5557.7697 | 16401 | 10647.6429 | 14492.5 | 9408.6315 | 41085 | 26672.6669 | 80539.36 | 52286.711 | 646800 | 419907.0454 | 1182722.8875 | 767831.9004 | 404602.352 | 262670.6527 | 1587325.2395 | 1030502.5531 | 2234125.2395 | 1450409.5985 | 775000 | 503135.3744 | 3089664.5995 | 2005831.6839 | 28870.38 | 18742.8509 | 8835.75 | 5736.2302 | 37706.13 | 24479.0811 | 374118 | 242880 | 6777.5 | 4400 | 380895.5 | 247280 | 418601.63 | 271759.0811 | 211860 | 137540.9812 | 1275868 | 828302.3534 | 64735 | 42026.4109 | 8910 | 5784.4338 | 99660 | 64699.9631 | 7920 | 5141.7189 | 196200 | 127374.4006 | 1865153 | 1210870.2619 | 420493.0437 | 272987 | 210271.9375 | 136510 | 29025.9654 | 18843.858 | 12022.6411 | 7805.182 | 449519.0091 | 291830.858 | 222294.5786 | 144315.182 | 699.1453 | 453.89 | 9900 | 6427.1487 | 10599.1453 | 6881.0387 | 0 | 0 | 5414935.7539 | 3515413.8425 | 640896.2086 | 416074.2631 | 1540340.9091 | 3766060.3116 | 6955276.663 | 4406956.5202
909-451 | oh | 3 | 24.5839 | 24.5839 | 20.5956 | 20.5956 | 4.5518 | 86831.58 | 4216.0168 | 166353 | 8077.0963 | 152872.5 | 7422.5647 | 416719.2857 | 20233.3701 | 822776.3657 | 39949.0479 | 6560400 | 318533.3762 | 11996189.2875 | 582462.4529 | 4103823.856 | 199256.885 | 16100013.1435 | 781719.3379 | 22660413.1435 | 1100252.7141 | 6475000 | 314386.8684 | 29958189.5092 | 1454588.6304 | 292828.14 | 14217.9648 | 97193.25 | 4719.1168 | 390021.39 | 18937.0816 | 5002270 | 242880 | 90620.8333 | 4400 | 5092890.8333 | 247280 | 5482912.2233 | 266217.0816 | 1502820 | 72967.8569 | 9050316 | 439428.6494 | 459195 | 22295.7341 | 84150 | 4085.8154 | 941233.3333 | 45700.6023 | 74800 | 3631.8359 | 1853000 | 89970.4814 | 13965514.3333 | 678080.9755 | 5622343.0521 | 272987 | 2811511.3542 | 136510 | 431698.1665 | 20960.654 | 168455.5202 | 8179.182 | 6054041.2186 | 293947.654 | 2979966.8744 | 144689.182 | 9348.1568 | 453.89 | 9900 | 480.6842 | 19248.1568 | 934.5742 | 0 | 0 | 49996993.218 | 2427551.834 | 8462879.0977 | 410906.2636 | 20595643.9394 | 9103664.6004 | 70592637.1574 | 17566543.6981
909-453R | oh | 2 | 2.3487 | 2.3487 | 2.2977 | 2.2977 | 1.6131 | 11006.82 | 4790.3074 | 21087 | 9177.3294 | 18232.5 | 7935.0148 | 52823.5714 | 22989.4871 | 103149.8914 | 44892.1387 | 831600 | 361922.8487 | 1520643.7125 | 661803.3961 | 520203.024 | 226398.9422 | 2040846.7365 | 888202.3383 | 2872446.7365 | 1250125.187 | 725000 | 315529.179 | 3700596.6279 | 1610546.5047 | 37119.06 | 16154.6849 | 589.05 | 256.362 | 37708.11 | 16411.0469 | 558072 | 242880 | 10110 | 4400 | 568182 | 247280 | 605890.11 | 263691.0469 | 143550 | 62474.7774 | 864490 | 376236.9931 | 43862.5 | 19089.5153 | 7920 | 3446.8843 | 88586.6667 | 38554.0389 | 7040 | 3063.8971 | 174400 | 75901.088 | 1329849.1667 | 578767.1942 | 627249.675 | 272987 | 313662.75 | 136510 |  |  |  |  | 627249.675 | 272987 | 313662.75 | 136510 | 1042.9154 | 453.89 | 9900 | 4308.6053 | 10942.9154 | 4762.4953 | 0 | 0 | 5668638.385 | 2467063.1943 | 919552.86 | 400201.0469 | 2297727.2727 | 3226219.2171 | 7966365.6578 | 4145772.0771
909-805R | oh | 2 | 14.386 | 14.386 | 13.4722 | 13.4722 | 4.8883 | 58906.87 | 4372.4892 | 112854.5 | 8376.8681 | 108460 | 8050.6769 | 282703.9286 | 20984.3075 | 562925.2986 | 41784.3417 | 4450600 | 330355.3625 | 8138259.8688 | 604079.8519 | 2784049.5173 | 206652.0666 | 10922309.3861 | 810731.9185 | 15372909.3861 | 1141087.281 | 5375000 | 398970.9418 | 21310834.6847 | 1581842.5644 | 198655.71 | 14745.6476 | 63028.35 | 4678.4149 | 261684.06 | 19424.0625 | 3272118 | 242880 | 59277.5 | 4400 | 3331395.5 | 247280 | 3593079.56 | 266704.0625 | 998910 | 74146.2444 | 6015658 | 446525.1605 | 305222.5 | 22655.7969 | 64845 | 4813.2597 | 725303.3333 | 53837.2007 | 57640 | 4278.453 | 1427900 | 105988.9503 | 9595478.8333 | 712245.0654 | 3677724.2937 | 272987 | 1839084.4375 | 136510 | 286733.5663 | 21283.416 | 110952.3642 | 8235.678 | 3964457.8601 | 294270.416 | 1950036.8017 | 144745.678 | 6114.8783 | 453.89 | 9900 | 734.8488 | 16014.8783 | 1188.7388 | 0 | 0 | 34886786.2564 | 2589546.7847 | 5543116.3617 | 411449.7405 | 13472159.0909 | 9776649.6473 | 48358945.3473 | 15319766.009
91-7F | oh | 2 | 14.6081 | 6.8655 | 4.8998 | 7.0892 | 8.9251 | 31389.82 | 4427.8339 | 60137 | 8482.8981 | 62645 | 8836.6755 | 103690.7143 | 14626.5655 | 257862.5343 | 36373.9729 | 2371600 | 334536.8278 | 4336650.5875 | 611725.9785 | 1483541.9573 | 209267.7603 | 5820192.5448 | 820993.7388 | 8191792.5448 | 1155530.5666 | 1925000 | 271539.6329 | 10374655.0791 | 1463444.1724 | 105858.06 | 14932.2903 | 66562.65 | 9389.2974 | 172420.71 | 24321.5877 | 1721826 | 242880 | 31192.5 | 4400 | 1753018.5 | 247280 | 1925439.21 | 271601.5877 | 574200 | 80996.3934 | 3457960 | 487778.28 | 175450 | 24748.898 | 26730 | 3770.5218 | 298980 | 42173.9841 | 23760 | 3351.5749 | 588600 | 83027.6509 | 5145680 | 725847.303 | 1337584.5979 | 188679.0809 | 668873.1458 | 94350.9447 | 68706.9621 | 9691.7731 | 34094.9058 | 4809.4121 | 1406291.5601 | 198370.854 | 702968.0517 | 99160.3567 | 3217.7191 | 453.89 | 9900 | 1396.4895 | 13117.7191 | 1850.3795 | 0 | 0 | 16939744.3582 | 2389512.709 | 2628407.2617 | 370761.9444 | 7089204.5455 | 17850237.5957 | 24028948.9037 | 20478644.8573
920-1342R | oh | 3 | 6.4608 | 6.2525 | 5.9248 | 6.1331 | 7.5598 | 23848.11 | 3888.3989 | 45688.5 | 7449.442 | 44880 | 7317.6173 | 108581.7857 | 17704.0987 | 222998.3957 | 36359.5568 | 1801800 | 293780.8109 | 3294728.0438 | 537200.5086 | 1127106.552 | 183773.0474 | 4421834.5958 | 720973.556 | 6223634.5958 | 1014754.367 | 1550000 | 252725.1953 | 7996632.9915 | 1303839.1191 | 80424.63 | 13113.1163 | 21205.8 | 3457.5742 | 101630.43 | 16570.6905 | 1489618 | 242880 | 26985.8333 | 4400 | 1516603.8333 | 247280 | 1618234.2633 | 263850.6905 | 333630 | 54397.8754 | 2009194 | 327596.0942 | 101942.5 | 16621.573 | 9900 | 1614.1803 | 110733.3333 | 18054.9054 | 8800 | 1434.8269 | 218000 | 35544.5759 | 2792199.8333 | 455264.0311 | 1617396.2729 | 263714.0574 | 808795.8958 | 131872.9682 | 90204.726 | 14707.7465 | 42481.923 | 6926.6144 | 1707600.9989 | 278421.8039 | 851277.8188 | 138799.5826 | 2783.7727 | 453.89 | 9900 | 1614.1803 | 12683.7727 | 2068.0703 | 0 | 0 | 12509117.5964 | 2039593.0244 | 2469512.0821 | 402650.2731 | 6133143.9394 | 15119542.0222 | 18642261.5358 | 17589054.1044
920-735AE | oh | 2 | 19.2903 | 4.75 | 1.5886 | 5.6727 | 6.3555 | 34243.44 | 6036.5038 | 65604 | 11564.8077 | 74800 | 13185.8974 | 34237.5 | 6035.4567 | 208884.94 | 36822.6657 | 2587200 | 456076.9231 | 4730891.55 | 833971.2668 | 1618409.408 | 285296.5303 | 6349300.958 | 1119267.7971 | 8936500.958 | 1575344.7202 | 600000 | 105769.2308 | 9745385.898 | 1717936.6166 | 115481.52 | 20357.3192 | 114275.7 | 20144.7548 | 229757.22 | 40502.074 | 1377792 | 242880 | 24960 | 4400 | 1402752 | 247280 | 1632509.22 | 287782.074 | 252450 | 44502.4038 | 1520310 | 268003.3654 | 77137.5 | 13597.9567 | 5445 | 959.8558 | 60903.3333 | 10736.1645 | 4840 | 853.2051 | 119900 | 21136.2179 | 2040985.8333 | 359789.1693 | 433677.075 | 76449.4844 | 216864.75 | 38229.363 | 24139.7728 | 4255.4087 | 11381.9218 | 2006.4285 | 457816.8478 | 80704.893 | 228246.6718 | 40235.7915 | 2574.7942 | 453.89 | 9900 | 1745.1923 | 12474.7942 | 2199.0823 | 0 | 0 | 12256663.3733 | 2160629.7613 | 1860755.8918 | 328017.8656 | 5672727.2727 | 12711073.2368 | 17929390.646 | 14571829.1287
921-800F | oh | 2 | 17.4883 | 2.0252 | 1.0703 | 4.6273 | 5.4693 | 27720.88 | 5990.7599 | 53108 | 11477.1709 | 57970 | 12527.8978 | 23477.1429 | 5073.6458 | 162276.0229 | 35069.4745 | 2094400 | 452620.8251 | 3829769.35 | 827651.5295 | 1310140.9493 | 283134.5863 | 5139910.2993 | 1110786.1158 | 7234310.2993 | 1563406.9409 | 450000 | 97249.5088 | 7846586.3222 | 1695725.9242 | 93485.04 | 20203.0538 | 111919.5 | 24186.9253 | 205404.54 | 44389.9792 | 1123872 | 242880 | 20360 | 4400 | 1144232 | 247280 | 1349636.54 | 291669.9792 | 412830 | 89216.6994 | 2486154 | 537282.7898 | 126142.5 | 27260.6582 | 6435 | 1390.668 | 71976.6667 | 15554.8788 | 5720 | 1236.1493 | 141700 | 30622.7898 | 3250958.1667 | 702564.6333 | 292168.4729 | 63140.5344 | 146101.8958 | 31574.0836 | 16265.8855 | 3515.2208 | 7668.7013 | 1657.2832 | 308434.3584 | 66655.7553 | 153770.5972 | 33231.3668 | 2100.2728 | 453.89 | 9900 | 2139.4892 | 12000.2728 | 2593.3792 | 0 | 0 | 11417979.1201 | 2467539.692 | 1503407.1372 | 324901.3459 | 4627272.7273 | 10938683.026 | 16045251.8474 | 12442090.1631
928-19 | oh | 2 | 2.2085 | 2.2085 | 2.1239 | 2.1239 | 3.1141 | 6726.39 | 3167.0536 | 12886.5 | 6067.4799 | 15427.5 | 7263.8844 | 32281.0714 | 15199.2204 | 67321.4614 | 31697.6383 | 508200 | 239280.8989 | 929282.2688 | 437543.2833 | 317901.848 | 149680.9129 | 1247184.1168 | 587224.1962 | 1755384.1168 | 826505.0951 | 275000 | 129481.0059 | 2097705.5782 | 987683.7393 | 22683.87 | 10680.4738 | 1178.1 | 554.6966 | 23861.97 | 11235.1705 | 515844 | 242880 | 9345 | 4400 | 525189 | 247280 | 549050.97 | 258515.1705 | 23760 | 11187.1589 | 143088 | 67371.557 | 7260 | 3418.2986 | 1485 | 699.1974 | 16610 | 7820.6528 | 1320 | 621.5088 | 32700 | 15396.4687 | 226223 | 106514.8422 | 579787.1625 | 272987 | 289928.625 | 136510 | 32347.881 | 15230.677 | 15230.8081 | 7171.274 | 612135.0435 | 288217.677 | 305159.4331 | 143681.274 | 964.0005 | 453.89 | 9900 | 4661.3162 | 10864.0005 | 5115.2062 | 0 | 0 | 2946927.6222 | 1387531.4647 | 854210.4031 | 402196.4445 | 2123863.6364 | 6228292.6709 | 5070791.2585 | 7082503.074
968-476F | oh | 2 | 3.5379 | 2.8345 | 1.8684 | 2.4922 | 3.7821 | 8764.69 | 3516.7994 | 16791.5 | 6737.5272 | 11220 | 4501.9834 | 32281.0714 | 12952.6603 | 69057.2614 | 27708.9703 | 662200 | 265705.2968 | 1210882.9563 | 485862.3003 | 414235.7413 | 166210.5566 | 1625118.6976 | 652072.8568 | 2287318.6976 | 917778.1536 | 400000 | 160498.5181 | 2756375.959 | 1105985.642 | 29557.77 | 11859.9457 | 4123.35 | 1654.4789 | 33681.12 | 13514.4246 | 605314 | 242880 | 10965.8333 | 4400 | 616279.8333 | 247280 | 649960.9533 | 260794.4246 | 52470 | 21053.3931 | 315986 | 126788.2119 | 16032.5 | 6432.9812 | 4950 | 1986.1692 | 55366.6667 | 22215.6699 | 4400 | 1765.4837 | 109000 | 43735.8462 | 558205.1667 | 223977.7551 | 510041.0521 | 204652.0826 | 255051.3542 | 102338.411 | 26193.3425 | 10509.9816 | 13000.0353 | 5216.216 | 536234.3946 | 215162.0642 | 268051.3895 | 107554.627 | 1131.2005 | 453.89 | 9900 | 3972.3383 | 11031.2005 | 4426.2283 | 0 | 0 | 3861846.7207 | 1549551.6897 | 918012.3428 | 368349.0516 | 2492234.8485 | 7564163.0209 | 6354081.5692 | 8482175.3637
970-1341R | oh | 3 | 5.7884 | 5.7884 | 4.1362 | 4.1362 | 5.3363 | 16917.89 | 4090.2266 | 32411.5 | 7836.106 | 14492.5 | 3503.8418 | 81191.7857 | 19629.6822 | 145013.6757 | 35059.8566 | 1278200 | 309029.5343 | 2337285.7062 | 565083.9566 | 799571.3147 | 193311.8065 | 3136857.0209 | 758395.7631 | 4415057.0209 | 1067425.2974 | 675000 | 163194.2855 | 5235070.6966 | 1265679.4395 | 57053.37 | 13793.754 | 16493.4 | 3987.598 | 73546.77 | 17781.352 | 1004594 | 242880 | 18199.1667 | 4400 | 1022793.1667 | 247280 | 1096339.9367 | 265061.352 | 60390 | 14600.4487 | 363682 | 87927.1468 | 18452.5 | 4461.2482 | 13365 | 3231.2469 | 149490 | 36142.0944 | 11880 | 2872.2194 | 294300 | 71152.7085 | 911559.5 | 220387.113 | 1129121.7979 | 272987 | 564629.1458 | 136510 | 71198.0974 | 17213.515 | 31105.1967 | 7520.282 | 1200319.8953 | 290200.515 | 595734.3425 | 144030.282 | 1877.3681 | 453.89 | 9900 | 2393.5162 | 11777.3681 | 2847.4062 | 0 | 0 | 7358727.46 | 1779114.4736 | 1692074.2792 | 409091.634 | 4136174.2424 | 10672566.4566 | 11494901.7025 | 12364640.7358
971-1973R | oh | 3 | 11.5199 | 11.5199 | 10.9521 | 10.9521 | 15.3808 | 53199.63 | 4857.4895 | 101920.5 | 9306.0377 | 64982.5 | 5933.346 | 255313.9286 | 23311.9052 | 475416.5586 | 43408.7784 | 4019400 | 366998.6684 | 7349777.9437 | 671084.9178 | 2514314.616 | 229574.0947 | 9864092.5598 | 900659.0125 | 13883492.5598 | 1267657.6809 | 3175000 | 289899.182 | 17533909.1183 | 1600965.6414 | 179408.79 | 16381.2477 | 68918.85 | 6292.7617 | 248327.64 | 22674.0094 | 2660042 | 242880 | 48189.1667 | 4400 | 2708231.1667 | 247280 | 2956558.8067 | 269954.0094 | 903870 | 82529.5035 | 5443306 | 497011.0101 | 276182.5 | 25217.3483 | 65835 | 6011.1851 | 736376.6667 | 67236.2184 | 58520 | 5343.2756 | 1449700 | 132367.51 | 8933790.1667 | 815716.051 | 2989776.3729 | 272987 | 1495068.8958 | 136510 | 187071.9111 | 17080.943 | 82119.5203 | 7498.073 | 3176848.2841 | 290067.943 | 1577188.4162 | 144008.073 | 4971.0411 | 453.89 | 9900 | 903.9376 | 14871.0411 | 1357.8276 | 0 | 0 | 29659418.6102 | 2708107.463 | 4533747.2228 | 413962.0824 | 10952083.3333 | 30761663.591 | 40611501.9435 | 35295410.8139
971-2050R | oh | 3 | 25.443 | 25.443 | 20.7013 | 20.7013 | 4.6372 | 97634.57 | 4716.3438 | 187049.5 | 9035.629 | 97240 | 4697.2837 | 468564.6429 | 22634.5234 | 850488.7129 | 41083.78 | 7376600 | 356334.666 | 13488672.9313 | 651584.9801 | 4614393.4907 | 222903.2838 | 18103066.4219 | 874488.2639 | 25479666.4219 | 1230822.9299 | 4075000 | 196847.296 | 30405155.1348 | 1468754.0059 | 329259.81 | 15905.2523 | 146084.4 | 7056.7654 | 475344.21 | 22962.0178 | 5027938 | 242880 | 91085.8333 | 4400 | 5119023.8333 | 247280 | 5594368.0433 | 270242.0178 | 1674090 | 80868.7337 | 10081742 | 487009.4852 | 511527.5 | 24709.8909 | 124740 | 6025.701 | 1395240 | 67398.5819 | 110880 | 5356.1787 | 2746800 | 132687.1541 | 16645019.5 | 804055.7255 | 5651192.8146 | 272987 | 2825937.9792 | 136510 | 353462.2197 | 17074.376 | 155195.6863 | 7496.896 | 6004655.0343 | 290061.376 | 2981133.6654 | 144006.896 | 9396.1247 | 453.89 | 9900 | 478.2302 | 19296.1247 | 932.1202 | 0 | 0 | 53074125.7938 | 2563803.2276 | 8575501.7088 | 414248.9138 | 20701325.7576 | 9274365.7931 | 73775451.5514 | 17849867.5019
971-29R | oh | 3 | 7.461 | 7.461 | 3.8006 | 3.8006 | 0.69508 | 18344.7 | 4826.8309 | 35145 | 9247.3015 | 28050 | 7380.4754 | 88039.2857 | 23164.7695 | 169578.9857 | 44619.3773 | 1386000 | 364682.3142 | 2534406.1875 | 666849.2884 | 867005.04 | 228125.1114 | 3401411.2275 | 894974.3998 | 4787411.2275 | 1259656.7141 | 1400000 | 368365.974 | 6356990.2132 | 1672642.0654 | 61865.1 | 16277.8556 | 22383.9 | 5889.6194 | 84249 | 22167.475 | 923082 | 242880 | 16722.5 | 4400 | 939804.5 | 247280 | 1024053.5 | 269447.475 | 176220 | 46366.7514 | 1061236 | 279230.8806 | 53845 | 14167.6185 | 20790 | 5470.2347 | 232540 | 61185.5883 | 18480 | 4862.4309 | 457800 | 120455.6735 | 2020911 | 531739.1778 | 1037505.7062 | 272987 | 518815.5625 | 136510 | 65360.6438 | 17197.598 | 28570.2658 | 7517.367 | 1102866.35 | 290184.598 | 547385.8283 | 144027.367 | 1725.0399 | 453.89 | 9900 | 2604.8737 | 11625.0399 | 3058.7637 | 0 | 0 | 9492392.6031 | 2497624.6048 | 1571439.3283 | 413474.842 | 3800568.1818 | 1390152.2727 | 13292960.7849 | 2961591.6011
971-371R | oh | 3 | 2.547 | 2.547 | 2.4735 | 2.4735 | 0.32838 | 10395.33 | 4202.7062 | 19915.5 | 8051.5957 | 2805 | 1134.0276 | 49888.9286 | 20169.4903 | 83004.7586 | 33557.8197 | 785400 | 317527.7182 | 1436163.5063 | 580623.5309 | 491302.856 | 198627.8009 | 1927466.3623 | 779251.3318 | 2712866.3622 | 1096779.05 | 125000 | 50535.9877 | 2920871.1208 | 1180872.8574 | 35056.89 | 14173.0765 | 8835.75 | 3572.1868 | 43892.64 | 17745.2633 | 600760 | 242880 | 10883.3333 | 4400 | 611643.3333 | 247280 | 655535.9733 | 265025.2633 | 109890 | 44427.1975 | 661782 | 267550.4564 | 33577.5 | 13574.977 | 8415 | 3402.0827 | 94123.3333 | 38052.925 | 7480 | 3024.0735 | 185300 | 74914.5482 | 1100567.8333 | 444946.2603 | 675229.2083 | 272987 | 337655.4167 | 136510 | 42533.291 | 17195.695 | 18594.692 | 7517.609 | 717762.4994 | 290182.695 | 356250.1086 | 144027.609 | 1122.69 | 453.89 | 9900 | 4002.4502 | 11022.69 | 4456.3402 | 0 | 0 | 4750224.1436 | 1920458.153 | 1011786.082 | 409052.8723 | 2473484.8485 | 656751.1364 | 7223708.9921 | 1668537.2183
971-383R | oh | 3 | 18.9534 | 18.9534 | 9.7428 | 9.7428 | 3.6821 | 43415.79 | 4456.1909 | 83176.5 | 8537.2248 | 67787.5 | 6957.6999 | 208359.6429 | 21386.0059 | 402739.4329 | 41337.1215 | 3280200 | 336679.2893 | 5998094.6437 | 615643.632 | 2051911.928 | 210607.9659 | 8050006.5718 | 826251.5979 | 11330206.5718 | 1162930.8872 | 3500000 | 359239.5319 | 15232946.0046 | 1563507.5406 | 146414.07 | 15027.9206 | 87179.4 | 8948.082 | 233593.47 | 23976.0025 | 2366332 | 242880 | 42868.3333 | 4400 | 2409200.3333 | 247280 | 2642793.8033 | 271256.0025 | 440550 | 45217.9931 | 2653090 | 272312.8028 | 134612.5 | 13816.609 | 35145 | 3607.2781 | 393103.3333 | 40348.0736 | 31240 | 3206.4694 | 773900 | 79432.9925 | 4461640.8333 | 457942.2184 | 2659658.5708 | 272987 | 1329990.0417 | 136510 | 166646.4662 | 17104.571 | 73095.974 | 7502.561 | 2826305.037 | 290091.571 | 1403086.0157 | 144012.561 | 4422.1609 | 453.89 | 9900 | 1016.1347 | 14322.1609 | 1470.0247 | 0 | 0 | 22535214.0358 | 2313011.3547 | 4045879.819 | 415268.5635 | 9742803.0303 | 7364206.8182 | 32278017.0661 | 11410086.6372
971-388R | oh | 3 | 18.6674 | 18.6674 | 17.9011 | 17.9011 | 24.4244 | 70729.01 | 3951.0905 | 135503.5 | 7569.5474 | 58437.5 | 3264.4576 | 339440.3571 | 18961.9447 | 604110.3671 | 33747.0401 | 5343800 | 298517.3618 | 9771543.8562 | 545861.6513 | 3342786.0987 | 186735.972 | 13114329.9549 | 732597.6233 | 18458129.9549 | 1031114.9851 | 1750000 | 97759.157 | 20812240.3221 | 1162621.1822 | 238524.33 | 13324.5357 | 65973.6 | 3685.442 | 304497.93 | 17009.9777 | 4347828 | 242880 | 78765 | 4400 | 4426593 | 247280 | 4731090.93 | 264289.9777 | 1148400 | 64152.3519 | 6915920 | 386339.7194 | 350900 | 19602.1075 | 69300 | 3871.2626 | 775133.3333 | 43300.7893 | 61600 | 3441.1223 | 1526000 | 85245.9849 | 10847253.3333 | 605953.338 | 4886777.5125 | 272987 | 2443684.125 | 136510 | 306873.3628 | 17142.675 | 134426.4533 | 7509.381 | 5193650.8753 | 290129.675 | 2578110.5783 | 144019.381 | 8125.1468 | 453.89 | 9900 | 553.0375 | 18025.1468 | 1006.9275 | 0 | 0 | 36871169.6775 | 2059711.1227 | 7309201.5083 | 408309.3587 | 17901136.3636 | 48848817.0328 | 54772306.0411 | 56158018.5411
972-1582R | oh | 3 | 18.5087 | 18.5087 | 11.1523 | 11.1523 | 14.9558 | 39135.36 | 3509.1825 | 74976 | 6722.9346 | 10285 | 922.2335 | 187817.1429 | 16841.154 | 312213.5029 | 27995.5046 | 2956800 | 265129.8146 | 5406733.2 | 484809.9874 | 1849610.752 | 165850.5667 | 7256343.952 | 650660.5541 | 10213143.952 | 915790.3686 | 450000 | 40350.5197 | 10975357.4549 | 984136.3929 | 131978.88 | 11834.2587 | 66562.65 | 5968.5278 | 198541.53 | 17802.7865 | 2708664 | 242880 | 49070 | 4400 | 2757734 | 247280 | 2956275.53 | 265082.7865 | 310860 | 27874.139 | 1872068 | 167864.2592 | 94985 | 8517.098 | 52470 | 4704.8706 | 586886.6667 | 52624.8489 | 46640 | 4182.1072 | 1155400 | 103602.2009 | 4119309.6667 | 369369.5238 | 3044425.475 | 272987 | 1522396.75 | 136510 | 192105.9831 | 17225.725 | 83917.1832 | 7524.671 | 3236531.4581 | 290212.725 | 1606313.9332 | 144034.671 | 5061.9051 | 453.89 | 9900 | 887.7114 | 14961.9051 | 1341.6014 | 0 | 0 | 18346160.4847 | 1645060.2432 | 4562589.4632 | 409117.4575 | 11152272.7273 | 29911686.4848 | 29498433.212 | 34474275.948
972-1590F | oh | 3 | 23.1068 | 23.1068 | 20.6786 | 20.6786 | 8.1567 | 100080.53 | 4839.812 | 191735.5 | 9272.1709 | 192142.5 | 9291.8531 | 480303.2143 | 23227.0681 | 964261.7443 | 46630.9042 | 7561400 | 365663.0794 | 13826593.7562 | 668642.6919 | 4729994.1627 | 228738.624 | 18556587.9189 | 897381.3159 | 26117987.9189 | 1263044.3953 | 10775000 | 521070.13 | 37857249.6632 | 1830745.4294 | 337508.49 | 16321.6327 | 111919.5 | 5412.3349 | 449427.99 | 21733.9676 | 5022418 | 242880 | 90985.8333 | 4400 | 5113403.8333 | 247280 | 5562831.8233 | 269013.9676 | 1383030 | 66882.1923 | 8328914 | 402779.4246 | 422592.5 | 20436.2254 | 84645 | 4093.3625 | 946770 | 45785.0178 | 75240 | 3638.5445 | 1863900 | 90136.6696 | 13105091.5 | 633751.4368 | 5644988.5646 | 272987 | 2822835.4792 | 136510 | 355658.6183 | 17199.358 | 155501.1582 | 7519.908 | 6000647.1829 | 290186.358 | 2978336.6373 | 144029.908 | 9385.8091 | 453.89 | 9900 | 478.7559 | 19285.8091 | 932.6459 | 0 | 0 | 56982274.1551 | 2755615.87 | 8541168.4607 | 413043.8756 | 20678598.4848 | 16313311.1976 | 77660872.64 | 24854479.6583
972-32R | oh | 2 | 19.7432 | 19.7432 | 15.7093 | 15.7093 | 6.3199 | 78882.21 | 5021.3764 | 151123.5 | 9620.0142 | 145392.5 | 9255.198 | 378568.9286 | 24098.426 | 753967.1386 | 47995.0147 | 5959800 | 379380.8427 | 10897946.6062 | 693726.6632 | 3728121.672 | 237319.6989 | 14626068.2782 | 931046.3622 | 20585868.2783 | 1310427.2049 | 7975000 | 507661.7035 | 29314835.4168 | 1866083.9231 | 266019.93 | 16933.9349 | 110741.4 | 7049.4254 | 376761.33 | 23983.3603 | 3815470 | 242880 | 69120.8333 | 4400 | 3884590.8333 | 247280 | 4261352.1633 | 271263.3603 | 934560 | 59490.9494 | 5628128 | 358267.7176 | 285560 | 18177.7901 | 43560 | 2772.8832 | 487226.6667 | 31015.2125 | 38720 | 2464.7851 | 959200 | 61059.449 | 8376954.6667 | 533248.787 | 4288429.3021 | 272987 | 2144473.8542 | 136510 | 271542.9218 | 17285.51 | 118358.3677 | 7534.296 | 4559972.2239 | 290272.51 | 2262832.2219 | 144044.296 | 7130.2852 | 453.89 | 9900 | 630.2007 | 17030.2852 | 1084.0907 | 0 | 0 | 42268792.5926 | 2690689.3109 | 6524184.3852 | 415307.6563 | 15709280.303 | 12639701.1364 | 57978072.8956 | 19163885.5216
972-942R | oh | 3 | 8.8354 | 8.8354 | 7.8388 | 7.8388 | 9.2654 | 31797.48 | 4056.4086 | 60918 | 7771.317 | 27115 | 3459.064 | 152601.4286 | 19467.3837 | 272431.9086 | 34754.1733 | 2402400 | 306474.4739 | 4392970.725 | 560411.8347 | 1502808.736 | 191713.5018 | 5895779.461 | 752125.3365 | 8298179.461 | 1058599.8104 | 1425000 | 181787.4314 | 9995611.3696 | 1275141.4151 | 107232.84 | 13679.7071 | 36521.1 | 4659.0014 | 143753.94 | 18338.7084 | 1903894 | 242880 | 34490.8333 | 4400 | 1938384.8333 | 247280 | 2082138.7733 | 265618.7084 | 369270 | 47107.8209 | 2223826 | 283693.766 | 112832.5 | 14394.0564 | 39600 | 5051.777 | 442933.3333 | 56505.0617 | 35200 | 4490.4685 | 872000 | 111241.151 | 4095661.8333 | 522484.1016 | 2139897.5271 | 272987 | 1070078.1042 | 136510 | 136145.1491 | 17368.054 | 59169.2833 | 7548.233 | 2276042.6761 | 290355.054 | 1129247.3874 | 144058.233 | 3557.9646 | 453.89 | 9900 | 1262.9443 | 13457.9646 | 1716.8343 | 0 | 0 | 16380773.8437 | 2089697.405 | 3211386.1608 | 409676.9414 | 7838825.7576 | 18530750.5109 | 24219599.6012 | 21742136.6717
973-1226R | oh | 3 | 16.147 | 16.147 | 8.4831 | 8.4831 | 11.9646 | 33020.46 | 3892.479 | 63261 | 7457.2588 | 59840 | 7053.9885 | 158470.7143 | 18680.6584 | 314592.1743 | 37084.3848 | 2494800 | 294089.0804 | 4561931.1375 | 537764.2028 | 1560609.072 | 183965.8838 | 6122540.2095 | 721730.0865 | 8617340.2095 | 1015819.1669 | 1625000 | 191556.3394 | 10556932.3838 | 1244459.8912 | 111357.18 | 13126.8762 | 70686 | 8332.5239 | 182043.18 | 21459.4001 | 2060386 | 242880 | 37325.8333 | 4400 | 2097711.8333 | 247280 | 2279755.0133 | 268739.4001 | 249480 | 29408.908 | 1502424 | 177106.9795 | 76230 | 8986.0552 | 34650 | 4084.5706 | 387566.6667 | 45686.6781 | 30800 | 3630.7294 | 763000 | 89943.0689 | 3044150.6667 | 358846.9898 | 2315788.0146 | 272987 | 1158033.9792 | 136510 | 145750.0073 | 17181.131 | 63747.671 | 7514.628 | 2461538.0219 | 290168.131 | 1221781.6501 | 144024.628 | 3850.4142 | 453.89 | 9900 | 1167.0202 | 13750.4142 | 1620.9102 | 0 | 0 | 16076371.4866 | 1895095.9221 | 3501536.6635 | 412764.0281 | 8483143.9394 | 23929188.3735 | 24559515.4259 | 27430725.0369
973-1245R | oh | 3 | 7.9356 | 7.9356 | 3.3436 | 3.3436 | 4.3593 | 12229.8 | 3657.7175 | 23430 | 7007.4997 | 13557.5 | 4054.8091 | 58692.8571 | 17553.9983 | 107910.1571 | 32274.0246 | 924000 | 276352.1015 | 1689604.125 | 505330.7908 | 578003.36 | 172870.6095 | 2267607.485 | 678201.4003 | 3191607.485 | 954553.5018 | 750000 | 224311.7707 | 4049517.6421 | 1211139.2971 | 41243.4 | 12335.1734 | 21205.8 | 6342.2807 | 62449.2 | 18677.4542 | 812084 | 242880 | 14711.6667 | 4400 | 826795.6667 | 247280 | 889244.8667 | 265957.4542 | 147510 | 44117.6391 | 888338 | 265686.2264 | 45072.5 | 13480.3897 | 15345 | 4589.4188 | 171636.6667 | 51333.4995 | 13640 | 4079.4834 | 337900 | 101059.9298 | 1619442.1667 | 484346.5866 | 912748.5792 | 272987 | 456429.4583 | 136510 | 57473.259 | 17189.238 | 25131.3149 | 7516.333 | 970221.8382 | 290176.238 | 481560.7733 | 144026.333 | 1517.6087 | 453.89 | 9900 | 2960.9154 | 11417.6087 | 3414.8054 | 0 | 0 | 6650599.2557 | 1989076.9271 | 1370805.6399 | 409983.7872 | 3343560.6061 | 8718540.9809 | 9994159.8618 | 10089346.6208
973-626R | oh | 3 | 15.6144 | 15.6144 | 10.9061 | 10.9061 | 13.9338 | 40358.34 | 3700.5424 | 77319 | 7089.5443 | 71060 | 6515.6432 | 193686.4286 | 17759.5225 | 382423.7686 | 35065.2525 | 3049200 | 279587.6632 | 5575693.6125 | 511247.2609 | 1907411.088 | 174894.5982 | 7483104.7005 | 686141.8592 | 10532304.7005 | 965729.5224 | 2625000 | 240691.8588 | 13539728.4691 | 1241486.6337 | 136103.22 | 12479.5951 | 61261.2 | 5617.1703 | 197364.42 | 18096.7654 | 2648864 | 242880 | 47986.6667 | 4400 | 2696850.6667 | 247280 | 2894215.0867 | 265376.7654 | 243540 | 22330.703 | 1466652 | 134480.4557 | 74415 | 6823.2704 | 47025 | 4311.8227 | 525983.3333 | 48228.5357 | 41800 | 3832.7313 | 1035500 | 94947.2076 | 3434915.3333 | 314954.7263 | 2977212.7667 | 272987 | 1488786.3333 | 136510 | 187291.2402 | 17173.134 | 81939.0328 | 7513.165 | 3164504.0069 | 290160.134 | 1570725.3662 | 144023.165 | 4950.1518 | 453.89 | 9900 | 907.7522 | 14850.1518 | 1361.6422 | 0 | 0 | 20153997.9611 | 1847963.1362 | 4464940.4528 | 409399.9304 | 10906060.6061 | 27867523.5861 | 31060058.5672 | 32332464.0389
974-23R | oh | 3 | 26.7687 | 26.7687 | 16.1822 | 16.1822 | 22.2326 | 62779.64 | 3879.5499 | 120274 | 7432.4889 | 77137.5 | 4766.8126 | 301290 | 18618.6091 | 561481.14 | 34697.4605 | 4743200 | 293112.2399 | 8673301.175 | 535977.9757 | 2967083.9147 | 183354.8263 | 11640385.0897 | 719332.8021 | 16383585.0897 | 1012445.0419 | 2075000 | 128227.3355 | 19020066.2297 | 1175369.8379 | 211716.12 | 13083.2742 | 107207.1 | 6625.0028 | 318923.22 | 19708.277 | 3930332 | 242880 | 71201.6667 | 4400 | 4001533.6667 | 247280 | 4320456.8867 | 266988.277 | 600930 | 37135.2543 | 3618934 | 223636.7538 | 183617.5 | 11346.8833 | 77715 | 4802.4999 | 869256.6667 | 53716.8512 | 69080 | 4268.8888 | 1711300 | 105752.0189 | 7130833.1667 | 440659.1503 | 4417529.4042 | 272987 | 2209031.7083 | 136510 | 277575.9594 | 17153.169 | 121523.8006 | 7509.722 | 4695105.3636 | 290140.169 | 2330555.5089 | 144019.722 | 7344.9374 | 453.89 | 9900 | 611.7834 | 17244.9374 | 1065.6734 | 0 | 0 | 30863249.6973 | 1907234.8307 | 6651012.3956 | 411007.999 | 16182196.9697 | 44465299.3414 | 47045446.667 | 51116311.737
974-715R | oh | 3 | 10.139 | 10.139 | 8.7187 | 8.7187 | 12.4541 | 24255.77 | 2782.0238 | 46469.5 | 5329.8351 | 20570 | 2359.2832 | 116407.5 | 13351.3978 | 207702.77 | 23822.5399 | 1832600 | 210190.681 | 3351048.1812 | 384349.6122 | 1146373.3307 | 131483.6795 | 4497421.5119 | 515833.2917 | 6330021.5119 | 726023.9727 | 550000 | 63082.4373 | 7087724.2819 | 812928.9499 | 81799.41 | 9382.0112 | 18260.55 | 2094.4 | 100059.96 | 11476.4112 | 2117610 | 242880 | 38362.5 | 4400 | 2155972.5 | 247280 | 2256032.46 | 258756.4112 | 76230 | 8743.2258 | 459074 | 52653.6487 | 23292.5 | 2671.5412 | 35640 | 4087.7419 | 398640 | 45722.1505 | 31680 | 3633.5484 | 784800 | 90012.9032 | 1809356.5 | 207524.7599 | 2380105.4062 | 272987 | 1190196.5625 | 136510 | 149726.4398 | 17172.925 | 65503.1056 | 7512.901 | 2529831.8461 | 290159.925 | 1255699.6681 | 144022.901 | 3957.3534 | 453.89 | 9900 | 1135.4839 | 13857.3534 | 1589.3739 | 0 | 0 | 11440769.9814 | 1312203.0086 | 3511732.1281 | 402779.3122 | 8718750 | 24908289.7098 | 20159519.9814 | 28420021.8379
975-22R | oh | 3 | 22.8629 | 22.8629 | 1.6544 | 1.6544 | 2.2795 | 6318.73 | 3819.4498 | 12105.5 | 7317.3486 |  |  | 30324.6429 | 18330.1791 | 48748.8729 | 29466.9775 | 477400 | 288571.494 | 872962.1312 | 527674.8773 | 298635.0693 | 180514.3865 | 1171597.2006 | 708189.2638 | 1648997.2006 | 996760.7578 | 0 | 0 | 1697746.0734 | 1026227.7353 | 21309.09 | 12880.5948 | 103672.8 | 62666.558 | 124981.89 | 75547.1527 | 401810 | 242880 | 7279.1667 | 4400 | 409089.1667 | 247280 | 534071.0567 | 322827.1527 | 18810 | 11369.9828 | 113278 | 68472.5633 | 5747.5 | 3474.1614 | 2475 | 1496.0504 | 27683.3333 | 16733.6005 | 2200 | 1329.8226 | 54500 | 32943.3314 | 224693.8333 | 135819.5123 | 451617.6979 | 272987 | 225836.1458 | 136510 | 40182.0555 | 24288.638 | 28717.368 | 17358.638 | 491799.7534 | 297275.638 | 254553.5138 | 153868.638 | 750.8957 | 453.89 | 9900 | 5984.2015 | 10650.8957 | 6438.0915 | 0 | 0 | 2424890.5558 | 1465760.9771 | 788624.5705 | 476695.7907 | 1654356.0606 | 4558978.0673 | 4079246.6164 | 5347602.6378
991-1 | oh | 2 | 7.993 | 7.993 | 1.2636 | 1.2636 | 1.6708 | 5911.07 | 4677.8252 | 11324.5 | 8961.8345 | 10752.5 | 8509.1727 | 28368.2143 | 22449.666 | 56356.2843 | 44598.4984 | 446600 | 353424.4604 | 816641.9938 | 646263.4483 | 279368.2907 | 221082.82 | 1096010.2844 | 867346.2682 | 1542610.2844 | 1220770.7287 | 575000 | 455035.9712 | 2173966.5687 | 1720405.1983 | 19934.31 | 15775.3532 | 38288.25 | 30300.054 | 58222.56 | 46075.4072 | 306912 | 242880 | 5560 | 4400 | 312472 | 247280 | 370694.56 | 293355.4072 | 198000 | 156690.6475 | 1192400 | 943625.8993 | 60500 | 47877.6978 | 6435 | 5092.446 | 71976.6667 | 56959.952 | 5720 | 4526.6187 | 141700 | 112136.6906 | 1676731.6667 | 1326909.952 | 344956.3 | 272987 | 172499 | 136510 | 18686.6596 | 14788.004 | 8963.6235 | 7093.515 | 363642.9596 | 287775.004 | 181462.6235 | 143603.515 | 573.5519 | 453.89 | 9900 | 7834.5324 | 10473.5519 | 8288.4224 | 0 | 0 | 4224814.7469 | 3343378.5767 | 552157.1835 | 436958.9222 | 1263636.3636 | 3341663.4936 | 5488451.1105 | 3893820.6771
991-1206R | oh | 2 | 9.2991 | 9.2991 | 9.0301 | 9.0301 | 12.1377 | 32408.97 | 3588.9881 | 62089.5 | 6875.8271 | 37867.5 | 4193.4688 | 155536.0714 | 17224.1544 | 287902.0414 | 31882.4384 | 2448600 | 271159.3783 | 4477450.9313 | 495835.5024 | 1531708.904 | 169622.3288 | 6009159.8352 | 665457.8311 | 8457759.8352 | 936617.2095 | 1850000 | 204870.0686 | 10595661.8767 | 1173369.7164 | 109295.01 | 12103.3925 | 8835.75 | 978.4761 | 118130.76 | 13081.8686 | 2193234 | 242880 | 39732.5 | 4400 | 2232966.5 | 247280 | 2351097.26 | 260361.8686 | 389070 | 43085.8365 | 2343066 | 259472.4822 | 118882.5 | 13165.1167 | 26730 | 2960.0956 | 298980 | 33109.2179 | 23760 | 2631.1961 | 588600 | 65181.904 | 3789088.5 | 419605.8491 | 2465103.6312 | 272987 | 1232700.8125 | 136510 | 133643.641 | 14799.774 | 64073.8215 | 7095.572 | 2598747.2723 | 287786.774 | 1296774.634 | 143605.572 | 4098.6783 | 453.89 | 9900 | 1096.3317 | 13998.6783 | 1550.2217 | 0 | 0 | 16997496.3272 | 1882312.5612 | 3647871.894 | 403967.4406 | 9030113.6364 | 24275323.3869 | 26027609.9636 | 27923195.2809
CB 1023 | oh | 2 | 4.8884 | 4.8884 | 3.8564 | 3.8564 | 4.5838 | 15694.91 | 4069.793 | 30068.5 | 7796.959 | 7480 | 1939.613 | 75322.5 | 19531.6177 | 128565.91 | 33337.9828 | 1185800 | 307485.7087 | 2168325.2938 | 562260.9543 | 741770.9787 | 192346.0744 | 2910096.2724 | 754607.0287 | 4095896.2724 | 1062092.7374 | 375000 | 97239.9568 | 4599462.1824 | 1192670.6769 | 52929.03 | 13724.8442 | 4123.35 | 1069.2117 | 57052.38 | 14794.0559 | 936652 | 242880 | 16968.3333 | 4400 | 953620.3333 | 247280 | 1010672.7133 | 262074.0559 | 200970 | 52112.8376 | 1210286 | 313835.0889 | 61407.5 | 15923.3671 | 15840 | 4107.4158 | 177173.3333 | 45942.2061 | 14080 | 3651.0362 | 348800 | 90446.1251 | 2028556.8333 | 526018.0768 | 1052757.8208 | 272987 | 526442.5417 | 136510 | 61438.0081 | 15931.278 | 28133.7512 | 7295.266 | 1114195.8289 | 288918.278 | 554576.2929 | 143805.266 | 1750.3993 | 453.89 | 9900 | 2567.1349 | 11650.3993 | 3021.0249 | 0 | 0 | 7753865.2439 | 2010628.0566 | 1565249.0062 | 405879.3219 | 3856439.3939 | 9167551.6128 | 11610304.6379 | 10732800.619
CB 1090 | oh | 2 | 8.9062 | 8.1292 | 4.5962 | 4.5962 | 6.342 | 17325.55 | 3769.5279 | 33192.5 | 7221.7076 | 28985 | 6306.2799 | 83148.2143 | 18090.5955 | 162651.2643 | 35388.1109 | 1309000 | 284799.7363 | 2393605.8438 | 520777.9321 | 818838.0933 | 178154.9832 | 3212443.9371 | 698932.9153 | 4521443.9371 | 983732.6515 | 875000 | 190374.1553 | 5559095.2014 | 1209494.9177 | 58428.15 | 12712.2397 | 20027.7 | 4357.436 | 78455.85 | 17069.6756 | 1116328 | 242880 | 20223.3333 | 4400 | 1136551.3333 | 247280 | 1215007.1833 | 264349.6756 | 137610 | 29939.8714 | 828718 | 180304.5591 | 42047.5 | 9148.294 | 12375 | 2692.4345 | 138416.6667 | 30115.3783 | 11000 | 2393.2751 | 272500 | 59287.9512 | 1442667.1667 | 313881.7636 | 1254706.1583 | 272987 | 627428.9167 | 136510 | 64435.5341 | 14019.269 | 31980.0165 | 6957.907 | 1319141.6924 | 287006.269 | 659408.9332 | 143467.907 | 2086.1747 | 453.89 | 9900 | 2153.9476 | 11986.1747 | 2607.8376 | 0 | 0 | 8332890.2352 | 1812990.7879 | 1874416.1165 | 407817.5826 | 4596212.1212 | 12683995.2919 | 12929102.3564 | 14558411.4084
CB 1101 | oh | 2 | 4.6873 | 4.6873 | 3.0366 | 3.0366 | 4.173 | 8357.03 | 2752.1436 | 16010.5 | 5272.5903 | 9817.5 | 3233.1067 | 40106.7857 | 13207.9978 | 74291.8157 | 24465.8384 | 631400 | 207933.1379 | 1154562.8188 | 380221.5233 | 394968.9627 | 130071.4852 | 1549531.7814 | 510293.0085 | 2180931.7814 | 718226.1464 | 325000 | 107029.2522 | 2580223.5971 | 849721.237 | 28182.99 | 9281.2441 | 1767.15 | 581.9592 | 29950.14 | 9863.2033 | 737518 | 242880 | 13360.8333 | 4400 | 750878.8333 | 247280 | 780828.9733 | 257143.2033 | 49500 | 16301.3784 | 298100 | 98170.5233 | 15125 | 4980.9767 | 9900 | 3260.2757 | 110733.3333 | 36466.7873 | 8800 | 2898.0228 | 218000 | 71791.9291 | 710158.3333 | 233869.8933 | 828939.5021 | 272987 | 414519.8542 | 136510 | 48669.4742 | 16027.869 | 22205.0704 | 7312.591 | 877608.9763 | 289014.869 | 436724.9245 | 143822.591 | 1378.2611 | 453.89 | 9900 | 3260.2757 | 11278.2611 | 3714.1657 | 0 | 0 | 4179269.1678 | 1376320.165 | 1217553.8979 | 400965.7943 | 3036553.0303 | 8345971.8868 | 7215822.1981 | 9563525.7847
CB 1106 | oh | 2 | 21.3295 | 21.3295 | 1.2773 | 1.2773 | 1.6177 | 4891.92 | 3829.973 | 9372 | 7337.5089 | 10285 | 8052.3132 | 23477.1429 | 18380.6812 | 48026.0629 | 37600.4763 | 369600 | 289366.548 | 675841.65 | 529128.694 | 231201.344 | 181011.7284 | 907042.994 | 710140.4223 | 1276642.994 | 999506.9704 | 350000 | 274021.3523 | 1674669.0569 | 1311128.799 | 16497.36 | 12916.0826 | 116042.85 | 90852.0534 | 132540.21 | 103768.1359 | 310224 | 242880 | 5620 | 4400 | 315844 | 247280 | 448384.21 | 351048.1359 | 192060 | 150367.2598 | 1156628 | 905545.0534 | 58685 | 45945.5516 | 3465 | 2712.8114 | 38756.6667 | 30343.2977 | 3080 | 2411.3879 | 76300 | 59736.6548 | 1528974.6667 | 1197062.0166 | 348678.85 | 272987 | 174360.5 | 136510 | 20326.711 | 15914.151 | 9314.3351 | 7292.362 | 369005.561 | 288901.151 | 183674.8351 | 143802.362 | 579.7413 | 453.89 | 9900 | 7750.8897 | 10479.7413 | 8204.7797 | 0 | 0 | 3583129.0259 | 2805296.7462 | 632059.0451 | 494850.4979 | 1277272.7273 | 3235377.7868 | 4860401.7532 | 3867436.8319
CB 1138 | oh | 2 | 9.0371 | 2.9983 | 2.589 | 4.9684 | 5.6873 | 33224.29 | 6687.1593 | 63651.5 | 12811.3414 | 70125 | 14114.2835 | 68475 | 13782.1827 | 235475.79 | 47394.9671 | 2510200 | 505236.0005 | 4590091.2062 | 923862.3706 | 1570242.4613 | 316047.7336 | 6160333.6676 | 1239910.1043 | 8670533.6676 | 1745146.1047 | 1300000 | 261655.1672 | 10206009.4576 | 2054196.2389 | 112044.57 | 22551.5698 | 47124 | 9484.7985 | 159168.57 | 32036.3683 | 1206718 | 242880 | 21860.8333 | 4400 | 1228578.8333 | 247280 | 1387747.4033 | 279316.3683 | 263340 | 53003.2859 | 1585892 | 319197.5664 | 80465 | 16195.4485 | 25245 | 5081.1421 | 282370 | 56833.515 | 22440 | 4516.5707 | 555900 | 111887.7749 | 2815652 | 566715.3036 | 706767.4792 | 142253.3561 | 353426.4583 | 71135.2762 | 43111.7625 | 8677.2426 | 19214.4096 | 3867.3458 | 749879.2417 | 150930.5987 | 372640.8679 | 75002.622 | 2255.094 | 453.89 | 9900 | 1992.6047 | 12155.094 | 2446.4947 | 0 | 0 | 13783695.7933 | 2774288.636 | 1760388.2713 | 354318.9903 | 4968371.2121 | 11374673.7166 | 18752067.0054 | 13135061.9878
CB 1162 | oh | 2 | 1.993 | 1.993 | 1.5536 | 1.5536 | 1.6602 | 6318.73 | 4067.1577 | 12105.5 | 7791.9103 | 5142.5 | 3310.0573 | 30324.6429 | 19518.9704 | 53891.3729 | 34688.0957 | 477400 | 307286.6025 | 872962.1312 | 561896.8735 | 298635.0693 | 192221.5246 | 1171597.2006 | 754118.398 | 1648997.2006 | 1061405.0005 | 250000 | 160916.7378 | 1952888.5734 | 1257009.8339 | 21309.09 | 13715.957 | 1767.15 | 1137.4561 | 23076.24 | 14853.413 | 377338 | 242880 | 6835.8333 | 4400 | 384173.8333 | 247280 | 407250.0733 | 262133.413 | 11880 | 7646.7634 | 71544 | 46050.5084 | 3630 | 2336.511 | 2475 | 1593.0757 | 27683.3333 | 17818.8468 | 2200 | 1416.0673 | 54500 | 35079.8488 | 173912.3333 | 111941.6214 | 424112.1896 | 272987 | 212081.7292 | 136510 | 24381.4693 | 15693.546 | 11268.1535 | 7252.938 | 448493.6589 | 288680.546 | 223349.8827 | 143762.938 | 705.1628 | 453.89 | 9900 | 6372.3028 | 10605.1628 | 6826.1928 | 0 | 0 | 2585899.7285 | 1664458.1941 | 630599.956 | 405896.351 | 1553598.4848 | 3320459.2367 | 4139498.2133 | 3951059.1927
CB 1234 | oh | 3 | 58.7422 | 58.7422 | 17.9339 | 17.9339 | 24.1903 | 71340.5 | 3977.9688 | 136675 | 7621.0411 | 96772.5 | 5396.0651 | 342375 | 19090.9379 | 647163 | 36086.0128 | 5390000 | 300548.0986 | 9856024.0625 | 549575.0077 | 3371686.2667 | 188006.2887 | 13227710.3292 | 737581.2964 | 18617710.3292 | 1038129.395 | 3725000 | 207707.1739 | 22989873.3292 | 1281922.5816 | 240586.5 | 13415.1791 | 242688.6 | 13532.3928 | 483275.1 | 26947.5719 | 4355786 | 242880 | 78909.1667 | 4400 | 4434695.1667 | 247280 | 4917970.2667 | 274227.5719 | 1311750 | 73143.5934 | 7899650 | 440486.9734 | 400812.5 | 22349.4313 | 68805 | 3836.5885 | 769596.6667 | 42912.9527 | 61160 | 3410.3009 | 1515100 | 84482.4535 | 12026874.1667 | 670622.2936 | 4895721.9729 | 272987 | 2448156.8958 | 136510 | 277863.6377 | 15493.764 | 129428.1961 | 7216.957 | 5173585.6106 | 288480.764 | 2577585.0919 | 143726.957 | 8140.0186 | 453.89 | 9900 | 552.0271 | 18040.0186 | 1005.9171 | 0 | 0 | 40208373.125 | 2242031.5563 | 7495555.3586 | 417954.5289 | 17933901.5152 | 48380522.4678 | 58142274.6401 | 55876077.8263
CB 1235 | oh | 2 | 41.3417 | 41.3417 | 17.4856 | 17.4856 | 21.3362 | 86220.09 | 4930.918 | 165181.5 | 9446.7129 | 153340 | 8769.4987 | 413784.6429 | 23664.3009 | 818526.2329 | 46811.4305 | 6514200 | 372546.4235 | 11911709.0813 | 681229.4089 | 4074923.688 | 233044.4638 | 15986632.7692 | 914273.8727 | 22500832.7693 | 1286820.2961 | 7500000 | 428924.2234 | 30819359.0021 | 1762555.95 | 290765.97 | 16628.8757 | 276264.45 | 15799.5353 | 567030.42 | 32428.411 | 4246904 | 242880 | 76936.6667 | 4400 | 4323840.6667 | 247280 | 4890871.0867 | 279708.411 | 2060190 | 117822.0528 | 12406922 | 709550.5845 | 629502.5 | 36001.1828 | 67320 | 3850.0238 | 752986.6667 | 43063.2295 | 59840 | 3422.2434 | 1482400 | 84778.3025 | 17459161.1667 | 998487.6193 | 4773343.1417 | 272987 | 2386960.0833 | 136510 | 245449.8936 | 14037.254 | 121718.0382 | 6961.042 | 5018793.0353 | 287024.254 | 2508678.1215 | 143471.042 | 7936.5417 | 453.89 | 9900 | 566.18 | 17836.5417 | 1020.07 | 0 | 0 | 53315149.7458 | 3049087.8933 | 7399549.2082 | 423179.453 | 17485606.0606 | 42672461.6229 | 70800755.8064 | 50072010.8311
CB 1243 | oh | 2 | 7.0297 | 7.0297 | 5.0473 | 5.0473 | 7.2047 | 21809.81 | 4321.043 | 41783.5 | 8278.3069 | 31322.5 | 6205.7336 | 104668.9286 | 20737.4087 | 199584.7386 | 39542.4923 | 1647800 | 326468.4428 | 3013127.3563 | 596972.3242 | 1030772.6587 | 204220.6243 | 4043900.0149 | 801192.9485 | 5691700.0149 | 1127661.3913 | 1125000 | 222889.3058 | 7016284.7535 | 1390093.1894 | 73550.73 | 14572.1521 | 17671.5 | 3501.1452 | 91222.23 | 18073.2974 | 1225900 | 242880 | 22208.3333 | 4400 | 1248108.3333 | 247280 | 1339330.5633 | 265353.2974 | 289080 | 57273.636 | 1740904 | 344914.5636 | 88330 | 17500.2777 | 16335 | 3236.3527 | 182710 | 36199.2045 | 14520 | 2876.758 | 359700 | 71265.1407 | 2691579 | 533265.9332 | 1377860.5208 | 272987 | 689013.5417 | 136510 |  |  |  |  | 1377860.5208 | 272987 | 689013.5417 | 136510 | 2290.941 | 453.89 | 9900 | 1961.4259 | 12190.941 | 2415.3159 | 0 | 0 | 11097915.2153 | 2198761.4385 | 2028344.105 | 401863.2974 | 5047348.4848 | 14409315.4099 | 16145263.7002 | 16437659.5149
CB 1250 | oh | 2 | 2.6504 | 2.6504 | 2.5689 | 2.5689 | 3.4661 | 6318.73 | 2459.6649 | 12105.5 | 4712.256 | 467.5 | 181.9817 | 30324.6429 | 11804.3434 | 49216.3729 | 19158.246 | 477400 | 185835.4468 | 872962.1312 | 339814.218 | 298635.0693 | 116248.3903 | 1171597.2006 | 456062.6083 | 1648997.2006 | 641898.0551 | 25000 | 9731.6426 | 1723213.5734 | 670787.9437 | 21309.09 | 8294.8979 | 1178.1 | 458.5939 | 22487.19 | 8753.4918 | 623944 | 242880 | 11303.3333 | 4400 | 635247.3333 | 247280 | 657734.5233 | 256033.4918 | 86130 | 33527.455 | 518694 | 201909.7847 | 26317.5 | 10244.5001 | 10890 | 4239.1035 | 121806.6667 | 47415.1578 | 9680 | 3768.092 | 239800 | 93345.9157 | 1013318.1667 | 394450.0088 | 701287.0583 | 272987 | 350685.9167 | 136510 | 41919.7115 | 16317.906 | 18916.0436 | 7363.367 | 743206.7699 | 289304.906 | 369601.9602 | 143873.367 | 1166.0159 | 453.89 | 9900 | 3853.7305 | 11066.0159 | 4307.6205 | 0 | 0 | 3490804.5259 | 1358850.479 | 1027336.4836 | 399906.8588 | 2568939.3939 | 6932271.5611 | 6059743.9198 | 7959608.0446
CB 1299 | oh | 2 | 5.4517 | 2.972 | 2.69 | 4.3905 | 5.8616 | 14268.1 | 3249.7441 | 27335 | 6225.8994 | 17297.5 | 3939.7291 | 29346.4286 | 6684.0282 | 88247.0286 | 20099.4009 | 1078000 | 245528.4272 | 1971204.8125 | 448967.363 | 674337.2533 | 153589.0216 | 2645542.0658 | 602556.3846 | 3723542.0658 | 848084.8118 | 0 | 0 | 3811789.0944 | 868184.2127 | 48117.3 | 10959.3367 | 7657.65 | 1744.1287 | 55774.95 | 12703.4654 | 1066372 | 242880 | 19318.3333 | 4400 | 1085690.3333 | 247280 | 1141465.2833 | 259983.4654 | 44550 | 10146.8381 | 268290 | 61106.5137 | 13612.5 | 3100.4227 | 990 | 225.4853 | 11073.3333 | 2522.0947 | 880 | 200.4314 | 21800 | 4965.2316 | 361195.8333 | 82267.0175 | 734324.6896 | 167251.9352 | 367206.7292 | 83636.0767 |  |  |  |  | 734324.6896 | 167251.9352 | 367206.7292 | 83636.0767 | 1992.8178 | 453.89 | 9900 | 2254.8529 | 11892.8178 | 2708.7429 | 0 | 0 | 4919202.4351 | 1120411.9083 | 1508672.0125 | 343619.5421 | 4390530.303 | 11723107.5232 | 9309732.7382 | 13231779.5357
CB 200 | oh | 2 | 40.1133 | 24.921 | 4.915 | 9.5201 | 12.1408 | 58499.21 | 6144.8261 | 112073.5 | 11772.3328 | 125290 | 13160.6096 | 101734.2857 | 10686.2895 | 397596.9957 | 41764.058 | 4419800 | 464261.0114 | 8081939.7313 | 848936.4935 | 2764782.7387 | 290416.0438 | 10846722.4699 | 1139352.5373 | 15266522.4699 | 1603613.5487 | 2150000 | 225838.539 | 17814119.4656 | 1871216.1457 | 197280.93 | 20722.6219 | 239154.3 | 25121.0501 | 436435.23 | 45843.672 | 2312236 | 242880 | 41888.3333 | 4400 | 2354124.3333 | 247280 | 2790559.5633 | 293123.672 | 357390 | 37540.6676 | 2152282 | 226078.2429 | 109202.5 | 11470.7596 | 3465 | 363.9677 | 38756.6667 | 4071.046 | 3080 | 323.5268 | 76300 | 8014.6421 | 2740476.1667 | 287862.8528 | 1341720.7646 | 140935.9336 | 670941.4792 | 70476.4853 | 70745.8321 | 7431.2257 | 34521.4259 | 3626.1713 | 1412466.5967 | 148367.1593 | 705462.905 | 74102.6566 | 4321.0672 | 453.89 | 9900 | 1039.9077 | 14221.0672 | 1493.7977 | 0 | 0 | 21981283.2961 | 2308939.9555 | 3496022.4684 | 367226.3286 | 9520075.7576 | 24281511.2735 | 31501359.0537 | 27777533.7419
CB 202 | oh | 2 | 12.4667 | 12.3087 | 11.567 | 11.567 | 14.7303 | 38523.87 | 3330.4849 | 73804.5 | 6380.5836 | 79475 | 6870.8125 | 184882.5 | 15983.5544 | 376685.87 | 32565.4353 | 2910600 | 251628.6472 | 5322252.9938 | 460122.0782 | 1820710.584 | 157404.9822 | 7142963.5778 | 617527.0605 | 10053563.5777 | 869155.7077 | 2350000 | 203163.3756 | 12780249.4478 | 1104884.5185 | 129916.71 | 11231.6244 | 17082.45 | 1476.8205 | 146999.16 | 12708.4449 | 2809404 | 242880 | 50895 | 4400 | 2860299 | 247280 | 3007298.16 | 259988.4449 | 336600 | 29099.9116 | 2027080 | 175246.1342 | 102850 | 8891.6397 | 3960 | 342.3519 | 44293.3333 | 3829.2694 | 3520 | 304.3128 | 87200 | 7538.658 | 2605503.3333 | 225252.2776 | 3157653.0375 | 272987 | 1579017.375 | 136510 |  |  |  |  | 3157653.0375 | 272987 | 1579017.375 | 136510 | 5250.1663 | 453.89 | 9900 | 855.8798 | 15150.1663 | 1309.7698 | 0 | 0 | 18558555.9848 | 1604433.5658 | 4586315.535 | 396498.4449 | 11567045.4545 | 29460681.8876 | 30125601.4394 | 34046997.4226
CB 203 | oh | 2 | 8.1913 | 5.2121 | 3.1794 | 3.4659 | 4.5235 | 24459.6 | 7057.1961 | 46860 | 13520.2623 | 50490 | 14567.6066 | 107603.5714 | 31046.2763 | 229413.1714 | 66191.3413 | 1848000 | 533193.4426 | 3379208.25 | 974984.6754 | 1156006.72 | 333536.3651 | 4535214.97 | 1308521.0405 | 6383214.97 | 1841714.4831 | 2275000 | 656393.4426 | 8887628.1414 | 2564299.267 | 82486.8 | 23799.4702 | 55959.75 | 16145.7639 | 138446.55 | 39945.2341 | 841800 | 242880 | 15250 | 4400 | 857050 | 247280 | 995496.55 | 287225.2341 | 310860 | 89690.7541 | 1872068 | 540137.6525 | 94985 | 27405.5082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2277913 | 657233.9148 | 867922.8729 | 250417.0912 | 434013.8958 | 125223.6814 | 45819.2422 | 13219.9781 | 22340.6292 | 6445.8209 | 913742.1151 | 263637.0693 | 456354.5251 | 131669.5023 | 1573.1415 | 453.89 | 9900 | 2856.3934 | 11473.1415 | 3310.2834 | 0 | 0 | 12090756.398 | 3488480.5345 | 1451851.0751 | 418894.7364 | 3465909.0909 | 9046980.0502 | 15556665.4889 | 10498831.1252
CB 204 | oh | 2 | 28.4297 | 28.4297 | 14.5576 | 14.5576 | 20.6359 | 45250.26 | 3108.3651 | 86691 | 5955.0437 | 87422.5 | 6005.2925 | 217163.5714 | 14917.5642 | 436527.3314 | 29986.2655 | 3418800 | 234846.7943 | 6251535.2625 | 429435.1866 | 2138612.432 | 146907.182 | 8390147.6945 | 576342.3687 | 11808947.6945 | 811189.163 | 4000000 | 274771.0241 | 16245475.0259 | 1115946.4527 | 152600.58 | 10482.5544 | 71275.05 | 4896.0796 | 223875.63 | 15378.634 | 3535744 | 242880 | 64053.3333 | 4400 | 3599797.3333 | 247280 | 3823672.9633 | 262658.634 | 496980 | 34138.9259 | 2992924 | 205592.1982 | 151855 | 10431.3385 | 23760 | 1632.1399 | 265760 | 18255.7868 | 21120 | 1450.791 | 523200 | 35940.05 | 4475599 | 307441.2302 | 3974028.9333 | 272987 | 1987254.6667 | 136510 | 209790.3597 | 14411.078 | 102291.572 | 7026.69 | 4183819.2931 | 287398.078 | 2089546.2387 | 143536.69 | 6607.5381 | 453.89 | 9900 | 680.0583 | 16507.5381 | 1133.9483 | 0 | 0 | 24921400.8571 | 1711919.7092 | 5913219.202 | 406195.324 | 14557575.7576 | 41271861.5908 | 39478976.6146 | 47185080.7928
CB 231 | oh | 2 | 11.4737 | 11.4737 | 7.2144 | 7.2144 | 0.10461 | 35466.42 | 4916.0637 | 67947 | 9418.2548 | 59840 | 8294.529 | 170209.2857 | 23593.0124 | 333462.7057 | 46221.8599 | 2679600 | 371424.1311 | 4899851.9625 | 679177.2121 | 1676209.744 | 232342.4196 | 6576061.7065 | 911519.6317 | 9255661.7065 | 1282943.7627 | 2800000 | 388112.9896 | 12389124.4122 | 1717278.6122 | 119605.86 | 16578.7814 | 77754.6 | 10777.7037 | 197360.46 | 27356.4851 | 1752232 | 242880 | 31743.3333 | 4400 | 1783975.3333 | 247280 | 1981335.7933 | 274636.4851 | 564300 | 78218.6286 | 3398340 | 471049.9632 | 172425 | 23900.1365 | 38610 | 5351.8009 | 431860 | 59860.8842 | 34320 | 4757.1564 | 850200 | 117847.7371 | 5490055 | 760986.3068 | 1969435.7583 | 272987 | 984836.9167 | 136510 | 101275.7559 | 14038.013 | 50220.6515 | 6961.174 | 2070711.5142 | 287025.013 | 1035057.5682 | 143471.174 | 3274.5413 | 453.89 | 9900 | 1372.2566 | 13174.5413 | 1826.1466 | 0 | 0 | 19963065.4677 | 2767116.0787 | 3016393.3615 | 418107.6591 | 7214393.9394 | 209226.1163 | 27177459.4071 | 3225619.4778
CB 232 | oh | 2 | 15.7966 | 15.7966 | 4.8062 | 4.8062 | 5.9273 | 30574.5 | 6361.4044 | 58575 | 12187.2562 | 51425 | 10699.6099 | 146732.1429 | 30529.4445 | 287306.6429 | 59777.715 | 2310000 | 480624.1873 | 4224010.3125 | 878857.8023 | 1445008.4 | 300651.9428 | 5669018.7125 | 1179509.7451 | 7979018.7125 | 1660133.9324 | 2450000 | 509752.9259 | 10716325.3554 | 2229664.5733 | 103108.5 | 21453.0039 | 96604.2 | 20099.7035 | 199712.7 | 41552.7074 | 1167342 | 242880 | 21147.5 | 4400 | 1188489.5 | 247280 | 1388202.2 | 288832.7074 | 522720 | 108758.3875 | 3147936 | 654967.1782 | 159720 | 33231.7295 | 14850 | 3089.7269 | 166100 | 34559.1678 | 13200 | 2746.4239 | 327000 | 68036.4109 | 4351526 | 905389.0247 | 1312043.7687 | 272987 | 656101.1875 | 136510 | 67468.7197 | 14037.705 | 33456.8253 | 6961.108 | 1379512.4884 | 287024.705 | 689558.0128 | 143471.108 | 2181.5088 | 453.89 | 9900 | 2059.8179 | 12081.5088 | 2513.7079 | 0 | 0 | 16459445.3526 | 3424592.0109 | 2077760.2128 | 432303.8154 | 4806250 | 11854551.2228 | 21265695.3526 | 13932311.4356
CB 233 | oh | 2 | 23.304 | 23.203 | 15.4678 | 15.5687 | 18.9286 | 80716.68 | 5184.5318 | 154638 | 9932.5893 | 136510 | 8768.2055 | 387372.8571 | 24881.436 | 759237.5371 | 48766.7627 | 6098400 | 391707.7479 | 11151387.225 | 716267.3448 | 3814822.176 | 245030.7299 | 14966209.401 | 961298.0747 | 21064609.401 | 1353005.8226 | 6525000 | 419108.7916 | 28348846.9381 | 1820881.377 | 272206.44 | 17484.1551 | 147851.55 | 9496.6873 | 420057.99 | 26980.8424 | 3781338 | 242880 | 68502.5 | 4400 | 3849840.5 | 247280 | 4269898.49 | 274260.8424 | 1634490 | 104985.3071 | 9843262 | 632244.8495 | 499427.5 | 32078.8438 | 70290 | 4514.8133 | 786206.6667 | 50499.0232 | 62480 | 4013.1674 | 1547800 | 99417.1016 | 14443956.1667 | 927753.1058 | 4222509.1458 | 271216.9664 | 2111509.7917 | 135624.8762 | 217132.6261 | 13946.6962 | 107673.2176 | 6915.9835 | 4439641.7719 | 285163.6626 | 2219183.0092 | 142540.8597 | 7066.4999 | 453.89 | 9900 | 635.8892 | 16966.4999 | 1089.7792 | 0 | 0 | 47249411.3767 | 3034887.9246 | 6489081.4992 | 416801.7021 | 15568750 | 37857161.5155 | 62818161.3767 | 44346243.0147
CB 234 | oh | 2 | 16.133 | 16.133 | 7.9689 | 7.9689 | 9.2192 | 42192.81 | 5294.6582 | 80833.5 | 10143.5707 | 64515 | 8095.8076 | 202490.3571 | 25409.9507 | 390031.6671 | 48943.9871 | 3187800 | 400028.1396 | 5829134.2313 | 731481.8125 | 1994111.592 | 250235.5073 | 7823245.8233 | 981717.3198 | 11011045.8232 | 1381745.4593 | 2825000 | 354501.3785 | 14226077.4904 | 1785190.8249 | 142289.73 | 17855.5417 | 109563.3 | 13748.7932 | 251853.03 | 31604.335 | 1935496 | 242880 | 35063.3333 | 4400 | 1970559.3333 | 247280 | 2222412.3633 | 278884.335 | 822690 | 103237.0758 | 4954422 | 621716.6118 | 251377.5 | 31544.662 | 14850 | 1863.4851 | 166100 | 20843.4262 | 13200 | 1656.4312 | 327000 | 41034.3189 | 6549639.5 | 821896.011 | 2175416.8583 | 272987 | 1087839.9167 | 136510 | 111867.5489 | 14037.947 | 55472.9107 | 6961.141 | 2287284.4072 | 287024.947 | 1143312.8274 | 143471.141 | 3617.0219 | 453.89 | 9900 | 1242.3234 | 13517.0219 | 1696.2134 | 0 | 0 | 23076518.4195 | 2895807.9964 | 3365725.1907 | 422355.476 | 7968939.3939 | 18438486.8696 | 31045457.8134 | 21804212.0603
CB 236 | oh | 2 | 9.5161 | 9.5161 | 6.3229 | 6.3229 | 0.098109 | 35262.59 | 5576.95 | 67556.5 | 10684.3888 | 57035 | 9020.3624 | 169231.0714 | 26764.7164 | 329085.1614 | 52046.4176 | 2664200 | 421356.1779 | 4871691.8937 | 770481.7493 | 1666576.3547 | 263577.15 | 6538268.2484 | 1034058.8993 | 9202468.2484 | 1455415.0772 | 2725000 | 430971.9934 | 12256553.4098 | 1938433.4882 | 118918.47 | 18807.534 | 61261.2 | 9688.7565 | 180179.67 | 28496.2905 | 1535710 | 242880 | 27820.8333 | 4400 | 1563530.8333 | 247280 | 1743710.5033 | 275776.2905 | 361350 | 57149.2586 | 2176130 | 344165.5354 | 110412.5 | 17462.2735 | 18810 | 2974.8929 | 210393.3333 | 33274.7282 | 16720 | 2644.3493 | 414200 | 65507.743 | 3308015.8333 | 523178.7809 | 1726074.0521 | 272987 | 863141.3542 | 136510 | 109681.3402 | 17346.637 | 47705.2871 | 7544.823 | 1835755.3923 | 290333.637 | 910846.6413 | 144054.823 | 2869.9086 | 453.89 | 9900 | 1565.7331 | 12769.9086 | 2019.6231 | 0 | 0 | 17413094.5441 | 2753965.5292 | 2654557.1446 | 419831.1135 | 6322916.6667 | 196218.2192 | 23736011.2108 | 2850775.3638
CB 240 | oh | 2 | 5.8034 | 5.6606 | 5.2343 | 5.2343 | 6.4158 | 27720.88 | 5296.0251 | 53108 | 10146.1895 | 51892.5 | 9913.9704 | 133037.1429 | 25416.511 | 265758.5229 | 50772.696 | 2094400 | 400131.418 | 3829769.35 | 731670.665 | 1310140.9493 | 250300.1126 | 5139910.2993 | 981970.7776 | 7234310.2993 | 1382102.1956 | 1450000 | 277019.937 | 8950068.8222 | 1709894.8287 | 93485.04 | 17860.1517 | 32397.75 | 6189.5329 | 125882.79 | 24049.6845 | 1271302 | 242880 | 23030.8333 | 4400 | 1294332.8333 | 247280 | 1420215.6233 | 271329.6845 | 196020 | 37449.2745 | 1180476 | 225527.8532 | 59895 | 11442.8339 | 15840 | 3026.204 | 177173.3333 | 33848.6522 | 14080 | 2689.9591 | 348800 | 66637.6235 | 1992284.3333 | 380622.4004 | 1428890.4771 | 272987 | 714531.6042 | 136510 | 76547.7535 | 14624.313 | 36977.6727 | 7064.519 | 1505438.2306 | 287611.313 | 751509.2768 | 143574.519 | 2375.7875 | 453.89 | 9900 | 1891.3775 | 12275.7875 | 2345.2675 | 0 | 0 | 12460067.1736 | 2380473.8096 | 2171724.9002 | 414904.2035 | 5234280.303 | 12831654.0732 | 17694347.4766 | 15003378.9734
CB 242 | oh | 2 | 6.0316 | 3.658 | 2.3436 | 2.8947 | 3.4215 | 11822.14 | 4084.0683 | 22649 | 7824.3078 | 22440 | 7752.1068 | 38150.3571 | 13179.3958 | 95061.4971 | 32839.8786 | 893200 | 308564.2502 | 1633283.9875 | 564233.1493 | 558736.5813 | 193020.7504 | 2192020.5688 | 757253.8997 | 3085220.5688 | 1065818.1499 | 1100000 | 380005.2342 | 4280282.066 | 1478663.2628 | 39868.62 | 13772.9857 | 25918.2 | 8953.6833 | 65786.82 | 22726.669 | 703064 | 242880 | 12736.6667 | 4400 | 715800.6667 | 247280 | 781587.4867 | 270006.669 | 38610 | 13338.1837 | 232518 | 80325.5064 | 11797.5 | 4075.5561 | 8910 | 3078.0424 | 99660 | 34428.4742 | 7920 | 2736.0377 | 196200 | 67779.1154 | 595615.5 | 205760.916 | 639761.5792 | 221011.5898 | 319919.4583 | 110519.1534 | 39002.0488 | 13473.6206 | 17390.2907 | 6007.6377 | 678763.628 | 234485.2104 | 337309.749 | 116526.7911 | 1313.874 | 453.89 | 9900 | 3420.0471 | 11213.874 | 3873.9371 | 0 | 0 | 5565875.068 | 1922783.3263 | 1118897.2357 | 386533.4601 | 2894696.9697 | 6843026.8095 | 8460572.0377 | 7961924.0452
CB 246 | oh | 2 | 16.883 | 11.5013 | 8.5994 | 11.0661 | 14.7379 | 49938.35 | 4512.7332 | 95672.5 | 8645.5493 | 68722.5 | 6210.1833 | 181947.8571 | 16441.9156 | 396281.2071 | 35810.3814 | 3773000 | 340951.24 | 6899216.8438 | 623455.218 | 2360180.3867 | 213280.2622 | 9259397.2304 | 836735.4803 | 13032397.2304 | 1177686.7202 | 3050000 | 275616.5603 | 16478678.4376 | 1489113.6619 | 168410.55 | 15218.6021 | 73631.25 | 6653.7678 | 242041.8 | 21872.37 | 2687734 | 242880 | 48690.8333 | 4400 | 2736424.8333 | 247280 | 2978466.6333 | 269152.37 | 631620 | 57077.0268 | 3803756 | 343730.5393 | 192995 | 17440.2026 | 25245 | 2281.2918 | 282370 | 25516.6715 | 22440 | 2027.815 | 555900 | 50234.5068 | 5514326 | 498308.0539 | 2347533.0937 | 212137.3759 | 1173908.4375 | 106081.51 | 125754.6339 | 11363.954 | 60750.1873 | 5489.7566 | 2473287.7277 | 223501.3299 | 1234658.6248 | 111571.2666 | 5022.7914 | 453.89 | 9900 | 894.6242 | 14922.7914 | 1348.5142 | 0 | 0 | 24481214.9567 | 2212271.5599 | 4213125.2581 | 380723.6366 | 11066098.4848 | 29475844.9075 | 35547313.4415 | 33688970.1656
CB 247 | oh | 2 | 20.7059 | 16.639 | 1.368 | 3.6366 | 4.9447 | 17529.38 | 4820.3284 | 33583 | 9234.844 | 22907.5 | 6299.2344 | 29346.4286 | 8069.8476 | 103366.3086 | 28424.2544 | 1324400 | 364191.0317 | 2421765.9125 | 665950.941 | 828471.4827 | 227817.7922 | 3250237.3952 | 893768.7332 | 4574637.3952 | 1257959.7649 | 350000 | 96244.9872 | 5028003.7037 | 1382629.0066 | 59115.54 | 16255.9268 | 86001.3 | 23649.1258 | 145116.84 | 39905.0526 | 883246 | 242880 | 16000.8333 | 4400 | 899246.8333 | 247280 | 1044363.6733 | 287185.0526 | 161370 | 44374.4388 | 971806 | 267232.7316 | 49307.5 | 13558.8563 | 7920 | 2177.8866 | 88586.6667 | 24360.0646 | 7040 | 1935.8992 | 174400 | 47957.5022 | 1460430.1667 | 401597.3793 | 373444.1479 | 102691.7921 | 186744.6458 | 51352.103 | 20006.13 | 5501.3992 | 9664.4793 | 2657.5934 | 393450.2779 | 108193.1914 | 196409.1252 | 54009.6964 | 1650.5951 | 453.89 | 9900 | 2722.3582 | 11550.5951 | 3176.2482 | 0 | 0 | 6893434.7433 | 1895595.8255 | 1240772.7985 | 341194.749 | 3636553.0303 | 9889348.9768 | 10529987.7736 | 11130121.7753
CB 248 | oh | 2 | 5.3392 | 5.1261 | 4.4809 | 4.4809 | 4.8125 | 27720.88 | 6186.4934 | 53108 | 11852.1594 | 21972.5 | 4903.6223 | 133037.1429 | 29690.0171 | 235838.5229 | 52632.2922 | 2094400 | 467409.1044 | 3829769.35 | 854693.0203 | 1310140.9493 | 292385.3169 | 5139910.2993 | 1147078.3372 | 7234310.2993 | 1614487.4416 | 25000 | 5579.2722 | 7495148.8222 | 1672699.0059 | 93485.04 | 20863.1392 | 0 | 0 | 93485.04 | 20863.1392 | 1088314 | 242880 | 19715.8333 | 4400 | 1108029.8333 | 247280 | 1201514.8733 | 268143.1392 | 179190 | 39989.9911 | 1079122 | 240828.6132 | 54752.5 | 12219.164 | 21285 | 4750.1923 | 238076.6667 | 53131.7807 | 18920 | 4222.3932 | 468700 | 104600.1944 | 2060046.1667 | 459742.3289 | 1223219.5896 | 272987 | 611683.7292 | 136510 |  |  |  |  | 1223219.5896 | 272987 | 611683.7292 | 136510 | 2033.8226 | 453.89 | 9900 | 2209.3918 | 11933.8226 | 2663.2818 | 0 | 0 | 10790348.4011 | 2408091.6166 | 1813198.6025 | 404653.1392 | 4480871.2121 | 9624905.6167 | 15271219.6132 | 11438104.2192
CB 249 | oh | 3 | 4.1148 | 4.1148 | 3.2322 | 3.2322 | 4.312 | 14064.27 | 4351.3035 | 26944.5 | 8336.2803 | 17765 | 5496.2616 | 67496.7857 | 20882.6338 | 126270.5557 | 39066.4792 | 1062600 | 328754.717 | 1943044.7437 | 601152.9501 | 664703.864 | 205650.7912 | 2607748.6077 | 806803.7413 | 3670348.6077 | 1135558.4583 | 650000 | 201101.6055 | 4446619.1635 | 1375726.543 | 47429.91 | 14674.2016 | 17671.5 | 5467.3339 | 65101.41 | 20141.5355 | 785036 | 242880 | 14221.6667 | 4400 | 799257.6667 | 247280 | 864359.0767 | 267421.5355 | 175230 | 54213.899 | 1055274 | 326488.1472 | 53542.5 | 16565.358 | 17325 | 5360.1313 | 193783.3333 | 59954.0607 | 15400 | 4764.5611 | 381500 | 118031.1731 | 1892054.8333 | 585377.3304 | 882347.7542 | 272987 | 441227.2083 | 136510 | 49272.813 | 15244.372 | 23187.9653 | 7174.057 | 931620.5671 | 288231.372 | 464415.1736 | 143684.057 | 1467.0619 | 453.89 | 9900 | 3062.9321 | 11367.0619 | 3516.8221 | 0 | 0 | 7281661.6258 | 2252852.0675 | 1328774.2503 | 411105.5925 | 3232196.9697 | 8623929.1295 | 10513858.5955 | 9952703.3798
CB 280 | oh | 2 | 12.0062 | 2.2157 | 1.4112 | 2.8042 | 3.2332 | 15083.42 | 5378.9314 | 28897 | 10305.0223 | 31790 | 11336.7013 | 31302.8571 | 11162.9803 | 107073.2771 | 38183.6352 | 1139600 | 406395.2452 | 2083845.0875 | 743124.5483 | 712870.8107 | 254218.4169 | 2796715.8982 | 997342.9652 | 3936315.8982 | 1403738.2103 | 600000 | 213967.3105 | 4643389.1753 | 1655889.1561 | 50866.86 | 18139.7421 | 60083.1 | 21426.3655 | 110949.96 | 39566.1076 | 681076 | 242880 | 12338.3333 | 4400 | 693414.3333 | 247280 | 804364.2933 | 286846.1076 | 174240 | 62136.107 | 1049312 | 374197.4443 | 53240 | 18986.0327 | 1980 | 706.0921 | 22146.6667 | 7897.7712 | 1760 | 627.6374 | 43600 | 15548.2912 | 1346278.6667 | 480099.3759 | 385232.2229 | 137378.5045 | 192639.3958 | 68697.5557 | 20861.0459 | 7439.3031 | 10009.6579 | 3569.566 | 406093.2688 | 144817.8076 | 202649.0537 | 72267.1217 | 1272.7832 | 453.89 | 9900 | 3530.4606 | 11172.7832 | 3984.3506 | 0 | 0 | 6406933.894 | 2284790.6903 | 1007013.347 | 359113.2293 | 2804166.6667 | 6466438.6887 | 9211100.5607 | 7473452.0357
CB 329 | oh | 2 | 5.3189 | 2.782 | 2.4417 | 2.4417 | 3.7285 | 6930.22 | 2838.3154 | 13277 | 5437.6792 | 13090 | 5361.0922 | 33259.2857 | 13621.5505 | 66556.5057 | 27258.6372 | 523600 | 214443.686 | 957442.3375 | 392126.5546 | 327535.2373 | 134144.1245 | 1284977.5748 | 526270.6791 | 1808577.5748 | 740714.3651 | 650000 | 266211.6041 | 2525134.0805 | 1034184.6064 | 23371.26 | 9571.8471 | 4712.4 | 1929.9932 | 28083.66 | 11501.8403 | 593032 | 242880 | 10743.3333 | 4400 | 603775.3333 | 247280 | 631858.9933 | 258781.8403 | 25740 | 10541.9795 | 155012 | 63486.1433 | 7865 | 3221.1604 | 3465 | 1419.1126 | 38756.6667 | 15873.0375 | 3080 | 1261.4334 | 76300 | 31249.1468 | 310218.6667 | 127052.0137 | 666543.2583 | 272987 | 333311.9167 | 136510 | 35206.4405 | 14419.02 | 17160.38 | 7028.142 | 701749.6988 | 287406.02 | 350472.2967 | 143538.142 | 1108.2481 | 453.89 | 9900 | 4054.6075 | 11008.2481 | 4508.4975 | 0 | 0 | 3548110.6941 | 1453151.1375 | 982331.29 | 402319.9823 | 2441666.6667 | 7456997.3316 | 5989777.3608 | 8439328.6217
CB 330 | oh | 2 | 5.636 | 5.3191 | 1.9597 | 2.2765 | 2.7373 | 18956.19 | 8326.8455 | 36316.5 | 15952.6722 | 38335 | 16839.3344 | 79235.3571 | 34805.5479 | 172843.0471 | 75924.4001 | 1432200 | 629119.4676 | 2618886.3937 | 1150392.6921 | 895905.208 | 393542.3875 | 3514791.6017 | 1543935.0796 | 4946991.6017 | 2173054.5472 | 1475000 | 647920.1331 | 6594834.6489 | 2896899.0804 | 63927.27 | 28081.1968 | 38877.3 | 17077.5494 | 102804.57 | 45158.7462 | 552920 | 242880 | 10016.6667 | 4400 | 562936.6667 | 247280 | 665741.2367 | 292438.7462 | 123750 | 54359.401 | 745250 | 327364.3927 | 37812.5 | 16609.817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 906812.5 | 398333.6106 | 534961.4562 | 234991.3884 | 267513.0625 | 117509.8977 | 28254.8547 | 12411.4503 | 13772.4606 | 6049.7997 | 563216.3109 | 247402.8387 | 281285.5231 | 123559.6973 | 1033.2875 | 453.89 | 9900 | 4348.7521 | 10933.2875 | 4802.6421 | 0 | 0 | 8075796.7473 | 3547438.1719 | 947026.7597 | 415998.4435 | 2276515.1515 | 5474695.1584 | 10352311.8988 | 6421721.9181
CB 331 | oh | 2 | 3.6384 | 3.6384 | 2.8949 | 2.8949 | 4.338 | 9783.84 | 3379.6974 | 18744 | 6474.8656 | 19635 | 6782.6497 | 46954.2857 | 16219.7336 | 95117.1257 | 32856.9463 | 739200 | 255346.8106 | 1351683.3 | 466921.0222 | 462402.688 | 159730.8598 | 1814085.988 | 626651.882 | 2553285.988 | 881998.6926 | 1000000 | 345436.7026 | 3648403.1137 | 1260292.3415 | 32994.72 | 11397.5873 | 0 | 0 | 32994.72 | 11397.5873 | 703110 | 242880 | 12737.5 | 4400 | 715847.5 | 247280 | 748842.22 | 258677.5873 | 18810 | 6497.6644 | 113278 | 39130.3788 | 5747.5 | 1985.3974 | 4455 | 1538.9205 | 49830 | 17213.1109 | 3960 | 1367.9293 | 98100 | 33887.3405 | 294180.5 | 101620.7419 | 790266.3437 | 272987 | 395180.9375 | 136510 |  |  |  |  | 790266.3437 | 272987 | 395180.9375 | 136510 | 1313.96 | 453.89 | 9900 | 3419.8234 | 11213.96 | 3873.7134 | 0 | 0 | 4744063.9174 | 1638773.7968 | 1144023.1575 | 395187.5873 | 2894886.3636 | 8675923.0898 | 7638950.2811 | 9819946.2473
CB 351 | oh | 2 | 7.646 | 7.646 | 6.4841 | 6.4841 | 8.4476 | 27313.22 | 4212.3438 | 52327 | 8070.0596 | 44412.5 | 6849.4567 | 131080.7143 | 20215.7428 | 255133.4343 | 39347.6029 | 2063600 | 318255.871 | 3773449.2125 | 581955.0135 | 1290874.1707 | 199083.2931 | 5064323.3832 | 781038.3066 | 7127923.3832 | 1099294.1776 | 2125000 | 327725.2015 | 9508056.8175 | 1466366.982 | 92110.26 | 14205.5781 | 31219.65 | 4814.8076 | 123329.91 | 19020.3857 | 1574856 | 242880 | 28530 | 4400 | 1603386 | 247280 | 1726715.91 | 266300.3857 | 602910 | 92982.9653 | 3630858 | 559964.0799 | 184222.5 | 28411.4616 | 22770 | 3511.6719 | 254686.6667 | 39278.7008 | 20240 | 3121.4862 | 501400 | 77327.7252 | 5217087.1667 | 804598.0909 | 1770072.525 | 272987 | 885143.25 | 136510 | 109581.8042 | 16900.103 | 48404.7112 | 7465.15 | 1879654.3292 | 289887.103 | 933547.9612 | 143975.15 | 2943.064 | 453.89 | 9900 | 1526.8139 | 12843.064 | 1980.7039 | 0 | 0 | 16617641.3774 | 2562832.8798 | 2660263.8712 | 410275.5357 | 6484090.9091 | 16895119.5564 | 23101732.2865 | 19555383.4277
CB 355 | oh | 2 | 8.9379 | 8.9379 | 6.6542 | 6.6542 | 8.3776 | 34651.1 | 5207.4289 | 66385 | 9976.4559 | 61710 | 9273.8885 | 166296.4286 | 24991.323 | 329042.5286 | 49449.0963 | 2618000 | 393437.6957 | 4787211.6875 | 719430.6857 | 1637676.1867 | 246112.8897 | 6424887.8742 | 965543.5753 | 9042887.8742 | 1358981.271 | 3025000 | 454602.3795 | 12396930.4027 | 1863032.7468 | 116856.3 | 17561.3726 | 65973.6 | 9914.6299 | 182829.9 | 27476.0025 | 1616164 | 242880 | 29278.3333 | 4400 | 1645442.3333 | 247280 | 1828272.2333 | 274756.0025 | 667260 | 100277.0194 | 4018388 | 603890.4947 | 203885 | 30640.2004 | 52965 | 7959.6744 | 592423.3333 | 89030.4321 | 47080 | 7075.2661 | 1166300 | 175273.6381 | 6748301.3333 | 1014146.7251 | 1816500.9958 | 272987 | 908360.2917 | 136510 | 106329.8304 | 15979.436 | 48602.4725 | 7304.066 | 1922830.8262 | 288966.436 | 956962.7642 | 143814.066 | 3020.2597 | 453.89 | 9900 | 1487.7896 | 12920.2597 | 1941.6796 | 0 | 0 | 21080982.822 | 3168087.5875 | 2785234.9975 | 418570.0685 | 6654166.6667 | 16755220.6382 | 27735149.4887 | 19540455.6357
CB 357 | oh | 3 | 11.7229 | 11.7229 | 3.9343 | 3.9343 | 4.4041 | 21605.98 | 5491.7236 | 41393 | 10521.1111 | 30387.5 | 7723.7761 | 103690.7143 | 26355.7007 | 197077.1943 | 50092.3115 | 1632400 | 414917.0558 | 2984967.2875 | 758707.3258 | 1021139.2693 | 259549.1909 | 4006106.5568 | 1018256.5166 | 5638506.5568 | 1433173.5724 | 1425000 | 362200.9339 | 7260583.7511 | 1845466.8178 | 72863.34 | 18520.1192 | 87768.45 | 22308.6418 | 160631.79 | 40828.7609 | 955558 | 242880 | 17310.8333 | 4400 | 972868.8333 | 247280 | 1133500.6233 | 288108.7609 | 372240 | 94614.5092 | 2241712 | 569789.6 | 113740 | 28909.9889 | 35640 | 9058.836 | 398640 | 101324.7581 | 31680 | 8052.2987 | 784800 | 199477.3985 | 3978452 | 1011227.3894 | 1074007.3771 | 272987 | 537068.6042 | 136510 | 67378.8268 | 17126.087 | 29527.3914 | 7505.157 | 1141386.2038 | 290113.087 | 566595.9955 | 144015.157 | 1785.7305 | 453.89 | 9900 | 2516.3433 | 11685.7305 | 2970.2333 | 0 | 0 | 12392107.6854 | 3149777.5275 | 1700096.6189 | 432123.9179 | 3934280.303 | 8808118.0472 | 16326387.9885 | 10508214.666
CB 441 | oh | 3 | 6.4297 | 6.4297 | 6.0636 | 6.0636 | 1.6796 | 17733.21 | 2924.5174 | 33973.5 | 5602.8261 | 1402.5 | 231.2969 | 85104.6429 | 14035.2484 | 138213.8529 | 22793.8888 | 1339800 | 220956.5217 | 2449925.9813 | 404035.769 | 838104.872 | 138218.1948 | 3288030.8533 | 542253.9638 | 4627830.8532 | 763210.4855 | 50000 | 8245.8771 | 4816044.7061 | 794250.2514 | 59802.93 | 9862.5522 | 7068.6 | 1165.7361 | 66871.53 | 11028.2883 | 1472736 | 242880 | 26680 | 4400 | 1499416 | 247280 | 1566287.53 | 258308.2883 | 143550 | 23673.913 | 864490 | 142569.5652 | 43862.5 | 7233.6957 | 7425 | 1224.5127 | 83050 | 13696.4018 | 6600 | 1088.4558 | 163500 | 26964.018 | 1312477.5 | 216450.5622 | 1655293.9 | 272987 | 827747 | 136510 | 181350.7634 | 29907.922 | 59156.23 | 9755.9 | 1836644.6634 | 302894.922 | 886903.23 | 146265.9 | 2752.2239 | 453.89 | 9900 | 1632.6837 | 12652.2239 | 2086.5737 | 0 | 0 | 7977819.0934 | 1315682.3093 | 2453190.76 | 404574.1883 | 6063636.3636 | 3359250.2377 | 14041455.4571 | 5812440.9977
CB 443 | oh | 2 | 3.6187 | 1.557 | 1.4752 | 1.7657 | 2.6203 | 7337.88 | 4155.7445 | 14058 | 7961.6261 | 12622.5 | 7148.6431 | 24455.3571 | 13850.0789 | 58473.7371 | 33116.0927 | 554400 | 313979.6203 | 1013762.475 | 574135.5645 | 346802.016 | 196408.3068 | 1360564.491 | 770543.8713 | 1914964.491 | 1084523.4916 | 375000 | 212377.9899 | 2348438.2281 | 1330017.5742 | 24746.04 | 14014.7046 | 0 | 0 | 24746.04 | 14014.7046 | 428858 | 242880 | 7769.1667 | 4400 | 436627.1667 | 247280 | 461373.2067 | 261294.7046 | 7920 | 4485.4231 | 47696 | 27012.215 | 2420 | 1370.546 | 495 | 280.3389 | 5536.6667 | 3135.643 | 440 | 249.1902 | 10900 | 6173.1202 | 75407.6667 | 42706.4765 | 402707.5271 | 228069.907 | 201378.1042 | 114048.7386 |  |  |  |  | 402707.5271 | 228069.907 | 201378.1042 | 114048.7386 | 801.4425 | 453.89 | 9900 | 5606.7789 | 10701.4425 | 6060.6689 | 0 | 0 | 2837254.8644 | 1606854.6266 | 662751.3108 | 375343.4432 | 1765719.697 | 5240673.4848 | 4602974.5614 | 5903424.7957
CB 461 | oh | 2 | 3.036 | 2.7937 | 2.2848 | 2.3676 | 3.6284 | 7337.88 | 3099.2726 | 14058 | 5937.6242 | 14025 | 5923.6861 | 29346.4286 | 12394.9398 | 64767.3086 | 27355.5227 | 554400 | 234159.8272 | 1013762.475 | 428179.0151 | 346802.016 | 146477.4534 | 1360564.491 | 574656.4685 | 1914964.491 | 808816.2957 | 625000 | 263978.8817 | 2604731.7996 | 1100150.7001 | 24746.04 | 10451.8911 | 2945.25 | 1243.9741 | 27691.29 | 11695.8652 | 575046 | 242880 | 10417.5 | 4400 | 585463.5 | 247280 | 613154.79 | 258975.8652 | 0 | 0 | 0 | 0 | 0 | 0 | 1980 | 836.2851 | 22146.6667 | 9354.0037 | 1760 | 743.3645 | 43600 | 18415.1668 | 69486.6667 | 29348.8201 | 623733.9333 | 263444.1379 | 311904.6667 | 131737.9922 |  |  |  |  | 623733.9333 | 263444.1379 | 311904.6667 | 131737.9922 | 1074.6362 | 453.89 | 9900 | 4181.4255 | 10974.6362 | 4635.3155 | 0 | 0 | 3308927.0357 | 1397578.9736 | 925059.4567 | 390713.8574 | 2367613.6364 | 7256895.9638 | 5676540.6721 | 8181955.4205
CB 470 | oh | 2 | 24.3706 | 5.0987 | 2.1447 | 12.4714 | 16.2705 | 60945.17 | 4886.794 | 116759.5 | 9362.1795 | 113602.5 | 9109.0404 | 47932.5 | 3843.3932 | 339239.67 | 27201.4071 | 4604600 | 369212.7139 | 8419860.5563 | 675133.468 | 2880383.4107 | 230959.0792 | 11300243.9669 | 906092.5473 | 15904843.9669 | 1275305.2612 | 1150000 | 92210.9675 | 17394083.6369 | 1394717.6358 | 205529.61 | 16480.0732 | 126056.7 | 10107.6611 | 331586.31 | 26587.7343 | 3029054 | 242880 | 54874.1667 | 4400 | 3083928.1667 | 247280 | 3415514.4767 | 273867.7343 | 1303830 | 104545.5876 | 7851954 | 629596.7611 | 398392.5 | 31944.4851 | 12375 | 992.2702 | 138416.6667 | 11098.7259 | 11000 | 882.018 | 272500 | 21849.9901 | 9988468.1667 | 800909.838 | 585474.3917 | 46945.3566 | 292772.5833 | 23475.5158 | 34091.02 | 2733.5356 | 15632.9943 | 1253.5074 | 619565.4116 | 49678.8922 | 308405.5777 | 24729.0232 | 5660.6444 | 453.89 | 9900 | 793.8162 | 15560.6444 | 1247.7062 | 0 | 0 | 28017677.8596 | 2246554.0722 | 3723920.0543 | 298596.7575 | 12471401.5152 | 32541088.773 | 40489079.3748 | 36265008.8273
CB 522 | oh | 2 | 7.7714 | 7.7714 | 4.4515 | 4.4515 | 5.1428 | 26701.73 | 5998.3464 | 51155.5 | 11491.7052 | 45347.5 | 10186.9809 | 128146.0714 | 28787.0685 | 251350.8014 | 56464.1011 | 2017400 | 453194.0095 | 3688969.0063 | 828699.6406 | 1261974.0027 | 283493.1388 | 4950943.0089 | 1112192.7794 | 6968343.0089 | 1565386.7889 | 2275000 | 511061.9469 | 9494693.8103 | 2132912.8369 | 90048.09 | 20228.6383 | 58905 | 13232.5732 | 148953.09 | 33461.2115 | 1081184 | 242880 | 19586.6667 | 4400 | 1100770.6667 | 247280 | 1249723.7567 | 280741.2115 | 414810 | 93184.0027 | 2498078 | 561174.772 | 126747.5 | 28472.8897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3039635.5 | 682831.6644 | 1215205.7667 | 272987 | 607676.3333 | 136510 | 65113.5719 | 14627.283 | 31449.6741 | 7064.937 | 1280319.3386 | 287614.283 | 639126.0074 | 143574.937 | 2020.4982 | 453.89 | 9900 | 2223.9619 | 11920.4982 | 2677.8519 | 0 | 0 | 13826569.1471 | 3106036.6362 | 1888849.7641 | 424316.1485 | 4451515.1515 | 10285540.9463 | 18278084.2986 | 12174390.7104
CB 523 | oh | 2 | 6.8523 | 6.8523 | 3.7699 | 3.7699 | 4.1754 | 27313.22 | 7245.1043 | 52327 | 13880.2592 | 54697.5 | 14509.058 | 131080.7143 | 34770.4683 | 265418.4343 | 70404.8899 | 2063600 | 547390.5049 | 3773449.2125 | 1000945.0812 | 1290874.1707 | 342417.2631 | 5064323.3832 | 1343362.3443 | 7127923.3832 | 1890752.8492 | 2550000 | 676412.9616 | 9943341.8175 | 2637570.7006 | 92110.26 | 24433.1662 | 55959.75 | 14843.8824 | 148070.01 | 39277.0486 | 915630 | 242880 | 16587.5 | 4400 | 932217.5 | 247280 | 1080287.51 | 286557.0486 | 220770 | 58561.4469 | 1329526 | 352670.0467 | 67457.5 | 17893.7754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1617753.5 | 429125.269 | 1029129.9687 | 272987 | 514627.1875 | 136510 | 55123.9947 | 14622.19 | 26630.4848 | 7064.002 | 1084253.9634 | 287609.19 | 541257.6723 | 143574.002 | 1711.1137 | 453.89 | 9900 | 2626.0739 | 11611.1137 | 3079.9639 | 0 | 0 | 12656960.3946 | 3357385.1235 | 1621545.1823 | 430131.0506 | 3769886.3636 | 8350768.1463 | 16426846.7582 | 9972313.3286
CB 524 | oh | 3 | 15.26 | 7.5614 | 1.0083 | 3.2093 | 4.2548 | 13656.61 | 4255.3497 | 26163.5 | 8152.4509 | 26180 | 8157.5922 | 17607.8571 | 5486.5439 | 83607.9671 | 26051.9366 | 1031800 | 321505.1048 | 1886724.6062 | 587896.484 | 645437.0853 | 201115.8342 | 2532161.6916 | 789012.3182 | 3563961.6916 | 1110517.4229 | 350000 | 109058.7194 | 3997569.6587 | 1245628.079 | 46055.13 | 14350.61 | 58905 | 18354.5825 | 104960.13 | 32705.1925 | 779470 | 242880 | 14120.8333 | 4400 | 793590.8333 | 247280 | 898550.9633 | 279985.1925 | 229680 | 71567.4476 | 1383184 | 430995.0735 | 70180 | 21867.8312 | 10395 | 3239.044 | 116270 | 36229.3066 | 9240 | 2879.1502 | 228900 | 71324.4025 | 2047849 | 638102.2555 | 275261.8917 | 85770.5983 | 137647.5833 | 42890.4833 | 14140.6771 | 4406.1832 | 7016.5883 | 2186.3433 | 289402.5688 | 90176.7815 | 144664.1717 | 45076.8266 | 1456.6602 | 453.89 | 9900 | 3084.8038 | 11356.6602 | 3538.6938 | 0 | 0 | 6346177.8877 | 1977445.8098 | 1043215.135 | 325062.019 | 3209280.303 | 8509507.5349 | 9555458.1908 | 9552722.6699
CB 536 | oh | 2 | 2.4767 | 2.4767 | 1.5705 | 1.5705 | 1.7654 | 7337.88 | 4672.4562 | 14058 | 8951.5485 | 6545 | 4167.5832 | 35215.7143 | 22423.8991 | 63156.5943 | 40215.487 | 554400 | 353018.8133 | 1013762.475 | 645521.6918 | 346802.016 | 220829.0695 | 1360564.491 | 866350.7613 | 1914964.491 | 1219369.5746 | 275000 | 175108.5384 | 2253121.0853 | 1434693.5999 | 24746.04 | 15757.2469 | 7068.6 | 4500.9899 | 31814.64 | 20258.2368 | 381432 | 242880 | 6910 | 4400 | 388342 | 247280 | 420156.64 | 267538.2368 | 11880 | 7564.6889 | 71544 | 45556.2373 | 3630 | 2311.4327 | 7425 | 4727.9305 | 83050 | 52882.7786 | 6600 | 4202.6049 | 163500 | 104109.9855 | 347629 | 221355.6585 | 428713.675 | 272987 | 214382.75 | 136510 | 24638.0887 | 15688.508 | 11388.9929 | 7252.036 | 453351.7637 | 288675.508 | 225771.7429 | 143762.036 | 712.8136 | 453.89 | 9900 | 6303.9074 | 10612.8136 | 6757.7974 | 0 | 0 | 3064714.6626 | 1951482.5637 | 645928.3829 | 411300.2728 | 1570454.5455 | 3530809.3472 | 4635169.2081 | 4176737.7301
CB 542 | oh | 2 | 4.9765 | 4.758 | 2.1884 | 2.1884 | 3.2935 | 7949.37 | 3632.4252 | 15229.5 | 6959.0446 | 6545 | 2990.7053 | 38150.3571 | 17432.6167 | 67874.2271 | 31014.7918 | 600600 | 274441.1943 | 1098242.6812 | 501836.5519 | 375702.184 | 171675.2515 | 1473944.8653 | 673511.8034 | 2074544.8653 | 947952.9977 | 75000 | 34270.8784 | 2217419.0924 | 1013238.6679 | 26808.21 | 12249.8787 | 10602.9 | 4844.9426 | 37411.11 | 17094.8214 | 531530 | 242880 | 9629.1667 | 4400 | 541159.1667 | 247280 | 578570.2767 | 264374.8214 | 52470 | 23975.9065 | 315986 | 144388.2371 | 16032.5 | 7325.9714 | 4950 | 2261.878 | 55366.6667 | 25299.524 | 4400 | 2010.5582 | 109000 | 49807.01 | 558205.1667 | 255069.0852 | 597417.5729 | 272987 | 298744.8958 | 136510 | 33362.7034 | 15244.922 | 15700.1155 | 7174.09 | 630780.2763 | 288231.922 | 314445.0114 | 143684.09 | 993.3142 | 453.89 | 9900 | 4523.7559 | 10893.3142 | 4977.6459 | 0 | 0 | 3417297.8495 | 1561517.3211 | 893015.288 | 408058.9114 | 2188446.9697 | 6587020.2957 | 5605744.8192 | 7480035.5837
CB 599 | oh | 2 | 35.6775 | 32.1263 | 11.3059 | 11.4604 | 14.8985 | 56257.08 | 4908.8163 | 107778 | 9404.3701 | 109862.5 | 9586.257 | 265096.0714 | 23131.4514 | 538993.6514 | 47030.8949 | 4250400 | 370876.5679 | 7772178.975 | 678175.9513 | 2658815.456 | 231999.8944 | 10430994.431 | 910175.8456 | 14681394.431 | 1281052.4135 | 4875000 | 425377.2041 | 20095388.0824 | 1753460.5126 | 189719.64 | 16554.3405 | 157865.4 | 13774.8395 | 347585.04 | 30329.18 | 2783506 | 242880 | 50425.8333 | 4400 | 2833931.8333 | 247280 | 3181516.8733 | 277609.18 | 988020 | 86211.5252 | 5950076 | 519184.9627 | 301895 | 26342.4105 | 20790 | 1814.0702 | 232540 | 20290.7108 | 18480 | 1612.5068 | 457800 | 39946.1916 | 7969601 | 695402.3777 | 3086355.8646 | 269305.729 | 1543364.4792 | 134669.142 |  |  |  |  | 3086355.8646 | 269305.729 | 1543364.4792 | 134669.142 | 5201.7685 | 453.89 | 9900 | 863.8429 | 15101.7685 | 1317.7329 | 0 | 0 | 31166446.7155 | 2719486.3522 | 4724881.3525 | 412278.322 | 11460416.6667 | 29796930.1275 | 42626863.3822 | 34521811.48
CB 776 | oh | 2 | 6.6053 | 3.4937 | 2.6153 | 2.6153 | 3.9609 | 10802.99 | 4130.624 | 20696.5 | 7913.4999 | 24777.5 | 9473.9083 | 51845.3571 | 19823.5561 | 108122.3471 | 41341.5883 | 816200 | 312081.6859 | 1492483.6438 | 570665.0474 | 510569.6347 | 195221.0639 | 2003053.2784 | 765886.1112 | 2819253.2784 | 1077967.7971 | 900000 | 344123.3978 | 3827375.6256 | 1463432.7832 | 36431.67 | 13929.989 | 13548.15 | 5180.2616 | 49979.82 | 19110.2505 | 635214 | 242880 | 11507.5 | 4400 | 646721.5 | 247280 | 696701.32 | 266390.2505 | 69300 | 26497.5016 | 417340 | 159573.8431 | 21175 | 8096.4588 | 3465 | 1324.8751 | 38756.6667 | 14818.9731 | 3080 | 1177.6667 | 76300 | 29174.0169 | 629416.6667 | 240663.3355 | 713954.0687 | 272987 | 357020.1875 | 136510 | 36653.1712 | 14014.682 | 18194.8535 | 6956.972 | 750607.2399 | 287001.682 | 375215.041 | 143466.972 | 1187.0771 | 453.89 | 9900 | 3785.3574 | 11087.0771 | 4239.2474 | 0 | 0 | 5218486.6092 | 1995337.0481 | 1071916.361 | 409857.2225 | 2615340.9091 | 7921749.2062 | 7833827.5183 | 8993665.5672
CB 907 | oh | 3 | 1.9294 | 1.9294 | 1.375 | 1.375 | 1.6857 | 7949.37 | 5781.36 | 15229.5 | 11076 | 14960 | 10880 | 38150.3571 | 27745.7143 | 76289.2271 | 55483.0743 | 600600 | 436800 | 1098242.6812 | 798721.95 | 375702.184 | 273237.952 | 1473944.8653 | 1071959.902 | 2074544.8653 | 1508759.902 | 700000 | 509090.9091 | 2850834.0924 | 2073333.8854 | 26808.21 | 19496.88 | 8835.75 | 6426 | 35643.96 | 25922.88 | 333960 | 242880 | 6050 | 4400 | 340010 | 247280 | 375653.96 | 273202.88 | 57420 | 41760 | 345796 | 251488 | 17545 | 12760 | 6930 | 5040 | 77513.3333 | 56373.3333 | 6160 | 4480 | 152600 | 110981.8182 | 663964.3333 | 482883.1515 | 375357.125 | 272987 | 187701.25 | 136510 | 19834.8796 | 14425.367 | 9665.3287 | 7029.33 | 395192.0046 | 287412.367 | 197366.5787 | 143539.33 | 624.0987 | 453.89 | 9900 | 7200 | 10524.0987 | 7653.89 | 0 | 0 | 3920514.5291 | 2851283.2939 | 573020.5387 | 416742.21 | 1375000 | 3371470.391 | 5295514.5291 | 3944490.9297
CB 91 | oh | 2 | 7.8125 | 4.35 | 2.1011 | 2.5282 | 3.559 | 10191.5 | 4031.0975 | 19525 | 7722.8257 | 13557.5 | 5362.4691 | 40106.7857 | 15863.6474 | 83380.7857 | 32980.0396 | 770000 | 304562.1395 | 1408003.4375 | 556914.9861 | 481669.4667 | 190517.251 | 1889672.9042 | 747432.2372 | 2659672.9042 | 1051994.3767 | 600000 | 237321.1477 | 3343053.6899 | 1322295.5639 | 34369.5 | 13594.3486 | 30630.6 | 12115.4819 | 65000.1 | 25709.8305 | 614054 | 242880 | 11124.1667 | 4400 | 625178.1667 | 247280 | 690178.2667 | 272989.8305 | 137610 | 54429.6052 | 828718 | 327787.1781 | 42047.5 | 16631.2683 | 7425 | 2936.8492 | 83050 | 32849.2022 | 6600 | 2610.5326 | 163500 | 64670.0127 | 1268950.5 | 501914.6483 | 573582.9125 | 226872.2584 | 286826.125 | 113449.8419 | 29445.7872 | 11646.8467 | 14617.3851 | 5781.691 | 603028.6997 | 238519.1052 | 301443.5101 | 119231.5329 | 1147.5336 | 453.89 | 9900 | 3915.7989 | 11047.5336 | 4369.6889 | 0 | 0 | 5226080.4233 | 2067099.0063 | 991621.7767 | 392221.3635 | 2528219.697 | 7118042.7874 | 7754300.1202 | 8109664.5642
CB 928 | oh | 2 | 25.2998 | 24.7487 | 3.1426 | 3.6036 | 5.1121 | 12637.46 | 3506.9001 | 24211 | 6718.562 | 16362.5 | 4540.6002 | 51845.3571 | 14387.107 | 105056.3171 | 29153.1694 | 954800 | 264957.3764 | 1745924.2625 | 484494.671 | 597270.1387 | 165742.6989 | 2343194.4012 | 650237.37 | 3297994.4012 | 915194.7463 | 475000 | 131812.6872 | 3878050.7183 | 1076160.603 | 42618.18 | 11826.5617 | 121344.3 | 33673.0911 | 163962.48 | 45499.6528 | 875242 | 242880 | 15855.8333 | 4400 | 891097.8333 | 247280 | 1055060.3133 | 292779.6528 | 65340 | 18131.8758 | 393492 | 109194.1851 | 19965 | 5540.2954 | 7425 | 2060.4404 | 83050 | 23046.4077 | 6600 | 1831.5026 | 163500 | 45371.3144 | 739372 | 205176.0214 | 857892.6687 | 238065.5537 | 428998.1875 | 119047.1661 | 47864.0295 | 13282.2871 | 22536.9929 | 6254.0244 | 905756.6983 | 251347.8408 | 451535.1804 | 125301.1905 | 1635.6373 | 453.89 | 9900 | 2747.2539 | 11535.6373 | 3201.1439 | 0 | 0 | 5534715.0539 | 1535885.6091 | 1506595.4937 | 418080.8434 | 3603598.4848 | 10224149.4642 | 9138313.5387 | 11730744.9579
CB 971 | oh | 2 | 5.3593 | 5.3593 | 5.1074 | 5.1074 | 1.3928 | 26294.07 | 5148.2438 | 50374.5 | 9863.0682 | 42075 | 8238.0688 | 126189.6429 | 24707.2835 | 244933.2129 | 47956.6642 | 1986600 | 388966.0696 | 3632648.8687 | 711253.9781 | 1242707.224 | 243315.6874 | 4875356.0927 | 954569.6655 | 6861956.0927 | 1343535.7351 | 2550000 | 499276.894 | 9656889.3056 | 1890769.2933 | 88673.31 | 17361.7784 | 19438.65 | 3805.9878 | 108111.96 | 21167.7661 | 1240482 | 242880 | 22472.5 | 4400 | 1262954.5 | 247280 | 1371066.46 | 268447.7661 | 163350 | 31983.0904 | 983730 | 192609.278 | 49912.5 | 9772.611 | 21780 | 4264.4121 | 243613.3333 | 47698.2386 | 19360 | 3790.5885 | 479600 | 93903.215 | 1961345.8333 | 384021.4336 | 1394250.0812 | 272987 | 697209.3125 | 136510 | 87623.4236 | 17156.216 | 38357.9732 | 7510.294 | 1481873.5049 | 290143.216 | 735567.2857 | 144020.294 | 2318.1916 | 453.89 | 9900 | 1938.3691 | 12218.1916 | 2392.2591 | 0 | 0 | 13112326.8354 | 2567326.2021 | 2106633.7457 | 412468.0601 | 5107386.3636 | 2785530.6818 | 18219713.1991 | 4892164.4275
CB 980 | oh | 2 | 10.8061 | 7.7888 | 1.8653 | 1.8653 | 2.7909 | 7134.05 | 3824.5288 | 13667.5 | 7327.0789 | 12155 | 6516.2352 | 34237.5 | 18354.5538 | 67194.05 | 36022.3966 | 539000 | 288955.2239 | 985602.4062 | 528376.5565 | 337168.6267 | 180754.4267 | 1322771.0329 | 709130.9832 | 1861771.0329 | 998086.2071 | 650000 | 348461.7728 | 2578965.0829 | 1382570.3765 | 24058.65 | 12897.7228 | 35932.05 | 19262.9936 | 59990.7 | 32160.7164 | 453054 | 242880 | 8207.5 | 4400 | 461261.5 | 247280 | 521252.2 | 279440.7164 | 507870 | 272266.5854 | 3058506 | 1639649.8812 | 155182.5 | 83192.5678 | 6435 | 3449.7716 | 71976.6667 | 38586.3336 | 5720 | 3066.4636 | 141700 | 75964.6665 | 3947390.1667 | 2116176.2697 | 509213.8187 | 272987 | 254637.6875 | 136510 |  |  |  |  | 509213.8187 | 272987 | 254637.6875 | 136510 | 846.6596 | 453.89 | 9900 | 5307.3408 | 10746.6596 | 5761.2308 | 0 | 0 | 7046315.7279 | 3777494.877 | 775889.8875 | 415950.7164 | 1865340.9091 | 5581715.7316 | 8911656.637 | 6357605.6191
CB FB1 | oh | 2 | 6.4737 | 6.4737 | 4.1775 | 4.1775 | 4.7175 | 33631.95 | 8050.8091 | 64432.5 | 15423.8382 | 70125 | 16786.5077 | 161405.3571 | 38637.1803 | 329594.8071 | 78898.3353 | 2541000 | 608264.0432 | 4646411.3438 | 1112256.9658 | 1589509.24 | 380496.3861 | 6235920.5838 | 1492753.3519 | 8776920.5838 | 2101017.395 | 3150000 | 754046.3345 | 12256515.3909 | 2933962.0648 | 113419.35 | 27150.3 | 62439.3 | 14946.7064 | 175858.65 | 42097.0065 | 1014622 | 242880 | 18380.8333 | 4400 | 1033002.8333 | 247280 | 1208861.4833 | 289377.0065 | 256410 | 61379.3716 | 1544158 | 369640.2158 | 78347.5 | 18754.808 | 2475 | 592.465 | 27683.3333 | 6626.8305 | 2200 | 526.6355 | 54500 | 13046.1985 | 1965773.8333 | 470566.5249 | 1140392.8521 | 272987 | 570265.3542 | 136510 | 61086.9075 | 14622.971 | 29510.4739 | 7064.211 | 1201479.7595 | 287609.971 | 599775.828 | 143574.211 | 1896.1083 | 453.89 | 9900 | 2369.8599 | 11796.1083 | 2823.7499 | 0 | 0 | 15435565.092 | 3694962.3106 | 1808637.3114 | 432951.2175 | 4177462.1212 | 9435090.7229 | 19613027.2133 | 11243728.0343
CB FB2 | oh | 2 | 6.2894 | 6.2894 | 3.8712 | 3.8712 | 4.3692 | 22421.3 | 5791.8035 | 42955 | 11096.0078 | 45815 | 11834.7945 | 107603.5714 | 27795.8345 | 218794.8714 | 56518.4404 | 1694000 | 437589.0411 | 3097607.5625 | 800164.7715 | 1059672.8267 | 273731.5325 | 4157280.3892 | 1073896.3041 | 5851280.3892 | 1511485.3451 | 2200000 | 568297.456 | 8270075.2606 | 2136301.2415 | 75612.9 | 19532.0994 | 44767.8 | 11564.2849 | 120380.7 | 31096.3843 | 940240 | 242880 | 17033.3333 | 4400 | 957273.3333 | 247280 | 1077654.0333 | 278376.3843 | 306900 | 79277.4951 | 1848220 | 477426.6928 | 93775 | 24223.6791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2248895 | 580927.8669 | 1056790.5833 | 272987 | 528459.1667 | 136510 | 56630.8937 | 14628.724 | 27351.4453 | 7065.344 | 1113421.477 | 287615.724 | 555810.612 | 143575.344 | 1757.1045 | 453.89 | 9900 | 2557.3386 | 11657.1045 | 3011.2286 | 0 | 0 | 11644048.8421 | 3007856.061 | 1633464.6453 | 421951.7283 | 3871212.1212 | 8738459.644 | 15515260.9633 | 10371924.2894
CB JU1 | oh | 3 | 3.2231 | 3.2231 | 2.6672 | 2.6672 | 3.7501 | 13656.61 | 5120.1378 | 26163.5 | 9809.2225 | 26647.5 | 9990.6838 | 65540.3571 | 24572.3983 | 132007.9671 | 49492.4424 | 1031800 | 386842.5762 | 1886724.6062 | 707371.0091 | 645437.0853 | 241987.3472 | 2532161.6916 | 949358.3563 | 3563961.6916 | 1336200.9324 | 1000000 | 374920.1165 | 4695969.6587 | 1760613.4913 | 46055.13 | 17266.9947 | 14137.2 | 5300.3207 | 60192.33 | 22567.3154 | 647818 | 242880 | 11735.8333 | 4400 | 659553.8333 | 247280 | 719746.1633 | 269847.3154 | 454410 | 170367.4501 | 2736558 | 1025990.644 | 138847.5 | 52056.7209 | 15345 | 5753.1492 | 171636.6667 | 64350.0391 | 13640 | 5113.9104 | 337900 | 126685.5073 | 3868337.1667 | 1450317.421 | 728120.4396 | 272987 | 364104.2292 | 136510 | 50983.0125 | 19114.557 | 20950.2522 | 7854.671 | 779103.4521 | 292101.557 | 385054.4814 | 144364.671 | 1210.6312 | 453.89 | 9900 | 3711.7092 | 11110.6312 | 4165.5992 | 0 | 0 | 9354520.9087 | 3507198.0685 | 1104800.6447 | 414211.9864 | 2667234.8485 | 7500271.7583 | 12021755.7572 | 8605072.403
CB MOR1 | oh | 2 | 5.2784 | 5.2784 | 3.55 | 3.55 | 4.8899 | 17733.21 | 4995.2704 | 33973.5 | 9570 | 30855 | 8691.5493 | 85104.6429 | 23973.1388 | 167666.3529 | 47229.9586 | 1339800 | 377408.4507 | 2449925.9813 | 690119.9947 | 838104.872 | 236085.8794 | 3288030.8533 | 926205.8742 | 4627830.8532 | 1303614.3249 | 1450000 | 408450.7042 | 6245497.2061 | 1759294.9876 | 59802.93 | 16845.8958 | 31219.65 | 8794.2676 | 91022.58 | 25640.1634 | 862224 | 242880 | 15620 | 4400 | 877844 | 247280 | 968866.58 | 272920.1634 | 290070 | 81709.8592 | 1746866 | 492074.9296 | 88632.5 | 24966.9014 | 28710 | 8087.3239 | 321126.6667 | 90458.216 | 25520 | 7188.7324 | 632200 | 178084.507 | 3133125.1667 | 882570.4695 | 969103.85 | 272987 | 484610.5 | 136510 | 61734.3012 | 17389.944 | 26810.5975 | 7552.281 | 1030838.1512 | 290376.944 | 511421.0975 | 144062.281 | 1611.3095 | 453.89 | 9900 | 2788.7324 | 11511.3095 | 3242.6224 | 0 | 0 | 10420971.8335 | 2935485.0235 | 1480287.6775 | 416982.4444 | 3550000 | 9779848.9167 | 13970971.8335 | 11260136.5943
CB OK1 | oh | 3 | 6.8367 | 6.8367 | 6.786 | 6.786 | 9.1292 | 31389.82 | 4625.6838 | 60137 | 8861.9414 | 62645 | 9231.5267 | 150645 | 22199.4306 | 304816.82 | 44918.5825 | 2371600 | 349485.0126 | 4336650.5875 | 639059.8689 | 1483541.9573 | 218618.519 | 5820192.5448 | 857678.3879 | 8191792.5448 | 1207163.4004 | 2325000 | 342617.9179 | 10821609.3648 | 1594699.9008 | 105858.06 | 15599.5132 | 25329.15 | 3732.568 | 131187.21 | 19332.0812 | 1648180 | 242880 | 29858.3333 | 4400 | 1678038.3333 | 247280 | 1809225.5433 | 266612.0812 | 697950 | 102851.6885 | 4203210 | 619395.7243 | 213262.5 | 31426.9048 | 29205 | 4303.7231 | 326663.3333 | 48137.9403 | 25960 | 3825.5317 | 643100 | 94768.8529 | 6139350.8333 | 904710.3656 | 1852485.6458 | 272987 | 926354.7917 | 136510 | 129638.9863 | 19103.931 | 53290.8547 | 7853.076 | 1982124.6321 | 292090.931 | 979645.6464 | 144363.076 | 3080.0907 | 453.89 | 9900 | 1458.8892 | 12980.0907 | 1912.7792 | 0 | 0 | 18956064.921 | 2793413.9766 | 2788871.1897 | 410975.1572 | 6785984.8485 | 18258394.0685 | 25742049.7695 | 21047265.2582
CB PE1 | oh | 3 | 5.3157 | 5.3157 | 5.0331 | 5.0331 | 0.24663 | 29147.69 | 5791.1497 | 55841.5 | 11094.7552 | 6077.5 | 1207.4958 | 139884.6429 | 27792.6967 | 230951.3329 | 45886.0974 | 2202200 | 437539.6425 | 4026889.8312 | 800074.4425 | 1377574.6747 | 273700.6315 | 5404464.5059 | 1073775.074 | 7606664.5059 | 1511314.7165 | 250000 | 49670.7432 | 8087615.8388 | 1606871.5571 | 98296.77 | 19529.8945 | 37110.15 | 7373.1549 | 135406.92 | 26903.0494 | 1222450 | 242880 | 22145.8333 | 4400 | 1244595.8333 | 247280 | 1380002.7533 | 274183.0494 | 1216710 | 241739.5597 | 7327298 | 1455809.3486 | 371772.5 | 73864.8655 | 40590 | 8064.5419 | 454006.6667 | 90203.3942 | 36080 | 7168.4817 | 893800 | 177582.841 | 10340257.1667 | 2054433.0325 | 1373982.8646 | 272987 | 687074.4792 | 136510 | 103469.2089 | 20557.57 | 40813.1099 | 8108.87 | 1477452.0734 | 293544.57 | 727887.5891 | 144618.87 | 2284.4937 | 453.89 | 9900 | 1966.9614 | 12184.4937 | 2420.8514 | 0 | 0 | 19917509.5726 | 3957270.011 | 2107890.3424 | 418801.9194 | 5033143.9394 | 493260.9871 | 24950653.512 | 2601151.3295
CB RA1 | oh | 2 | 9.0178 | 9.0178 | 7.7369 | 7.7369 | 0 | 45046.43 | 5822.2602 | 86300.5 | 11154.3571 | 75267.5 | 9728.3396 | 216185.3571 | 27942.0011 | 422799.7871 | 54646.9579 | 3403400 | 439890.1373 | 6223375.1937 | 804372.5006 | 2128979.0427 | 275170.9712 | 8352354.2364 | 1079543.4718 | 11755754.2364 | 1519433.6092 | 3550000 | 458838.2169 | 15728554.0236 | 2032918.784 | 151913.19 | 19634.8105 | 56548.8 | 7308.9438 | 208461.99 | 26943.7543 | 1879146 | 242880 | 34042.5 | 4400 | 1913188.5 | 247280 | 2121650.49 | 274223.7543 | 372240 | 48112.0952 | 2241712 | 289741.7287 | 113740 | 14700.918 | 40095 | 5182.2868 | 448470 | 57964.8381 | 35640 | 4606.4772 | 882900 | 114115.0033 | 4134797 | 534423.3473 | 2112081.8062 | 272987 | 1056168.5625 | 136510 | 134565.9174 | 17392.672 | 58433.3555 | 7552.523 | 2246647.7236 | 290379.672 | 1114601.918 | 144062.523 | 3511.716 | 453.89 | 9900 | 1279.577 | 13411.716 | 1733.467 | 0 | 0 | 22123410.4632 | 2859455.2703 | 3236252.408 | 418286.2773 | 7736931.8182 | 0 | 29860342.2814 | 3236252.408
CB RA2 | oh | 2 | 2.8144 | 2.8144 | 2.7417 | 2.7417 | 0 | 16306.4 | 5947.6231 | 31240 | 11394.5289 | 30387.5 | 11083.5866 | 78257.1429 | 28543.6387 | 156191.0429 | 56969.3773 | 1232000 | 449361.7021 | 2252805.5 | 821691.9757 | 770671.1467 | 281095.859 | 3023476.6467 | 1102787.8347 | 4255476.6467 | 1552149.5368 | 1450000 | 528875.3799 | 5861667.6895 | 2137994.2941 | 54991.2 | 20057.5805 | 15315.3 | 5586.1277 | 70306.5 | 25643.7082 | 665896 | 242880 | 12063.3333 | 4400 | 677959.3333 | 247280 | 748265.8333 | 272923.7082 | 219780 | 80162.9179 | 1323564 | 482758.9058 | 67155 | 24494.2249 | 12375 | 4513.6778 | 138416.6667 | 50486.3222 | 11000 | 4012.1581 | 272500 | 99392.0973 | 2044790.6667 | 745820.304 | 748439.3583 | 272987 | 374264.9167 | 136510 | 47743.9591 | 17414.21 | 20717.056 | 7556.373 | 796183.3174 | 290401.21 | 394981.9726 | 144066.373 | 1244.4151 | 453.89 | 9900 | 3610.9422 | 11144.4151 | 4064.8322 | 0 | 0 | 8713786.0887 | 3178280.6403 | 1143247.806 | 416990.0812 | 2741666.6667 | 0 | 11455452.7554 | 1143247.806
CB RA3 | oh | 2 | 3.6301 | 3.6301 | 2.986 | 2.986 | 0 | 23236.62 | 7781.8948 | 44517 | 14908.649 | 30855 | 10333.2741 | 111516.4286 | 37346.6157 | 210125.0486 | 70370.4336 | 1755600 | 587946.7208 | 3210247.8375 | 1075105.1999 | 1098206.384 | 367786.9915 | 4308454.2215 | 1442892.1914 | 6064054.2215 | 2030838.9122 | 1425000 | 477229.4812 | 7699179.2701 | 2578438.827 | 78362.46 | 26243.4218 | 35932.05 | 12033.5674 | 114294.51 | 38276.9893 | 725236 | 242880 | 13138.3333 | 4400 | 738374.3333 | 247280 | 852668.8433 | 285556.9893 | 135630 | 45422.1997 | 816794 | 273542.5802 | 41442.5 | 13879.0055 | 4455 | 1491.9701 | 49830 | 16687.9614 | 3960 | 1326.1956 | 98100 | 32853.4822 | 1150211.5 | 385203.3946 | 815135.0458 | 272987 | 407616.7917 | 136510 | 51966.3126 | 17403.408 | 22557.0074 | 7554.294 | 867101.3584 | 290390.408 | 430173.7991 | 144064.294 | 1355.3087 | 453.89 | 9900 | 3315.489 | 11255.3087 | 3769.379 | 0 | 0 | 9727747.4372 | 3257802.0086 | 1282842.6424 | 429621.2833 | 2985984.8485 | 0 | 12713732.2857 | 1282842.6424
CB RC1 | oh | 2 | 2.5881 | 2.5881 | 2.5881 | 2.5881 | 3.2776 | 12025.97 | 4646.6975 | 23039.5 | 8902.1998 | 24777.5 | 9573.7431 | 57714.6429 | 22300.2791 | 117557.6129 | 45422.9196 | 908600 | 351072.6674 | 1661444.0562 | 641963.0162 | 568369.9707 | 219611.6681 | 2229814.0269 | 861574.6844 | 3138414.0269 | 1212647.3518 | 1225000 | 473326.0154 | 4480971.6398 | 1731396.2867 | 40556.01 | 15670.3793 | 15904.35 | 6145.2593 | 56460.36 | 21815.6386 | 628590 | 242880 | 11387.5 | 4400 | 639977.5 | 247280 | 696437.86 | 269095.6386 | 287100 | 110932.1625 | 1728980 | 668058.1339 | 87725 | 33895.9385 | 15345 | 5929.1328 | 171636.6667 | 66318.4486 | 13640 | 5270.3403 | 337900 | 130560.7025 | 2642326.6667 | 1020964.8591 | 706508.9687 | 272987 | 353297.1875 | 136510 | 41686.8476 | 16107.322 | 18961.5255 | 7326.517 | 748195.8163 | 289094.322 | 372258.713 | 143836.517 | 1174.6983 | 453.89 | 9900 | 3825.247 | 11074.6983 | 4279.137 | 0 | 0 | 7882568.821 | 3045734.6048 | 1068696.573 | 412932.1556 | 2588068.1818 | 6555264.096 | 10470637.0028 | 7623960.669
CB SL1 | oh | 3 | 7.0095 | 7.0095 | 6.8343 | 6.8343 | 6.0706 | 38116.21 | 5577.2091 | 73023.5 | 10684.8851 | 67787.5 | 9918.7474 | 182926.0714 | 26765.9597 | 361853.2814 | 52946.8013 | 2879800 | 421375.7517 | 5265932.8563 | 770517.5414 | 1801443.8053 | 263589.3943 | 7067376.6616 | 1034106.9357 | 9947176.6616 | 1455482.6874 | 3550000 | 519440.2106 | 13859029.943 | 2027869.6993 | 128541.93 | 18808.4077 | 41233.5 | 6033.3346 | 169775.43 | 24841.7423 | 1659910 | 242880 | 30070.8333 | 4400 | 1689980.8333 | 247280 | 1859756.2633 | 272121.7423 | 827640 | 121101.2665 | 4984232 | 729298.738 | 252890 | 37003.1647 | 57915 | 8474.1915 | 647790 | 94785.4011 | 51480 | 7532.6147 | 1275300 | 186603.4086 | 8097247 | 1184798.7851 | 1865669.6771 | 272987 | 932947.6042 | 136510 | 130389.6894 | 19078.774 | 53635.9171 | 7848.071 | 1996059.3664 | 292065.774 | 986583.5212 | 144358.071 | 3102.0115 | 453.89 | 9900 | 1448.5797 | 13002.0115 | 1902.4697 | 0 | 0 | 23965338.3209 | 3506636.7281 | 2846339.7846 | 416479.8133 | 6834280.303 | 12141200.8812 | 30799618.624 | 14987540.6658
CTL1-3R | oh | 3 | 5.7568 | 5.7568 | 3.9705 | 3.9705 | 5.1512 | 28332.37 | 7135.8001 | 54279.5 | 13670.8529 | 37400 | 9419.5764 | 135971.7857 | 34245.8991 | 255983.6557 | 64472.1285 | 2140600 | 539132.2267 | 3914249.5562 | 985844.1928 | 1339041.1173 | 337251.3404 | 5253290.6736 | 1323095.5331 | 7393890.6736 | 1862227.7598 | 1875000 | 472238.1225 | 9524874.3293 | 2398938.0108 | 95547.21 | 24064.552 | 38288.25 | 9643.2914 | 133835.46 | 33707.8434 | 964344 | 242880 | 17470 | 4400 | 981814 | 247280 | 1115649.46 | 280987.8434 | 1066230 | 268541.0418 | 6421074 | 1617213.8294 | 325792.5 | 82054.2072 | 29205 | 7355.581 | 326663.3333 | 82273.5356 | 25960 | 6538.2942 | 643100 | 161971.3795 | 8838024.8333 | 2225947.8687 | 1083882.475 | 272987 | 542006.75 | 136510 | 104695.3515 | 26368.606 | 36255.5347 | 9131.331 | 1188577.8265 | 299355.606 | 578262.2847 | 145641.331 | 1802.1496 | 453.89 | 9900 | 2493.4173 | 11702.1496 | 2947.3073 | 0 | 0 | 19563179.1388 | 4927188.7928 | 1693911.7447 | 426629.1744 | 3970454.5455 | 10302341.025 | 23533633.6842 | 11996252.7697
DV1-3R | oh | 3 | 10.4451 | 10.4451 | 7.4436 | 7.4436 | 9.3052 | 35874.08 | 4819.4785 | 68728 | 9233.2156 | 70125 | 9420.8946 | 172165.7143 | 23129.4838 | 346892.7943 | 46603.0725 | 2710400 | 364126.8129 | 4956172.1 | 665833.512 | 1695476.5227 | 227777.6205 | 6651648.6227 | 893611.1325 | 9362048.6227 | 1257737.9453 | 3875000 | 520584.1942 | 13583941.417 | 1824925.212 | 120980.64 | 16253.0604 | 53603.55 | 7201.3318 | 174584.19 | 23454.3922 | 1807892 | 242880 | 32751.6667 | 4400 | 1840643.6667 | 247280 | 2015227.8567 | 270734.3922 | 428670 | 57589.3746 | 2581546 | 346816.0114 | 130982.5 | 17596.7533 | 64350 | 8645.0562 | 719766.6667 | 96696.5549 | 57200 | 7684.4944 | 1417000 | 190365.8847 | 5399515.1667 | 725394.1296 | 2031995.2792 | 272987 | 1016120.4583 | 136510 | 141798.4227 | 19049.811 | 58377.2257 | 7842.648 | 2173793.7019 | 292036.811 | 1074497.684 | 144352.648 | 3378.5577 | 453.89 | 9900 | 1330.0087 | 13278.5577 | 1783.8987 | 0 | 0 | 21170528.8432 | 2844140.0512 | 3089725.5407 | 415087.0402 | 7443560.6061 | 18610404.4457 | 28614089.4493 | 21700129.9864
RA1-402R | oh | 3 | 4.0562 | 4.0562 | 3.1917 | 3.1917 | 0 | 15287.25 | 4789.7389 | 29287.5 | 9176.2402 | 21505 | 6737.859 | 73366.0714 | 22986.7587 | 139445.8214 | 43690.5968 | 1155000 | 361879.8956 | 2112005.1562 | 661724.8531 | 722504.2 | 226372.0731 | 2834509.3563 | 888096.9262 | 3989509.3563 | 1249976.8218 | 1050000 | 328981.7232 | 5178955.1777 | 1622649.1418 | 51554.25 | 16152.7676 | 28863.45 | 9043.3786 | 80417.7 | 25196.1462 | 775192 | 242880 | 14043.3333 | 4400 | 789235.3333 | 247280 | 869653.0333 | 272476.1462 | 300960 | 94295.5614 | 1812448 | 567868.8251 | 91960 | 28812.5326 | 19800 | 6203.6554 | 221466.6667 | 69389.0339 | 17600 | 5514.3603 | 436000 | 136605.7441 | 2900234.6667 | 908689.7128 | 871283.5083 | 272987 | 435694.4167 | 136510 | 55679.6048 | 17445.307 | 24133.9247 | 7561.543 | 926963.1132 | 290432.307 | 459828.3414 | 144071.543 | 1448.6656 | 453.89 | 9900 | 3101.8277 | 11348.6656 | 3555.7177 | 0 | 0 | 9017501.6231 | 2825326.8793 | 1329481.3747 | 416547.6892 | 3191666.6667 | 0 | 12209168.2898 | 1329481.3747
RB1-427R | oh | 3 | 13.1669 | 13.1669 | 12.6949 | 12.6949 | 16.4338 | 62779.64 | 4945.2699 | 120274 | 9474.2085 | 93967.5 | 7401.9962 | 301290 | 23733.1782 | 578311.14 | 45554.6528 | 4743200 | 373630.7568 | 8673301.175 | 683212.1948 | 2967083.9147 | 233722.7628 | 11640385.0897 | 916934.9576 | 16383585.0897 | 1290565.7144 | 4800000 | 378104.9993 | 21761896.2297 | 1714225.3665 | 211716.12 | 16677.2757 | 70096.95 | 5521.6682 | 281813.07 | 22198.9439 | 3083334 | 242880 | 55857.5 | 4400 | 3139191.5 | 247280 | 3421004.57 | 269478.9439 | 1092960 | 86094.5083 | 6582048 | 518480.2614 | 333960 | 26306.6553 | 91575 | 7213.5344 | 1024283.3333 | 80684.7186 | 81400 | 6412.0306 | 2016500 | 158843.4857 | 11222726.3333 | 884035.1943 | 3465538.9437 | 272987 | 1732978.9375 | 136510 | 218318.7595 | 17197.378 | 95431.7009 | 7517.334 | 3683857.7032 | 290184.378 | 1828410.6384 | 144027.334 | 5762.082 | 453.89 | 9900 | 779.8416 | 15662.082 | 1233.7316 | 0 | 0 | 36684142.3482 | 2889678.6704 | 5249415.2084 | 413506.2779 | 12694886.3636 | 32867521.7129 | 49379028.7118 | 38116936.9213
RB1-433R | oh | 3 | 7.6284 | 7.6284 | 6.3644 | 6.3644 | 8.5599 | 24051.94 | 3779.1407 | 46079 | 7240.1238 | 33192.5 | 5215.3434 | 115429.2857 | 18136.7286 | 218752.7257 | 34371.3365 | 1817200 | 285526.0088 | 3322888.1125 | 522105.9765 | 1136739.9413 | 178609.2992 | 4459628.0538 | 700715.2757 | 6276828.0538 | 986241.2845 | 1700000 | 267111.0582 | 8195580.7795 | 1287723.6792 | 81112.02 | 12744.6574 | 20027.7 | 3146.8354 | 101139.72 | 15891.4927 | 1545784 | 242880 | 28003.3333 | 4400 | 1573787.3333 | 247280 | 1674927.0533 | 263171.4927 | 445500 | 69998.8097 | 2682900 | 421548.3871 | 136125 | 21388.5252 | 20790 | 3266.6111 | 232540 | 36537.6503 | 18480 | 2903.6543 | 457800 | 71931.4367 | 3994135 | 627575.0744 | 1737396.8083 | 272987 | 868803.4167 | 136510 | 113471.0468 | 17829.042 | 48557.3599 | 7629.534 | 1850867.8552 | 290816.042 | 917360.7766 | 144139.534 | 2888.7348 | 453.89 | 9900 | 1555.5291 | 12788.7348 | 2009.4191 | 0 | 0 | 14053372.3695 | 2208124.2147 | 2592287.8299 | 407311.0267 | 6364393.9394 | 17119794.117 | 20417766.3089 | 19712081.9469
TM1-10R | oh | 3 | 3.5502 | 3.5502 | 3.39 | 3.39 | 4.2225 | 16714.06 | 4930.4563 | 32021 | 9445.8283 | 27115 | 7998.6144 | 79235.3571 | 23373.5229 | 155085.4171 | 45748.4218 | 1262800 | 372511.537 | 2309125.6375 | 681165.6163 | 789937.9253 | 233022.6407 | 3099063.5628 | 914188.257 | 4361863.5628 | 1286699.7939 | 1325000 | 390859.8246 | 5841948.98 | 1723308.0404 | 56365.98 | 16627.3185 | 14726.25 | 4344.0751 | 71092.23 | 20971.3936 | 823354 | 242880 | 14915.8333 | 4400 | 838269.8333 | 247280 | 909362.0633 | 268251.3936 | 499950 | 147479.524 | 3010810 | 888154.4667 | 152762.5 | 45063.1879 | 13860 | 4088.5413 | 155026.6667 | 45731.0911 | 12320 | 3634.2589 | 305200 | 90030.5045 | 4149929.1667 | 1224181.5744 | 925415.5896 | 272987 | 462763.7292 | 136510 | 55403.1476 | 16343.294 | 24976.1154 | 7367.668 | 980818.7372 | 289330.294 | 487739.8446 | 143877.668 | 1538.6699 | 453.89 | 9900 | 2920.3866 | 11438.6699 | 3374.2766 | 0 | 0 | 10984135.5537 | 3240194.1854 | 1397101.9079 | 412129.0616 | 3389962.1212 | 8445095.6983 | 14374097.6749 | 9842197.6062

## metadata definition
Field | Description | Calculation Method
upstreamardfacilityid | feeder segment, unique identifier | feeder segment, unique identifier
total_oh_inspection_cost_per_mile | if cc mitigation is applied, total cost of conducting all overhead inspections for assets on the segment in 55 years | Cost = units * (unit cost per year) * Years (55) / miles
total_oh_repair_cost_per_mile | if cc mitigation is applied, total cost of repairing assets for assets on the segment in 55 years | Cost = units * (unit cost per year) * Years (55) / miles
pole_replacement_cost_per_mile | if cc mitigation is applied, cost of pole replacement for assets on the segment in 55 years | Cost = units * (unit cost per year) * Years (55) / miles
total_oh_asset_cost_per_mile | if cc mitigation is applied, cost of conducting overhead inspections, repair and replacement for assets on the segment in 55 years | total_oh_inspection_cost_per_mile + total_oh_repair_cost_per_mile + pole_replacement_cost_per_mile
total_ug_inspection_cost_per_mile | if ug mitigation is applied, cost of conducting all underground inspections for assets on the segment in 55 years | Cost = units * (unit cost per year) * Years (55) / miles
total_ug_repair_cost_per_mile | if ug mitigation is applied, total cost of repair and replacement assets for assets on the segment in 55 years | Cost = units * (unit cost per year) * Years (55) / miles
total_ug_asset_cost_per_mile | if ug mitigation is applied, cost of conducting underground inspections, repair and replacement for assets on the segment in 55 years | total_ug_inspection_cost_per_mile + total_ug_repair_cost_per_mile
total_oh_veg_cost_per_mile | if cc mitigation is applied, cost of conducting all vegetation management operations for the segment in 55 years | Cost = units * (unit cost per year) * Years (55) / miles
total_cc_psps_cost_per_mile | if cc mitigation is applied, cost of psps activation and community outreach for the segment in 55 years | Cost = units * (unit cost per year) * Years (55) / miles
total_ug_psps_cost_per_mile | if ug mitigation is applied, cost of psps activation and community outreach for the segment in 55 years | Cost = units * (unit cost per year) * Years (55) / miles
total_oh_peds_cost_per_mile | if cc mitigation is applied, cost of maintenance for peds (efd and fcp) for the segment in 55 years | Cost = units * (unit cost per year) * Years (55) / miles
microgrid_cost_per_mile | if cc mitigation is applied, cost of maintenance for microgrids for the segment in 55 years | Cost = units * (unit cost per year) * Years (55) / miles
total_if_cc_cost_per_mile | total cost of combined covered conductor related cost divided by the length of the circuit miles of the given segment | total_oh_asset_cost_per_mile + total_oh_veg_cost_per_mile + total_cc_psps_cost_per_mile + total_oh_peds_cost_per_mile + microgrid_cost_per_mile
total_if_ug_cost_per_mile | total cost of undergrounding related cost divided by the length of the circuit miles after the given segment is undergrounded | total_ug_asset_cost_per_mile + total_ug_psps_cost_per_mile

## Unit Cost
Activity | OH/UG | Average Annual Cost (HFTD) - Based on Model | Average Annual Cost (HFTD) - Based on Historical Data for Validation Purpose | Frequency (Actual/Estimated) | Unit Cost | Units | Data Derived From | Notes | Assumptions
Detailed Inspections | OH | 290038.972 |  | 5 years | 18.53 | Pole | From SME | From SME - contains only the inspection cost (O&M from repair removed)
Patrol Inspections | OH | 555660.2 |  | 1 year | 7.1 | Pole | From SME | From SME - contains only the inspection cost (O&M from repair removed)
WPI Inspections | OH | 409428 |  | 10 years | 85 | Pole | From SME | WPI costs around $70-100 (midpoint selected here) but additional $700 a permit when permits are required (not included here)
Drone Inspections | OH | 1339388.7857 |  | 7 years | 124.5 | Pole | From SME | From SME - contains only the inspection cost (O&M from repair is removed)
Total OH Inspection Cost | OH | 2594515.9577
OH Replacement Capital | OH | 35621147 |  | 700 wood poles/year | 25000 | Pole | Historical Data (2020-2024) | 700 poles on average were replaced in the last 5 years. The poles for replacement are selected based on the age (oldest poles first)
OH Repair Capital | OH | 17400000 |  | 45 years* (every 45 years ) | 21000 | Pole | Historical Data (2020-2024) |  | *Frequencies were adjusted to match the current yearly spend
OH Repair and Replacement O&M | OH | 40070241.8275 |  | 8 years* (every 8 years) | 13136 | Equipment | Historical Data (2020-2024) |  | *Frequencies were adjusted to match the current yearly spend
Total OH Repair and Replcament Cost | OH | 75691388.8275
O&M Inspection and Repair/Replacement Cost | OH | 42664757.7852 | 44291000
Capital Inspection and Repair/Replacement Cost | OH | 53021147 | 51081000
Total Inspection and Repair/Replacement Cost | OH | 95685904.7852 | 95372000
SS10 Inspection (Subsurface) | UG | 978118.476 |  | 10 years | 124.98 | Structure | Historical Data (2024) | Evaluate how much it costs to maintain UG asset in HFTD | 1 pole to 1 surface structure
AGI Inspection (Padmount) | UG | 448416.99 |  | 5 years | 53.55 | Padmount | Historical Data (2024) |  | 1 transformer to 1 padmount
Total UG Inspection Cost | UG | 1426535.466 | NA
UG Repair and Replacement Capital | UG | 16083971.0909 |  | 5 years** | 22080 | Mile | Historical Data (2020-2024) |  | In order to estimate the UG repair costs, we first look at the Non-HFTD (costs per structure converted it into miles) which have been maintained over a lot of years. HFTD costs are assumed to be 50% of Non-HFTD **The Non-HFTD costs used were 5 years of data (2020-2024) so this cost is estimated to occur every 5 years in the entire territory.
UF Repair and Replacement O&M | UG | 291376.2879 |  | 5 years** | 400 | Mile | Historical Data (2020-2024)
Total UG Repair Cost | UG | 16375347.3788 | NA
Veg Inspection | OH | 4364010 | All Territory: $ 06.10 M | 1/2 year (very half year) | 9 | Tree | Historical Data (2020-2024) |  | Twice a year in HFTD
Tree Trimming | OH | 26281038 | All Territory: $ 49.41 M | 2.5 years (40% of all inspections) | 271 | Tree | Historical Data (2020-2024) |  | Assume 50% work/cost in HFTD.
Tree Auditing | OH | 1333447.5 | All Territory: $ 02.46 M | 4 years (25% of all inspection) | 22 | Tree | Historical Data (2020-2024) |  | Assume 50% work/cost in HFTD.
Veg Pole Clearance Inspection | OH | 251370 | All Territory: $ 00.36 M | 1 year | 9 | Pole | Historical Data (2020-2024)
Veg Pole Clearance Clearing | OH | 2811620 | All Territory: $ 5.42 M | 1.5 years (66% of all inspection) | 151 | Pole | Historical Data (2020-2024)
Veg Pole Clearance Audting | OH | 223440 | All Territory: $ 00.29 M | 3 years (33% of all inspection) | 24 | Pole | Historical Data (2020-2024) |  | Same % of poles in hftd are audited in the future
Fules Management | OH | 5535218.1818 | 5450000 | 55 years | 10900 | Pole | Historical Data (2020-2024) |  | $5.45M budget per year
Total Veg Cost | OH | 40800143.6818
Total CC PSPS Cost | OH | 18731138.4065 | 21151000 | 1 year | $1000 (activation) + $252/ (baseline) + $4963.4 (community outreach and engagement) | Mile | Historical Data (2020-2024) Community Outreach (2024) |  | - Activiation cost is calculated using difference between costs for years where PSPS occurred - PSPS did not occur/miles. The rest is considered as baseline. - To calculate the likelihood of segment being PSPS'ed, we use simulation PSPS events per year (if CCed). This is then multiplied by the unit cost to estimate the cost of PSPS.
Total UG PSPS Cost | UG | 9275319.9543 | NA | 1 year | $1000 (activation) + $126 (baseline) + $2482 (community outreach and engagement) | Mile | Historical Data (2020-2024) Community Outreach (2024) |  | - Activiation cost is calculated using difference between costs for years where PSPS occurred - PSPS did not occur. The rest is considered as baseline. - To calculate the likelihood of segment being PSPS'ed, we use simulation PSPS events per year (if UGed). This is then multiplied by the unit cost to estimate the cost of PSPS. - baseline EOC activation cost, community outreach and engagement 50% of OH
Total OH PEDS Cost | OH | 1733979.7913 | NA | 1 year | $634 ($454 EFD + $180 FCP) | Mile + Scada | From SME |  | EFD device would be installed every 3 miles (5 km) - confirmed with EFD team and FCP per segment (180 from SME for maintenance)
Total OH Microgrid Cost | OH | 0 | 0 | 1 year | 1273000 | Microgrid | From SME | No Microgrids for HFTD Segments