## Unit Cost
Component | Mitigation | Unit Cost | Units | Frequency per Year | Cycle | Used for Columns | Data Derived From | File Name
Detailed Inspection | CC | 18.53 | Pole | 0.2 | 5 | oh_detailed_insp_cost oh_detailed_insp_cost_per_mile | From SME | n/a
Patrol Inspection | CC | 7.1 | Pole | 1 | 1 | oh_patrol_insp_cost oh_patrol_insp_cost_per_mile | From SME | n/a
Drone Inspection | CC | 124.5 | Pole | 0.14286 | 7 | oh_drone_insp_cost oh_drone_insp_cost_per_mile | From SME | n/a
Steel Pole Replacement (vehicle contact only ~13/year) | CC | 25000 | Pole | 1 | 1 | cc_pole_replace_cost cc_pole_replace_cost_per_mile | From SME | n/a
Equipment Repair Capital | CC | 14706.01 | Issue | See sheet "Age based frequency" | See sheet "Age based frequency" | cc_repair_cost_cap cc_repair_cost_cap_per_mile | Historical Data (2023-2024) | “SDGE Response SPD-SDGE-WMP2026-02_Q7_Overhead Repair Costs (2023-24).xlsx”
Equipment Repair O&M | CC | 3678.72 | Issue | See sheet "Age based frequency" | See sheet "Age based frequency" | cc_repair_cost_om cc_repair_cost_om_per_mile | Historical Data (2023-2024) | “SDGE Response SPD-SDGE-WMP2026-02_Q7_Overhead Repair Costs (2023-24).xlsx”
Vegetation (Inspection) | CC | 9 | Tree | 0.5 | 2 | veg_insp_cost veg_insp_cost_per_mile | Historical Data (2015-2023) | “SDGE Response SPD-SDGE-WMP2026-02_Q7_Vegetation Management Costs (2015-2023).xlsx”
Vegetation (Tree Trimming) | CC | 271 | Tree | 0.4 | 2.5 | tree_trimming_cost tree_trimming_cost_per_mile | Historical Data (2015-2023) | “SDGE Response SPD-SDGE-WMP2026-02_Q7_Vegetation Management Costs (2015-2023).xlsx”
Vegetation (Tree Auditing) | CC | 22 | Tree | 0.25 | 4 | tree_audit_cost tree_audit_cost_per_mile | Historical Data (2015-2023) | “SDGE Response SPD-SDGE-WMP2026-02_Q7_Vegetation Management Costs (2015-2023).xlsx”
Veg Pole Clearance (Inspection) | CC | 9 | Pole | 1 | 1 | veg_pole_clearance_insp_cost veg_pole_clearance_insp_cost_per_mile | Historical Data (2015-2023) | “SDGE Response SPD-SDGE-WMP2026-02_Q7_Vegetation Management Costs (2015-2023).xlsx”
Veg Pole Clearance | CC | 151 | Pole | 0.66667 | 1.5 | veg_pole_clearance_cost veg_pole_clearance_cost_per_mile | Historical Data (2015-2023) | “SDGE Response SPD-SDGE-WMP2026-02_Q7_Vegetation Management Costs (2015-2023).xlsx”
Veg Pole Clearance (Auditing) | CC | 24 | Pole | 0.33333 | 3 | veg_pole_clearance_audit_cost veg_pole_clearance_audit_cost_per_mile | Historical Data (2015-2023) | “SDGE Response SPD-SDGE-WMP2026-02_Q7_Vegetation Management Costs (2015-2023).xlsx”
Fuels Management | CC | 10900 | Pole | 1 | 1 | fuels_management_cost fuels_management_cost_per_mile | Historical Data (2015-2023) | “SDGE Response SPD-SDGE-WMP2026-02_Q7_Vegetation Management Costs (2015-2023).xlsx”
EFD Installation | CC | 454 | Node | 1 per 55 years | 55 | efd efd_per_mile | From SME | n/a
FCP Maintenance | CC | 180 | SCADA Device | 1 | 1 | fcp fcp_per_mile | From SME | n/a
PSPS Customer Outreach | CC | 4249 | Mile | 1 | 1 | oh_psps_comm_outreach_cost_per_mile oh_psps_comm_outreach_cost | Historical Data (2024) | “SDGE Response SPD-SDGE-WMP2026-02_Q7_PSPS Costs (2021-2024).xlsx”
PSPS Customer Outreach | UG | 1033 | Mile | 1 | 1 | ug_psps_comm_outreach_cost_per_mile ug_psps_comm_outreach_cost | Historical Data (2024) | “SDGE Response SPD-SDGE-WMP2026-02_Q7_PSPS Costs (2021-2024).xlsx”
PSPS Activation | CC | 434 | Mile | statistically simulated | 1 | cc_psps_activation_cost cc_psps_activation_cost_per_mile | Historical Data (2021-2024) | “SDGE Response SPD-SDGE-WMP2026-02_Q7_PSPS Costs (2021-2024).xlsx”
PSPS Activation - Baseline | CC | 109 | Mile | 1 | 1 | cc_psps_activation_cost cc_psps_activation_cost_per_mile | Historical Data (2021-2024) | “SDGE Response SPD-SDGE-WMP2026-02_Q7_PSPS Costs (2021-2024).xlsx”
PSPS Activation | UG | 434 | Mile | statistically simulated | 1 | ug_psps_activation_cost ug_psps_activation_cost_per_mile | Historical Data (2021-2024) | “SDGE Response SPD-SDGE-WMP2026-02_Q7_PSPS Costs (2021-2024).xlsx”
PSPS Activation - Baseline | UG | 109 | Mile | 1 | 1 | ug_psps_activation_cost ug_psps_activation_cost_per_mile | Historical Data (2021-2024) | “SDGE Response SPD-SDGE-WMP2026-02_Q7_PSPS Costs (2021-2024).xlsx”
Padmount (dead front AGI) Inspections | UG | 54 | Structure | 0.2 | 5 | ug_padmount_insp_cost ug_padmount_insp_cost_per_mile | Historical Data (2024) | “SDGE Response SPD-SDGE-WMP2026-02_Q7d_Underground Inspection Costs 2024.xlsx”
Subsurface Inspections (SS10 - not required by GO) | UG | 125 | Structure | 0.1 | 10 | ug_ss_insp_cost ug_ss_insp_cost_per_mile | Historical Data (2024) | “SDGE Response SPD-SDGE-WMP2026-02_Q7d_Underground Inspection Costs 2024.xlsx”
Patrol Inspections | UG | 73 | Mile | 1 | 1 | ug_patrol_insp_cost ug_patrol_insp_cost_per_mile | From SME | n/a
Padmount Repair Capital (dead front AGI) | UG | 11000 | Issue | Age Based Frequency | 5 | padmount_repair_cost_capital padmount_repair_cost_capital_per_mile | Historical Data (2023-2024) | “SDGE Response SPD-SDGE-WMP2026-02_Q7d_Underground Repair Costs (2023-24).xlsx”
Padmount Repair O&M (dead front AGI) | UG | 3650 | Issue | Age Based Frequency | 5 | padmount_repair_cost_om padmount_repair_cost_om_per_mile | Historical Data (2023-2024) | “SDGE Response SPD-SDGE-WMP2026-02_Q7d_Underground Repair Costs (2023-24).xlsx”
Subsurface Repair Capital (SS10 - not required by GO) | UG | 18500 | Issue | Age Based Frequency | 10 | ss_repair_cost_capital ss_repair_cost_capital_per_mile | Historical Data (2023-2024) | “SDGE Response SPD-SDGE-WMP2026-02_Q7d_Underground Repair Costs (2023-24).xlsx”
Subsurface Repair O&M (SS10 - not required by GO) | UG | 9100 | Issue | Age Based Frequency | 10 | ss_repair_cost_om ss_repair_cost_om_per_mile | Historical Data (2023-2024) | “SDGE Response SPD-SDGE-WMP2026-02_Q7d_Underground Repair Costs (2023-24).xlsx”
Unplanned Outage Restoration and Repair Costs | CC | 237 | Mile-Year | 1 | 1 | oh_failure_repair_cost oh_failure_repair_cost_per_mile | Historical Data (2019-2024) | “SDGE Response SPD-SDGE-WMP2026-02_Q7_Unplanned Outage Restoration and Repair Costs (2019-2024).xlsx”
Unplanned Outage Restoration and Repair Costs | UG | 297 | Mile-Year | 1 | 1 | ug_failure_repair_cost ug_failure_repair_cost_per_mile | Historical Data (2019-2024) | “SDGE Response SPD-SDGE-WMP2026-02_Q7_Unplanned Outage Restoration and Repair Costs (2019-2024).xlsx”
Microgrid Maintenance | Both | 1200000 | Microgrid | 1 | 1 | microgrid_cost microgrid_cost_per_mile | From SME | n/a

## Age Based Frequency
structuretype | cap_om | age_bucket | finding_per_mile_per_inspection | insp_type | cycles | structuretype | cap_om | age_bucket | finding_per_mile_per_year | cycles
Overhead | Both | 1-10 | 0.12543 | Detailed | 2 | Surface | Capital | 1-10 | 0.05439 | 10
Overhead | Both | 11-20 | 0.19579 | Detailed | 2 | Surface | O&M | 1-10 | 0.0026159 | 10
Overhead | Both | 21-30 | 0.38991 | Detailed | 2 | Underground | Capital | 1-10 | 0.0051212 | 10
Overhead | Both | 31-40 | 0.60544 | Detailed | 2 | Underground | O&M | 1-10 | 0.0023695 | 10
Overhead | Both | 41-50 | 0.69402 | Detailed | 2 | Surface | Capital | 11-20 | 0.067987 | 10
Overhead | Both | 51-55 | 0.76359 | Detailed | 1 | Surface | O&M | 11-20 | 0.0032699 | 10
Overhead | Both | 1-10 | 1.8568 | Drone | 1 | Underground | Capital | 11-20 | 0.0064015 | 10
Overhead | Both | 11-20 | 2.9155 | Drone | 1 | Underground | O&M | 11-20 | 0.0029619 | 10
Overhead | Both | 21-30 | 4.4492 | Drone | 2 | Surface | Capital | 21-30 | 0.084984 | 10
Overhead | Both | 31-40 | 4.9112 | Drone | 1 | Surface | O&M | 21-30 | 0.0040874 | 10
Overhead | Both | 41-50 | 6.5527 | Drone | 1 | Underground | Capital | 21-30 | 0.0080019 | 10
Overhead | Both | 51-55 | 4.7205 | Drone | 1 | Underground | O&M | 21-30 | 0.0037024 | 10
[6 empty] | Surface | Capital | 31-40 | 0.10623 | 10
[6 empty] | Surface | O&M | 31-40 | 0.0051092 | 10
[6 empty] | Underground | Capital | 31-40 | 0.010002 | 10
[6 empty] | Underground | O&M | 31-40 | 0.004628 | 10
[6 empty] | Surface | Capital | 41-55 | 0.13279 | 15
[6 empty] | Surface | O&M | 41-55 | 0.0063866 | 15
[6 empty] | Underground | Capital | 41-55 | 0.012503 | 15
[6 empty] | Underground | O&M | 41-55 | 0.005785 | 15