## SummaryHFTD_2019 (hidden)
Project ID | Unhardened Faults | Unhardened Years | Unhardened faults per operating year average | Hardened Faults | Hardened Years | Hardened faults per operating year average | Poles
0078-D | 6 | 16.6712 | 0.3599 | 0 | 2.337 | 0 | 26
0078-E | 3 | 15.2329 | 0.19694 | 0 | 3.7753 | 0 | 8
0078-G | 2 | 16.674 | 0.11995 | 0 | 2.3342 | 0 | 26
0079-A | 2 | 15.2219 | 0.13139 | 3 | 3.7863 | 0.79233 | 29
0079-M | 2 | 15.2356 | 0.13127 | 1 | 3.7726 | 0.26507 | 18
0079-P | 1 | 14.9315 | 0.066972 | 1 | 4.0767 | 0.2453 | 45
0157-T | 3 | 18.9562 | 0.15826 | 0 | 0.052055 | 0 | 8
0175-A | 2 | 16.0603 | 0.12453 | 0 | 2.9479 | 0 | 40
0175-B | 5 | 16.3068 | 0.30662 | 0 | 2.7014 | 0 | 32
0175-C | 3 | 16.2521 | 0.18459 | 0 | 2.7562 | 0 | 38
0175-D | 1 | 16.1178 | 0.062043 | 2 | 2.8904 | 0.69194 | 17
0175-E | 1 | 15.8274 | 0.063182 | 0 | 3.1808 | 0 | 9
0176-A | 2 | 16.2712 | 0.12292 | 2 | 2.737 | 0.73073 | 32
0176-C | 4 | 16.1178 | 0.24817 | 0 | 2.8904 | 0 | 24
0176-D | 4 | 18.0356 | 0.22178 | 0 | 0.9726 | 0 | 24
0176-E | 1 | 16.3123 | 0.061303 | 0 | 2.6959 | 0 | 28
0176-F | 0 | 17.6548 | 0 | 1 | 1.3534 | 0.73887 | 31
0176-H | 2 | 18.0356 | 0.11089 | 0 | 0.9726 | 0 | 17
0176-J | 2 | 16.3836 | 0.12207 | 0 | 2.6247 | 0 | 23
0212-A | 12 | 18.9973 | 0.63167 | 0 | 0.010959 | 0 | 71
0212-B | 20 | 18.9973 | 1.0528 | 0 | 0.010959 | 0 | 47
0215-A | 6 | 17.4932 | 0.34299 | 0 | 1.5151 | 0 | 27
0215-B | 5 | 17.4438 | 0.28663 | 0 | 1.5644 | 0 | 29
0215-C | 2 | 18.6877 | 0.10702 | 0 | 0.32055 | 0 | 32
0217-B | 2 | 17.6466 | 0.11334 | 0 | 1.3616 | 0 | 23
0217-C | 2 | 17.1726 | 0.11646 | 1 | 1.8356 | 0.54478 | 37
0217-D | 5 | 18.9753 | 0.2635 | 0 | 0.032877 | 0 | 33
0217-E | 3 | 18.9753 | 0.1581 | 0 | 0.032877 | 0 | 37
0217-F | 1 | 17.3781 | 0.057544 | 0 | 1.6301 | 0 | 28
0217-G | 1 | 17.674 | 0.05658 | 0 | 1.3342 | 0 | 18
0217-H | 3 | 18.2685 | 0.16422 | 0 | 0.73973 | 0 | 26
0217-J | 6 | 18.4603 | 0.32502 | 0 | 0.54795 | 0 | 26
0217-K | 1 | 18.2685 | 0.054739 | 0 | 0.73973 | 0 | 34
0217-M | 4 | 18.1808 | 0.22001 | 0 | 0.8274 | 0 | 31
0217-N | 2 | 18.1041 | 0.11047 | 0 | 0.90411 | 0 | 29
0217-P | 1 | 18.2685 | 0.054739 | 0 | 0.73973 | 0 | 27
0217-Q | 1 | 18.4603 | 0.05417 | 0 | 0.54795 | 0 | 30
0217-R | 6 | 18.7096 | 0.32069 | 0 | 0.29863 | 0 | 26
0217-V | 1 | 18.9781 | 0.052692 | 0 | 0.030137 | 0 | 5
0217-X (ASD) | 1 | 18.937 | 0.052807 | 0 | 0.071233 | 0 | 5
0220-C | 2 | 15.2767 | 0.13092 | 0 | 3.7315 | 0 | 18
0220-K | 2 | 15.789 | 0.12667 | 0 | 3.2192 | 0 | 28
0220-N | 6 | 15.8274 | 0.37909 | 0 | 3.1808 | 0 | 28
0220-Q | 3 | 16.3425 | 0.18357 | 0 | 2.6658 | 0 | 11
0221-A | 9 | 17.2685 | 0.52118 | 2 | 1.7397 | 1.1496 | 32
0221-F | 3 | 17.4164 | 0.17225 | 1 | 1.5918 | 0.62823 | 36
0221-G | 2 | 17.0904 | 0.11702 | 0 | 1.9178 | 0 | 22
0221-H | 1 | 15.8055 | 0.063269 | 0 | 3.2027 | 0 | 22
0221-I | 1 | 16.3863 | 0.061027 | 0 | 2.6219 | 0 | 32
0221-J | 3 | 16.0055 | 0.18744 | 0 | 3.0027 | 0 | 36
0221-K | 2 | 15.6137 | 0.12809 | 0 | 3.3945 | 0 | 42
0221-L | 0 | 15.9671 | 0 | 1 | 3.0411 | 0.32883 | 29
0221-M | 0 | 15.7726 | 0 | 1 | 3.2356 | 0.30906 | 24
0221-N | 2 | 15.9671 | 0.12526 | 0 | 3.0411 | 0 | 38
0221-O | 1 | 17.3644 | 0.057589 | 0 | 1.6438 | 0 | 14
0221-P | 0 | 17.1342 | 0 | 1 | 1.874 | 0.53363 | 25
0221-S | 2 | 17.6767 | 0.11314 | 0 | 1.3315 | 0 | 30
0221-V | 2 | 15.9233 | 0.1256 | 1 | 3.0849 | 0.32416 | 27
0221-W | 1 | 17.6548 | 0.056642 | 0 | 1.3534 | 0 | 13
0221-Y-PH1-SLAUGHTER | 1 | 17.5726 | 0.056907 | 1 | 1.4356 | 0.69656 | 2
0222-AA | 3 | 16.5945 | 0.18078 | 1 | 2.4137 | 0.4143 | 29
0222-K | 3 | 15.5452 | 0.19299 | 1 | 3.463 | 0.28877 | 32
0222-N | 1 | 15.6493 | 0.063901 | 0 | 3.3589 | 0 | 31
0222-R | 3 | 15.2795 | 0.19634 | 0 | 3.7288 | 0 | 45
0222-S | 1 | 15.1753 | 0.065896 | 0 | 3.8329 | 0 | 18
0222-U | 2 | 15.5726 | 0.12843 | 1 | 3.4356 | 0.29107 | 36
0222-W | 1 | 15.4877 | 0.064567 | 0 | 3.5205 | 0 | 40
0222-X | 3 | 15.8438 | 0.18935 | 0 | 3.1644 | 0 | 32
0222-Y | 2 | 15.8932 | 0.12584 | 0 | 3.1151 | 0 | 24
0222-Z | 3 | 16.3671 | 0.18329 | 0 | 2.6411 | 0 | 26
0230-A | 1 | 17.2493 | 0.057973 | 0 | 1.7589 | 0 | 16
0230-B | 8 | 18.0356 | 0.44357 | 0 | 0.9726 | 0 | 48
0230-C | 8 | 18.0356 | 0.44357 | 0 | 0.9726 | 0 | 39
0230-D | 6 | 18.0767 | 0.33192 | 0 | 0.93151 | 0 | 43
0230-E | 2 | 17.4411 | 0.11467 | 0 | 1.5671 | 0 | 22
0230-F | 1 | 17.589 | 0.056854 | 0 | 1.4192 | 0 | 31
0236-B | 2 | 15.8082 | 0.12652 | 1 | 3.2 | 0.3125 | 36
0237-C | 6 | 15.5452 | 0.38597 | 0 | 3.463 | 0 | 27
0237-F | 0 | 15.074 | 0 | 2 | 3.9342 | 0.50836 | 26
0237-G | 1 | 17.1726 | 0.058232 | 0 | 1.8356 | 0 | 26
0237-I | 2 | 18.9863 | 0.10534 | 0 | 0.021918 | 0 | 28
0237-N | 2 | 15.6493 | 0.1278 | 0 | 3.3589 | 0 | 25
0237-O | 2 | 15.4274 | 0.12964 | 0 | 3.5808 | 0 | 40
0237-P | 1 | 15.3671 | 0.065074 | 0 | 3.6411 | 0 | 45
0237-Q | 3 | 15.4274 | 0.19446 | 0 | 3.5808 | 0 | 28
0240-C | 1 | 15.1562 | 0.06598 | 0 | 3.8521 | 0 | 24
0240-D | 2 | 15.5589 | 0.12854 | 0 | 3.4493 | 0 | 23
0240-G | 2 | 17.7616 | 0.1126 | 1 | 1.2466 | 0.8022 | 33
0350-A | 1 | 17.3781 | 0.057544 | 0 | 1.6301 | 0 | 30
0350-D | 2 | 18.9753 | 0.1054 | 0 | 0.032877 | 0 | 34
0350-E | 1 | 18.5918 | 0.053787 | 0 | 0.41644 | 0 | 32
0350-F | 2 | 18.7781 | 0.10651 | 0 | 0.23014 | 0 | 41
0350-G | 3 | 17.7452 | 0.16906 | 0 | 1.263 | 0 | 26
0350-H | 1 | 17.7808 | 0.05624 | 0 | 1.2274 | 0 | 40
0350-I | 1 | 17.6932 | 0.056519 | 0 | 1.3151 | 0 | 24
0350-J | 1 | 18.5699 | 0.053851 | 0 | 0.43836 | 0 | 24
0350-K | 1 | 18.0712 | 0.055337 | 0 | 0.93699 | 0 | 32
0350-L | 2 | 18.7425 | 0.10671 | 0 | 0.26575 | 0 | 11
0350-M | 1 | 18.7425 | 0.053355 | 0 | 0.26575 | 0 | 3
0350-N-FT | 2 | 18.9342 | 0.10563 | 0 | 0.073973 | 0 | 8
0358-C | 1 | 15.4027 | 0.064924 | 2 | 3.6055 | 0.55471 | 30
0358-D | 1 | 14.8575 | 0.067306 | 0 | 4.1507 | 0 | 27
0441-CFSP | 1 | 15.8055 | 0.063269 | 0 | 3.2027 | 0 | 25
0442-D | 3 | 14.8959 | 0.2014 | 0 | 4.1123 | 0 | 14
0442-L | 1 | 18.9562 | 0.052753 | 0 | 0.052055 | 0 | 29
0442-M | 0 | 15.3178 | 0 | 1 | 3.6904 | 0.27097 | 12
0445-C | 1 | 17.5671 | 0.056925 | 1 | 1.4411 | 0.69392 | 42
0445-D | 1 | 17.7507 | 0.056336 | 0 | 1.2575 | 0 | 31
0445-F | 1 | 17.4164 | 0.057417 | 0 | 1.5918 | 0 | 14
0445-G | 1 | 17.4301 | 0.057372 | 0 | 1.5781 | 0 | 3
0445-K | 1 | 18.3178 | 0.054592 | 0 | 0.69041 | 0 | 41
0445-N | 6 | 18.3836 | 0.32638 | 0 | 0.62466 | 0 | 36
0445-U | 1 | 18.7068 | 0.053456 | 0 | 0.30137 | 0 | 20
0520-B | 2 | 16.6575 | 0.12007 | 0 | 2.3507 | 0 | 49
0520-C | 3 | 16.6356 | 0.18034 | 0 | 2.3726 | 0 | 28
0520-D | 1 | 16.4795 | 0.060682 | 0 | 2.5288 | 0 | 31
0520-F | 5 | 17.5726 | 0.28453 | 0 | 1.4356 | 0 | 60
0520-G | 1 | 16.5753 | 0.060331 | 0 | 2.4329 | 0 | 19
0520-H | 2 | 17.1342 | 0.11673 | 0 | 1.874 | 0 | 33
0520-I | 2 | 17.1342 | 0.11673 | 0 | 1.874 | 0 | 54
0520-L | 5 | 17.4438 | 0.28663 | 0 | 1.5644 | 0 | 51
0908-A | 2 | 17.9808 | 0.11123 | 0 | 1.0274 | 0 | 39
0908-C | 1 | 18.1151 | 0.055203 | 0 | 0.89315 | 0 | 39
0908-D | 5 | 18.8356 | 0.26545 | 0 | 0.1726 | 0 | 38
0908-E | 3 | 18.7068 | 0.16037 | 0 | 0.30137 | 0 | 33
0971-A | 5 | 16.4082 | 0.30473 | 0 | 2.6 | 0 | 37
0971-C | 1 | 16.7726 | 0.059621 | 0 | 2.2356 | 0 | 33
0971-D | 2 | 16.7726 | 0.11924 | 0 | 2.2356 | 0 | 44
0971-E | 3 | 16.1945 | 0.18525 | 0 | 2.8137 | 0 | 21
0971-F | 2 | 17.1726 | 0.11646 | 0 | 1.8356 | 0 | 34
0971-G | 3 | 16.3014 | 0.18403 | 0 | 2.7068 | 0 | 34
0971-I | 1 | 16.5041 | 0.060591 | 0 | 2.5041 | 0 | 27
0971-J | 6 | 16.4082 | 0.36567 | 1 | 2.6 | 0.38462 | 33
0971-M | 4 | 17.1726 | 0.23293 | 0 | 1.8356 | 0 | 32
0972-A | 2 | 16.5014 | 0.1212 | 0 | 2.5068 | 0 | 32
0972-B | 2 | 16.3589 | 0.12226 | 0 | 2.6493 | 0 | 26
0972-C | 2 | 16.2055 | 0.12342 | 1 | 2.8027 | 0.35679 | 26
0972-D | 1 | 16.2274 | 0.061624 | 0 | 2.7808 | 0 | 24
0974-B | 6 | 16.9342 | 0.35431 | 0 | 2.074 | 0 | 29
0974-C | 7 | 16.7836 | 0.41707 | 0 | 2.2247 | 0 | 27
0974-D | 2 | 16.8274 | 0.11885 | 0 | 2.1808 | 0 | 38
1030-B | 1 | 15.5589 | 0.064272 | 0 | 3.4493 | 0 | 17
1030-C | 5 | 16.3589 | 0.30564 | 1 | 2.6493 | 0.37746 | 42
1030-D | 3 | 18.726 | 0.1602 | 0 | 0.28219 | 0 | 41
1030-E | 1 | 16.8877 | 0.059215 | 0 | 2.1205 | 0 | 35
1030-F | 4 | 16.6384 | 0.24041 | 1 | 2.3699 | 0.42197 | 44
1030-I | 1 | 15.6356 | 0.063957 | 0 | 3.3726 | 0 | 29
1030-J | 5 | 16.8986 | 0.29588 | 0 | 2.1096 | 0 | 42
1030-K | 3 | 16.5753 | 0.18099 | 0 | 2.4329 | 0 | 26
1030-L | 2 | 16.2329 | 0.12321 | 0 | 2.7753 | 0 | 24
1030-M | 1 | 16.0356 | 0.062361 | 0 | 2.9726 | 0 | 31
1030-N | 2 | 16.6274 | 0.12028 | 0 | 2.3808 | 0 | 44
1030-O | 6 | 16.3589 | 0.36677 | 0 | 2.6493 | 0 | 58
1030-Q | 2 | 16.4603 | 0.1215 | 0 | 2.5479 | 0 | 31
1030-R | 3 | 16.6274 | 0.18043 | 0 | 2.3808 | 0 | 36
1030-T | 0 | 15.6411 | 0 | 1 | 3.3671 | 0.29699 | 7
1030-U | 5 | 16.8877 | 0.29607 | 0 | 2.1205 | 0 | 38
1458-B | 2 | 16.389 | 0.12203 | 0 | 2.6192 | 0 | 33
C1215 MAINLINE CFSP W/S R1 | 2 | 14.3397 | 0.13947 | 2 | 4.6685 | 0.4284 | 17
C157:2013 CFSP CNF RIDGEPI | 1 | 13.5973 | 0.073544 | 0 | 5.411 | 0 | 3
C220 PH 2 I RECONDUCT R8 | 3 | 14.6712 | 0.20448 | 0 | 4.337 | 0 | 50
C220 PH 2 L RECONDUCT R1 | 1 | 14.5589 | 0.068686 | 0 | 4.4493 | 0 | 29
C220 PH 2 O RECONDUCTOR | 2 | 14.8822 | 0.13439 | 0 | 4.126 | 0 | 15
C220 PH 4 G POLE CHGO R2 | 0 | 14.8274 | 0 | 2 | 4.1808 | 0.47837 | 8
C221 PH4 D POLE REPLA R2 | 2 | 15.3973 | 0.12989 | 1 | 3.611 | 0.27693 | 4
C221:ERI 2012 REBUILD | 3 | 14.6658 | 0.20456 | 0 | 4.3425 | 0 | 4
C221:ERI 2012 REBUILD IM R9 | 0 | 12.8164 | 0 | 2 | 6.1918 | 0.32301 | 11
C222 FIRE RISK MITIG PRJPH | 3 | 14.1233 | 0.21242 | 0 | 4.8849 | 0 | 74
C222 FIRE RISK MITIG PRO R1 | 1 | 14.1096 | 0.070874 | 1 | 4.8986 | 0.20414 | 15
C222 FIRE RISK MITIG PRO R2 | 1 | 13.1836 | 0.075852 | 0 | 5.8247 | 0 | 26
C222 FIRE RISK MITIG PROJP | 4 | 12.9699 | 0.30841 | 0 | 6.0384 | 0 | 51
C222 PH 1 F RECONDUCTOR | 1 | 15.2 | 0.065789 | 0 | 3.8082 | 0 | 24
C222 PH 1 H RECONDUC R1 | 1 | 14.863 | 0.067281 | 0 | 4.1452 | 0 | 10
C222 PH 1 I RECONDUC R7 | 3 | 14.6219 | 0.20517 | 1 | 4.3863 | 0.22798 | 25
C222 PH 1 P RECONDUC R7 | 4 | 14.4219 | 0.27736 | 0 | 4.5863 | 0 | 25
C222 PH 2 #T RECONDU R11 | 2 | 14.8548 | 0.13464 | 0 | 4.1534 | 0 | 23
C222 PH4 SEC2 CPOLE CHGOU | 5 | 14.3342 | 0.34881 | 0 | 4.674 | 0 | 29
C222 PH4 SEC2 DPOLE CH R1 | 2 | 14.0055 | 0.1428 | 0 | 5.0027 | 0 | 22
C230: 2013 FIRE HARDNG 4 R2 | 1 | 14.3123 | 0.06987 | 0 | 4.6959 | 0 | 2
C233 LONG SPAN EVAL P61 R18 | 1 | 13.9808 | 0.071527 | 0 | 5.0274 | 0 | 3
C236 PH 2 C RECONDUCTOR | 2 | 15.3507 | 0.13029 | 0 | 3.6575 | 0 | 20
C236 PH 2 D RECONDUCTOR | 3 | 15.4822 | 0.19377 | 0 | 3.526 | 0 | 35
C237 PH 2 A RECONDUCTOR | 1 | 14.6438 | 0.068288 | 0 | 4.3644 | 0 | 27
C237 PH 2 D RECONDUCT R1 | 3 | 14.5781 | 0.20579 | 1 | 4.4301 | 0.22573 | 38
C237 PH 2 E RECONDUCTOR | 1 | 14.4795 | 0.069063 | 0 | 4.5288 | 0 | 22
C237 PH 2 H RECONDUCT R8 | 1 | 14.6247 | 0.068378 | 1 | 4.3836 | 0.22813 | 22
C237 PH 2 J RECONDUCTOR | 2 | 14.5781 | 0.13719 | 0 | 4.4301 | 0 | 24
C237 PH 2 M RECONDUCTOR | 2 | 14.663 | 0.1364 | 0 | 4.3452 | 0 | 41
C239:2013 RIRAT RELIABILITY | 2 | 14.5753 | 0.13722 | 0 | 4.4329 | 0 | 12
C240 PH 2 E RECONDUCT R1 | 1 | 14.9425 | 0.066923 | 0 | 4.0658 | 0 | 28
C357:2011 CFSP WS,TW ON R12 | 1 | 14.2164 | 0.070341 | 0 | 4.7918 | 0 | 6
C358 PH 2 A RECONDUCTOR | 0 | 14.7918 | 0 | 1 | 4.2164 | 0.23717 | 9
C441 BRLINE CFSP W/S(P1 R1 | 1 | 14.926 | 0.066997 | 0 | 4.0822 | 0 | 28
C441 PH 4 POLE REPLACE R2 | 1 | 13.8219 | 0.072349 | 0 | 5.1863 | 0 | 16
C442 PH 2 J RECONDUCT R8 | 1 | 14.9671 | 0.066813 | 0 | 4.0411 | 0 | 10
C442 PH 4 BPOLE CHGOUT R1 | 2 | 14.2767 | 0.14009 | 0 | 4.7315 | 0 | 25
C442 PH 4 EPOLE CHGOUT R7 | 1 | 13.8027 | 0.072449 | 0 | 5.2055 | 0 | 4
C442 PH 4 FPOLE CHGOUT R1 | 2 | 15.3534 | 0.13026 | 0 | 3.6548 | 0 | 40
C442 PH 4 GPOLE CHGOUT R1 | 2 | 14.9397 | 0.13387 | 1 | 4.0685 | 0.24579 | 9
C442 PH 4 HPOLE CHGOUT/RE | 1 | 14.6137 | 0.068429 | 0 | 4.3945 | 0 | 21
C444 BRANCHLN CFSP P4 R1 | 11 | 14.9616 | 0.73521 | 0 | 4.0466 | 0 | 16
C444 BRANCHLN CFSP W/S R1 | 1 | 14.4055 | 0.069418 | 0 | 4.6027 | 0 | 5
C444 BRANCHLN PH1 P41936 | 1 | 14.389 | 0.069497 | 0 | 4.6192 | 0 | 13
C444 BRANCHLN PH2 P4196 R1 | 5 | 14.2274 | 0.35143 | 0 | 4.7808 | 0 | 23
C444,BU:2011 CFSP RCNDCT R8 | 2 | 12.7342 | 0.15706 | 0 | 6.274 | 0 | 14
C445 2012 CFSP WS BRANCH R1 | 6 | 14.9781 | 0.40059 | 1 | 4.0301 | 0.24813 | 34
C445,BU:LG SPAN/DESIMI R16 | 2 | 14.1068 | 0.14178 | 0 | 4.9014 | 0 | 5
C67,BAR:LG SPAN/DESIMIL R3 | 1 | 13.6411 | 0.073308 | 0 | 5.3671 | 0 | 13
C73 PH 4 APOLE CHGOUT/ R9 | 1 | 14.2192 | 0.070328 | 0 | 4.789 | 0 | 17
C73 PH 4 BPOLE CHGOUT/ R5 | 1 | 13.9836 | 0.071513 | 0 | 5.0247 | 0 | 28
C73 PH 4 CPOLE CHGOUT R11 | 2 | 15.0055 | 0.13328 | 0 | 4.0027 | 0 | 40
C73 PH 4 EPOLE CHGOUT R11 | 2 | 14.3068 | 0.13979 | 1 | 4.7014 | 0.2127 | 29
C78 PH4 BPOLE CHGOUT/R R8 | 1 | 14.2329 | 0.07026 | 0 | 4.7753 | 0 | 9
C78 PH4 CPOLE CHGOUT/RECO | 2 | 14.2329 | 0.14052 | 1 | 4.7753 | 0.20941 | 20
C79 FIRE RISK MITIGATION R2 | 5 | 14.5452 | 0.34376 | 0 | 4.463 | 0 | 72
C79 PH 2 R RECONDUCTOR | 1 | 14.8082 | 0.06753 | 0 | 4.2 | 0 | 22
C79 PH4 SEC 2 #G POLE R6 | 2 | 14.5671 | 0.1373 | 0 | 4.4411 | 0 | 15
C79 PH4 SEC 2 E POLE R1 | 2 | 14.4219 | 0.13868 | 0 | 4.5863 | 0 | 18
C79 PH4 SEC 2 K POLE R7 | 1 | 14.463 | 0.069142 | 0 | 4.5452 | 0 | 42
C973 PH 2 #A RECOND | 2 | 14.5233 | 0.13771 | 0 | 4.4849 | 0 | 17
CPE1-D | 1 | 15.0767 | 0.066327 | 0 | 3.9315 | 0 | 28
CPE1-PH-04-B | 1 | 14.3753 | 0.069564 | 0 | 4.6329 | 0 | 18
CRA1 PH 2 A RECONDUCTOR | 2 | 14.7507 | 0.13559 | 0 | 4.2575 | 0 | 23
PE1 PH 4 A POLE CHGO R11 | 6 | 14.5014 | 0.41375 | 0 | 4.5068 | 0 | 51
PE1 PH 4#C POLE CHGOUT/RE | 1 | 14.2795 | 0.070031 | 0 | 4.7288 | 0 | 11
C221 PH4 D POLE REPLA R2 | 0 | 15.3973 | 0 | 0 | 3.611 | 0 | 4
C221:ERI 2012 REBUILD | 0 | 14.6658 | 0 | 0 | 4.3425 | 0 | 4
C221:ERI 2012 REBUILD IM R9 | 0 | 12.8164 | 0 | 0 | 6.1918 | 0 | 11
C222 FIRE RISK MITIG PRJPH | 0 | 14.1233 | 0 | 0 | 4.8849 | 0 | 74
C222 FIRE RISK MITIG PRO R1 | 0 | 14.1096 | 0 | 0 | 4.8986 | 0 | 15
C222 FIRE RISK MITIG PRO R2 | 0 | 13.1836 | 0 | 0 | 5.8247 | 0 | 26
C222 FIRE RISK MITIG PROJP | 0 | 12.9699 | 0 | 0 | 6.0384 | 0 | 51
C222 PH 1 #L RECONDUC R1 | 0 | 14.6 | 0 | 0 | 4.4082 | 0 | 5
C222 PH 1 #O RECONDUC R1 | 0 | 14.4548 | 0 | 0 | 4.5534 | 0 | 39
C222 PH 1 #Q RECONDUC R3 | 0 | 14.6767 | 0 | 0 | 4.3315 | 0 | 15
C222 PH 1 F RECONDUCTOR | 0 | 15.2 | 0 | 0 | 3.8082 | 0 | 24
C222 PH 1 H RECONDUC R1 | 0 | 14.863 | 0 | 0 | 4.1452 | 0 | 10
C222 PH 1 I RECONDUC R7 | 0 | 14.6219 | 0 | 0 | 4.3863 | 0 | 25
C222 PH 1 J RECONDUC R6 | 0 | 14.7562 | 0 | 0 | 4.2521 | 0 | 19
C222 PH 1 M RECONDUC R6 | 0 | 14.7534 | 0 | 0 | 4.2548 | 0 | 19
C222 PH 1 P RECONDUC R7 | 0 | 14.4219 | 0 | 0 | 4.5863 | 0 | 25
C222 PH 2 #T RECONDU R11 | 0 | 14.8548 | 0 | 0 | 4.1534 | 0 | 23
C222 PH 2 V RECONDUCTOR | 0 | 14.8548 | 0 | 0 | 4.1534 | 0 | 35
C222 PH4 SEC2 APOLE CH R1 | 0 | 14.0603 | 0 | 0 | 4.9479 | 0 | 4
C222 PH4 SEC2 BPOLE CH R1 | 0 | 14.3479 | 0 | 0 | 4.6603 | 0 | 12
C222 PH4 SEC2 CPOLE CHGOU | 0 | 14.3342 | 0 | 0 | 4.674 | 0 | 29
C222 PH4 SEC2 DPOLE CH R1 | 0 | 14.0055 | 0 | 0 | 5.0027 | 0 | 22
C230: 2013 FIRE HARDNG 4 R2 | 0 | 14.3123 | 0 | 0 | 4.6959 | 0 | 2
C233 LONG SPAN EVAL P61 R18 | 0 | 13.9808 | 0 | 0 | 5.0274 | 0 | 3
C233, MN: RECONDUCTOR R4 | 0 | 13.0795 | 0 | 0 | 5.9288 | 0 | 38
C236 PH 2 A RECONDUCTOR | 0 | 14.4795 | 0 | 0 | 4.5288 | 0 | 19
C236 PH 2 C RECONDUCTOR | 0 | 15.3507 | 0 | 0 | 3.6575 | 0 | 20
C236 PH 2 D RECONDUCTOR | 0 | 15.4822 | 0 | 0 | 3.526 | 0 | 35
C237 PH 2 A RECONDUCTOR | 0 | 14.6438 | 0 | 0 | 4.3644 | 0 | 27
C237 PH 2 D RECONDUCT R1 | 0 | 14.5781 | 0 | 0 | 4.4301 | 0 | 38
C237 PH 2 E RECONDUCTOR | 0 | 14.4795 | 0 | 0 | 4.5288 | 0 | 22
C237 PH 2 H RECONDUCT R8 | 0 | 14.6247 | 0 | 0 | 4.3836 | 0 | 22
C237 PH 2 J RECONDUCTOR | 0 | 14.5781 | 0 | 0 | 4.4301 | 0 | 24
C237 PH 2 L RECONDUCTOR | 0 | 14.7589 | 0 | 0 | 4.2493 | 0 | 30
C237 PH 2 M RECONDUCTOR | 0 | 14.663 | 0 | 0 | 4.3452 | 0 | 41
C239: RELOCATION TO MITI R5 | 0 | 13.4356 | 0 | 0 | 5.5726 | 0 | 3
C239:2013 RIRAT RELIABILITY | 0 | 14.5753 | 0 | 0 | 4.4329 | 0 | 12
C240 PH 2 A RECONDUCT R1 | 0 | 14.8274 | 0 | 0 | 4.1808 | 0 | 32
C240 PH 2 E RECONDUCT R1 | 0 | 14.9425 | 0 | 0 | 4.0658 | 0 | 28
C240 PH 2 H RECONDUCT R1 | 0 | 14.8877 | 0 | 0 | 4.1205 | 0 | 8
C350,LI:LG SPA/DESIMILAR W | 0 | 13.8329 | 0 | 0 | 5.1753 | 0 | 7
C357:2011 CFSP WS,TW ON R12 | 0 | 14.2164 | 0 | 0 | 4.7918 | 0 | 6
C357:2011 CFSP WS,TW ON R4 | 0 | 13.5616 | 0 | 0 | 5.4466 | 0 | 7
C358 PH 2 A RECONDUCTOR | 0 | 14.7918 | 0 | 0 | 4.2164 | 0 | 9
C358 PH 2 B RECONDUCTOR | 0 | 14.6192 | 0 | 0 | 4.389 | 0 | 14
C441 BRLINE CFSP W/S(P1 R1 | 0 | 14.926 | 0 | 0 | 4.0822 | 0 | 28
C441 PH 4 POLE REPLACE R2 | 0 | 13.8219 | 0 | 0 | 5.1863 | 0 | 16
C441 PHASE 4RECONDCTR P R6 | 0 | 13.2822 | 0 | 0 | 5.726 | 0 | 7
C441: REBUILD P40714 TO R13 | 0 | 13.3973 | 0 | 0 | 5.611 | 0 | 10
C442 PH 2 J RECONDUCT R8 | 0 | 14.9671 | 0 | 0 | 4.0411 | 0 | 10
C442 PH 2 K RECONDUCT R7 | 0 | 15.1562 | 0 | 0 | 3.8521 | 0 | 32
C442 PH 4 APOLE CHGOUT R1 | 0 | 14.1589 | 0 | 0 | 4.8493 | 0 | 5
C442 PH 4 BPOLE CHGOUT R1 | 0 | 14.2767 | 0 | 0 | 4.7315 | 0 | 25
C442 PH 4 CPOLE CHGOUT R1 | 0 | 14.5534 | 0 | 0 | 4.4548 | 0 | 9
C442 PH 4 EPOLE CHGOUT R7 | 0 | 13.8027 | 0 | 0 | 5.2055 | 0 | 4
C442 PH 4 FPOLE CHGOUT R1 | 0 | 15.3534 | 0 | 0 | 3.6548 | 0 | 40
C442 PH 4 GPOLE CHGOUT R1 | 0 | 14.9397 | 0 | 0 | 4.0685 | 0 | 9
C442 PH 4 HPOLE CHGOUT/RE | 0 | 14.6137 | 0 | 0 | 4.3945 | 0 | 21
C444 BRANCHLN CFSP P4 R1 | 0 | 14.9616 | 0 | 0 | 4.0466 | 0 | 16
C444 BRANCHLN CFSP W/S R1 | 0 | 14.4055 | 0 | 0 | 4.6027 | 0 | 5
C444 BRANCHLN PH1 P41936 | 0 | 14.389 | 0 | 0 | 4.6192 | 0 | 13
C444 BRANCHLN PH2 P4196 R1 | 0 | 14.2274 | 0 | 0 | 4.7808 | 0 | 23
C444,BU:2011 CFSP RCNDCT R8 | 0 | 12.7342 | 0 | 0 | 6.274 | 0 | 14
C445 2012 CFSP WS BRANCH R1 | 0 | 14.9781 | 0 | 0 | 4.0301 | 0 | 34
C445,BU:LG SPAN/DESIMI R16 | 0 | 14.1068 | 0 | 0 | 4.9014 | 0 | 5
C521,AV:LG SPAN/DESIMILAR | 0 | 14.1178 | 0 | 0 | 4.8904 | 0 | 4
C67,BAR:LG SPAN/DESIMIL R3 | 0 | 13.6411 | 0 | 0 | 5.3671 | 0 | 13
C73 PH 2 I RECONDUCTO R1 | 0 | 14.8959 | 0 | 0 | 4.1123 | 0 | 8
C73 PH 2 JPOLE CHGOUT/ R1 | 0 | 15.2575 | 0 | 0 | 3.7507 | 0 | 6
C73 PH 4 APOLE CHGOUT/ R9 | 0 | 14.2192 | 0 | 0 | 4.789 | 0 | 17
C73 PH 4 BPOLE CHGOUT/ R5 | 0 | 13.9836 | 0 | 0 | 5.0247 | 0 | 28
C73 PH 4 CPOLE CHGOUT R11 | 0 | 15.0055 | 0 | 0 | 4.0027 | 0 | 40
C73 PH 4 EPOLE CHGOUT R11 | 0 | 14.3068 | 0 | 0 | 4.7014 | 0 | 29
C73 PH 4 FPOLE CHGOUT/ R8 | 0 | 14.1973 | 0 | 0 | 4.811 | 0 | 7
C78 PH2 F RECONDUCTOR | 0 | 15.4082 | 0 | 0 | 3.6 | 0 | 12
C78 PH4 APOLE CHGOUT/R R1 | 0 | 14.0027 | 0 | 0 | 5.0055 | 0 | 8
C78 PH4 BPOLE CHGOUT/R R8 | 0 | 14.2329 | 0 | 0 | 4.7753 | 0 | 9
C78 PH4 CPOLE CHGOUT/RECO | 0 | 14.2329 | 0 | 0 | 4.7753 | 0 | 20
C79 FIRE RISK MITIGATION R2 | 0 | 14.5452 | 0 | 0 | 4.463 | 0 | 72
C79 PH 1 #O RECONDUCTOR | 0 | 14.8521 | 0 | 0 | 4.1562 | 0 | 14
C79 PH 1 N RECONDUCTO R2 | 0 | 14.4822 | 0 | 0 | 4.526 | 0 | 6
C79 PH 2 R RECONDUCTOR | 0 | 14.8082 | 0 | 0 | 4.2 | 0 | 22
C79 PH4 SEC 2 #G POLE R6 | 0 | 14.5671 | 0 | 0 | 4.4411 | 0 | 15
C79 PH4 SEC 2 E POLE R1 | 0 | 14.4219 | 0 | 0 | 4.5863 | 0 | 18
C79 PH4 SEC 2 F POLE R1 | 0 | 14.6192 | 0 | 0 | 4.389 | 0 | 14
C79 PH4 SEC 2 H POLE R1 | 0 | 14.526 | 0 | 0 | 4.4822 | 0 | 22
C79 PH4 SEC 2 K POLE R7 | 0 | 14.463 | 0 | 0 | 4.5452 | 0 | 42
C79 PH4 SEC 2 L POLE R1 | 0 | 14.3753 | 0 | 0 | 4.6329 | 0 | 15
C908:LONG SPAN RFS REL R2 | 0 | 12.8904 | 0 | 0 | 6.1178 | 0 | 7
C973 PH 2 #A RECOND | 0 | 14.5233 | 0 | 0 | 4.4849 | 0 | 17
C974 E RECONDUCTOR R1 | 0 | 15.2 | 0 | 0 | 3.8082 | 0 | 24
CPE1-D | 0 | 15.0767 | 0 | 0 | 3.9315 | 0 | 28
CPE1-PH-04-B | 0 | 14.3753 | 0 | 0 | 4.6329 | 0 | 18
CRA1 PH 2 A RECONDUCTOR | 0 | 14.7507 | 0 | 0 | 4.2575 | 0 | 23
PE1 PH 4 A POLE CHGO R11 | 0 | 14.5014 | 0 | 0 | 4.5068 | 0 | 51
PE1 PH 4#C POLE CHGOUT/RE | 0 | 14.2795 | 0 | 0 | 4.7288 | 0 | 11
Track 2 530000153622 | 0 | 18.6384 | 0 | 0 | 0.36986 | 0 | 13
Average | 1.6925 | 15.6848 | 0.10791 | 0.15839 | 3.3235 | 0.047657 | 24.9783
Unhardened faults per year per 100 miles | 10.0055
Hardened faults per year per 100 miles | 4.4187
Reduction | 55.84%

## Read Me
The distribution hardening study calculates the fault rate per 100 miles for all risk events that included location information​
Tab | Description
Raw Data | This tab represent underlying hardening data and outage data used to perform this analysis
Summary Effectiveness | This tab summarizes outage data and hardening data by Project and calculates before/after overhead hardening average fault rate per year per 100 circuit miles​
Effectiveness_by_Driver | This tab has summary calculations by cause and lists the average fault rate per year per 100 circuit miles by driver
The blue highlighted number represents asset degradation in 10 years
Effectiveness_by_Driver
Avg_Unhardened Faults | Before overhead hardening, the average fault per year
Avg_Unhardened Years | Before overhead hardening, the average age of the asset per year
Unhardened faults per operating year average | Before overhead hardening, the average fault rate per year
Avg_Hardened Faults | After overhead hardening, the average fault per year
Avg_Hardened Years | After overhead hardening, the average age of the asset per year
Hardened faults per operating year average | After overhead hardening, the average fault rate per year
Avg_Poles | Average number of poles in scope per project
Avg_Hardened rate | After overhead hardening, the average fault rate per year per 100 circuit miles​
Avg_Unhardened rate | Before overhead hardening, the average fault rate per year per 100 circuit miles​

## Raw Data
Outage_ID | Project_ID | failure_time | h_years_calc | uh_years_calc | Hardened Faults | Zone | Hardened Date | Outage Date | Cause_Category | Cause | Secondary_Cause | DamagedDevice | StructureID | FromFacility | ToFacility | Hyear | Oyear
010312E5006 | 0212-W | Before | 3.6849 | 19.326 | 2 | Tier 2 | 2020-04-25 | 2001-03-12 | Tree Contact | 322 | 532 | POLE | P218166 | P218166 | 0 | 2020 | 2001
010815E5027 | 0217-R | Before | 4.3014 | 18.7096 | 2 | Tier 2 | 2019-09-13 | 2001-08-15 | Equipment | 508 |  |  | P112447 | P112447 | 0 | 2019 | 2001
010818E5014 | 0217-R | Before | 4.3014 | 18.7096 | 2 | Tier 2 | 2019-09-13 | 2001-08-18 | Equipment | 508 |  |  | P112447 | P112447 | 0 | 2019 | 2001
010902E5016 | 0222-FF-PH-02 | Before | 1.7863 | 21.2247 | 2 | Tier 3 | 2022-03-19 | 2001-09-02 | Weather | 410 |  |  | P412773 | P412773 | 0 | 2022 | 2001
010902E5028 | 0221-F | Before | 5.5945 | 17.4164 | 2 | Tier 3 | 2018-05-29 | 2001-09-02 | Weather | 410 |  |  | P117926 | P117926 | 0 | 2018 | 2001
010903E5009 | 0971-A | Before | 6.6027 | 16.4082 | 2 | Tier 3 | 2017-05-26 | 2001-09-03 | Customer Contact | 710 | 532 | POLE | P318998 | P318998 | 0 | 2017 | 2001
010920E7502 | 0971-G | Before | 6.7096 | 16.3014 | 2 | Tier 3 | 2017-04-17 | 2001-09-20 | Customer Contact | 702 | 214 |  | P111551 | P111551 | 0 | 2017 | 2001
010924E5001 | C222 PH 1 P RECONDUC R7 | Before | 8.589 | 14.4219 | 2 | Tier 3 | 2015-06-01 | 2001-09-24 | Undetermined | 100 |  |  | P318190 | P318190 | 0 | 2015 | 2001
010926E5040 | C236 PH 2 C RECONDUCTOR | Before | 7.6603 | 15.3507 | 2 | Tier 3 | 2016-05-05 | 2001-09-26 | Undetermined | 100 |  |  | P101313 | P101313 | 0 | 2016 | 2001
010930E5026 | 0971-A | Before | 6.6027 | 16.4082 | 2 | Tier 2 | 2017-05-26 | 2001-09-30 | Weather | 412 |  |  | P111379 | P111379 | 0 | 2017 | 2001
011001E5002 | 0212-A | Before | 4.0137 | 18.9973 | 2 | Tier 2 | 2019-12-27 | 2001-10-01 | Weather | 404 |  |  | P19585 | P19585 | 0 | 2019 | 2001
011004E5006 | C222 FIRE RISK MITIG PROJP | Before | 10.0411 | 12.9699 | 2 | Tier 3 | 2013-12-18 | 2001-10-04 | Undetermined | 100 |  |  | P179178 | P179178 | 0 | 2013 | 2001
011013E5013 | PE1 PH 4 A POLE CHGO R11 | Before | 8.5096 | 14.5014 | 2 | Tier 3 | 2015-06-30 | 2001-10-13 | Foreign Object | 308 |  |  | P18901 | P18901 | 0 | 2015 | 2001
011016E5001 | 0212-A | Before | 4.0137 | 18.9973 | 2 | Tier 2 | 2019-12-27 | 2001-10-16 | Undetermined | 100 |  |  | P19585 | P19585 | 0 | 2019 | 2001
011028E7501 | 0350-G | Before | 5.2658 | 17.7452 | 2 | Tier 2 | 2018-09-26 | 2001-10-28 | Equipment | 516 |  |  | P413166 | P413166 | 0 | 2018 | 2001
011110E5004 | CPE1-PH-04-B | Before | 8.6356 | 14.3753 | 2 | Tier 3 | 2015-05-15 | 2001-11-10 | Foreign Object | 308 |  |  | P19722 | P19722 | 0 | 2015 | 2001
011113E5009 | 0212-D | Before | 3.2822 | 19.7288 | 2 | Tier 3 | 2020-09-19 | 2001-11-13 | Weather | 412 |  |  | P112501 | P112501 | 0 | 2020 | 2001
011124E5080 | 0230-E | Before | 5.5699 | 17.4411 | 1 | Tier 2 | 2018-06-07 | 2001-11-24 | Weather | 408 | 520 | FUSE | P610754 | P610754 | 0 | 2018 | 2001
011126E5007 | C222 FIRE RISK MITIG PROJP | Before | 10.0411 | 12.9699 | 2 | Tier 3 | 2013-12-18 | 2001-11-26 | Undetermined | 100 |  |  | P179178 | P179178 | 0 | 2013 | 2001
011207E5090 | C78 PH4 CPOLE CHGOUT/RECO | Before | 8.7781 | 14.2329 | 2 | Tier 3 | 2015-03-24 | 2001-12-07 | Weather | 412 |  |  | P172729 | P172729 | 0 | 2015 | 2001
011207E5099 | CNF-TL629A | Before | 3.2849 | 19.726 | 1 | Tier 3 | 2020-09-18 | 2001-12-07 | Weather | 408 | 516 |  | P273070 | P273070 | 0 | 2020 | 2001
011210E7501 | 0972-D | Before | 6.7836 | 16.2274 | 3 | Tier 2 | 2017-03-21 | 2001-12-10 | Undetermined | 100 |  |  | P513013 | P513013 | 0 | 2017 | 2001
011229E5007 | 0212-GG | Before | 2.3863 | 20.6247 | 2 | Tier 2 | 2021-08-12 | 2001-12-29 | Undetermined | 100 |  |  | P216828 | P216828 | 0 | 2021 | 2001
020116E5050 | 0175-C | Before | 6.7589 | 16.2521 | 2 | Tier 3 | 2017-03-30 | 2002-01-16 | Foreign Object | 308 | 510 |  | P103768 | P103768 | 0 | 2017 | 2002
020209E5079 | 0442-L | Before | 4.0548 | 18.9562 | 3 | Tier 3 | 2019-12-12 | 2002-02-09 | Weather | 412 | 420 |  | P772067 | P772067 | 0 | 2019 | 2002
020210E5005 | 0212-B | Before | 4.0137 | 18.9973 | 1 | Tier 3 | 2019-12-27 | 2002-02-10 | Weather | 412 | 532 | POLE | P19514 | P19514 | 0 | 2019 | 2002
020210E5005 | 0212-B | Before | 4.0137 | 18.9973 | 2 | Tier 3 | 2019-12-27 | 2002-02-10 | Weather | 412 | 532 | POLE | P19514 | P19514 | 0 | 2019 | 2002
020210E5064 | 1030-R | Before | 6.3836 | 16.6274 | 2 | Tier 3 | 2017-08-14 | 2002-02-10 | Weather | 426 | 510 |  | P115512 | P115512 | 0 | 2017 | 2002
020210E5125 | 0215-B | Before | 5.5671 | 17.4438 | 2 | Tier 2 | 2018-06-08 | 2002-02-10 | Weather | 412 | 532 | POLE | P318284 | P318284 | 0 | 2018 | 2002
020210E5277 | 0078-D | Before | 6.3397 | 16.6712 | 2 | Tier 3 | 2017-08-30 | 2002-02-10 | Weather | 412 | 510 |  | P175204 | P175204 | 0 | 2017 | 2002
020210E7502 | 0221-K | Before | 7.3973 | 15.6137 | 3 | Tier 3 | 2016-08-09 | 2002-02-10 | Weather | 412 | 513 |  | P115701 | P115701 | 0 | 2016 | 2002
020211E5005 | 0445-N | Before | 4.6274 | 18.3836 | 1 | Tier 2 | 2019-05-17 | 2002-02-11 | Customer Contact | 710 | 532 | POLE | P41245 | P41245 | 0 | 2019 | 2002
020211E5005 | 0445-O | Before | 3.3397 | 19.6712 | 1 | Tier 2 | 2020-08-29 | 2002-02-11 | Customer Contact | 710 | 532 | POLE | P41245 | P41245 | 0 | 2020 | 2002
020216E5025 | 0078-G | Before | 6.337 | 16.674 | 1 | Tier 3 | 2017-08-31 | 2002-02-16 | Customer Contact | 710 | 532 | POLE | P78900 | P78900 | 0 | 2017 | 2002
020216E5025 | 0078-G | Before | 6.337 | 16.674 | 2 | Tier 3 | 2017-08-31 | 2002-02-16 | Customer Contact | 710 | 532 | POLE | P78900 | P78900 | 0 | 2017 | 2002
020610E5002 | 0974-D | Before | 6.1836 | 16.8274 | 2 | Tier 3 | 2017-10-26 | 2002-06-10 | Foreign Object | 308 |  |  | P876248 | P876248 | 0 | 2017 | 2002
020629E5024 | 0222-FF-PH-02 | Before | 1.7863 | 21.2247 | 2 | Tier 3 | 2022-03-19 | 2002-06-29 | Equipment | 522 |  | FUSE | P412773 | P412773 | 0 | 2022 | 2002
020727E5032 | 0445-Q | Before | 2.0356 | 20.9753 | 1 | Tier 2 | 2021-12-18 | 2002-07-27 | Customer Contact | 710 | 532 | POLE | P41365 | P41365 | 0 | 2021 | 2002
020727E5032 | 0445-Q | Before | 2.0356 | 20.9753 | 1 | Tier 2 | 2021-12-18 | 2002-07-27 | Customer Contact | 710 | 532 | POLE | P41365 | P41365 | 0 | 2021 | 2002
020928E7601 | 0212-B | Before | 4.0137 | 18.9973 | 2 | Tier 3 | 2019-12-27 | 2002-09-28 | Foreign Object | 308 | 520 | FUSE | P19529 | P19529 | 0 | 2019 | 2002
021103E5002 | 0222-PP | Before | 2.1123 | 20.8986 | 3 | Tier 3 | 2021-11-20 | 2002-11-03 | Undetermined | 100 |  | FUSE | P110228 | P110228 | 0 | 2021 | 2002
021103E5002 | 0222-PP | Before | 2.1123 | 20.8986 | 2 | Tier 3 | 2021-11-20 | 2002-11-03 | Undetermined | 100 |  | FUSE | P110228 | P110228 | 0 | 2021 | 2002
021107E5005 | 0448-A | Before | 2.2466 | 20.7644 | 2 | Tier 3 | 2021-10-02 | 2002-11-07 | Customer Contact | 710 | 532 | POLE | P45608 | P45608 | 0 | 2021 | 2002
021125E5135 | C445,BU:LG SPAN/DESIMI R16 | Before | 8.9041 | 14.1068 | 2 | Tier 2 | 2015-02-06 | 2002-11-25 | Customer Contact | 710 | 532 | POLE | P41268 | P41268 | 0 | 2015 | 2002
021128E5052 | 1030-J | Before | 6.1123 | 16.8986 | 1 | Tier 3 | 2017-11-21 | 2002-11-28 | Weather | 412 | 510 | OH CONDUCTOR | P112248 | P112248 | 0 | 2017 | 2002
021128E5052 | 1030-K | Before | 6.4356 | 16.5753 | 2 | Tier 3 | 2017-07-26 | 2002-11-28 | Weather | 412 | 510 | OH CONDUCTOR | P112248 | P112248 | 0 | 2017 | 2002
021128E5115 | 0908-G | Before | 0.99178 | 22.0192 | 1 | Tier 2 | 2023-01-03 | 2002-11-28 | Weather | 412 | 510 | OH CONDUCTOR | P112884 | P112884 | 0 | 2023 | 2002
021128E7101 | 0217-D | Before | 4.0356 | 18.9753 | 2 | Tier 3 | 2019-12-19 | 2002-11-28 | Weather | 404 |  | FUSE | P514940 | P514940 | 0 | 2019 | 2002
021128E7102 | 448U | Before | 2.4822 | 20.5288 | 2 | Tier 3 | 2021-07-08 | 2002-11-28 | Weather | 420 | 510 | FUSE | P46054 | P46054 | 0 | 2021 | 2002
021211E5034 | 0217-C | Before | 5.8384 | 17.1726 | 2 | Tier 3 | 2018-03-01 | 2002-12-11 | Equipment | 554 |  | CROSSARM | P214792 | P214792 | 0 | 2018 | 2002
030107E5010 | 0237-I | Before | 4.0247 | 18.9863 | 2 | Tier 3 | 2019-12-23 | 2003-01-07 | Weather | 412 | 513 | OH CONDUCTOR | P113838 | P113838 | 0 | 2019 | 2003
030107E7101 | 0350-H | Before | 5.2301 | 17.7808 | 2 | Tier 2 | 2018-10-09 | 2003-01-07 | Weather | 412 | 513 | OH CONDUCTOR | P213248 | P213248 | 0 | 2018 | 2003
030107E7101 | 0350-J | Before | 4.4411 | 18.5699 | 1 | Tier 2 | 2019-07-24 | 2003-01-07 | Weather | 412 | 513 | OH CONDUCTOR | P213248 | P213248 | 0 | 2019 | 2003
030107E7604 | 0908-E | Before | 4.3041 | 18.7068 | 2 | Tier 2 | 2019-09-12 | 2003-01-07 | Weather | 404 |  | FUSE | P116881 | P116881 | 0 | 2019 | 2003
030108E5335 | C222 PH 1 I RECONDUC R7 | Before | 8.389 | 14.6219 | 2 | Tier 3 | 2015-08-13 | 2003-01-08 | Weather | 412 | 513 | OH CONDUCTOR | P416864 | P416864 | 0 | 2015 | 2003
030109E5119 | 0908-D | Before | 4.1753 | 18.8356 | 2 | Tier 2 | 2019-10-29 | 2003-01-09 | Equipment | 534 |  | POTHEAD | P133517 | P133517 | 0 | 2019 | 2003
030303E7601 | 0971-M | Before | 5.8384 | 17.1726 | 2 | Tier 3 | 2018-03-01 | 2003-03-03 | Customer Contact | 710 | 532 | POLE | P413406 | P413406 | 0 | 2018 | 2003
030329E7104 | 0442-D | Before | 8.1151 | 14.8959 | 2 | Tier 3 | 2015-11-21 | 2003-03-29 | Equipment | 532 |  | POLE | P173172 | P173172 | 0 | 2015 | 2003
030412E5006 | 0217-R | Before | 4.3014 | 18.7096 | 2 | Tier 2 | 2019-09-13 | 2003-04-12 | Customer Contact | 710 | 513 | OH CONDUCTOR | P14988 | P14988 | 0 | 2019 | 2003
030413E5004 | 0237-C | Before | 7.4658 | 15.5452 | 2 | Tier 3 | 2016-07-15 | 2003-04-13 | Equipment | 534 |  | POTHEAD | P17649 | P17649 | 0 | 2016 | 2003
030414E5004 | 0237-C | Before | 7.4658 | 15.5452 | 2 | Tier 3 | 2016-07-15 | 2003-04-14 | Equipment | 534 |  | POTHEAD | P17649 | P17649 | 0 | 2016 | 2003
030420E5014 | 0520-L | Before | 5.5671 | 17.4438 | 2 | Tier 2 | 2018-06-08 | 2003-04-20 | Equipment | 513 |  | OH CONDUCTOR | P119029 | P119029 | 0 | 2018 | 2003
030421E5013 | C445 2012 CFSP WS BRANCH R1 | Before | 8.0329 | 14.9781 | 2 | Tier 2 | 2015-12-21 | 2003-04-21 | Equipment | 513 | 530 | OH CONDUCTOR | P41589 | P41589 | 0 | 2015 | 2003
030614E5042 | 1030-K | Before | 6.4356 | 16.5753 | 2 | Tier 3 | 2017-07-26 | 2003-06-14 | Undetermined | 100 |  | FUSE | P112257 | P112257 | 0 | 2017 | 2003
030614E5042 | 1030-O | Before | 6.6521 | 16.3589 | 1 | Tier 3 | 2017-05-08 | 2003-06-14 | Undetermined | 100 |  | FUSE | P112257 | P112257 | 0 | 2017 | 2003
030824E5063 | 0215-A | Before | 5.5178 | 17.4932 | 2 | Tier 2 | 2018-06-26 | 2003-08-24 | Equipment | 534 |  | POTHEAD | P211167 | P211167 | 0 | 2018 | 2003
030827E5057 | 1030-F | Before | 6.3726 | 16.6384 | 1 | Tier 3 | 2017-08-18 | 2003-08-27 | Customer Contact | 710 | 532 | POLE | P112233 | P112233 | 0 | 2017 | 2003
030827E5057 | 1030-J | Before | 6.1123 | 16.8986 | 1 | Tier 3 | 2017-11-21 | 2003-08-27 | Customer Contact | 710 | 532 | POLE | P112233 | P112233 | 0 | 2017 | 2003
030902E5072 | 0078-D | Before | 6.3397 | 16.6712 | 2 | Tier 3 | 2017-08-30 | 2003-09-02 | Weather | 410 |  | JUMPER | P172678 | P172678 | 0 | 2017 | 2003
030904E5033 | 0212-B | Before | 4.0137 | 18.9973 | 3 | Tier 3 | 2019-12-27 | 2003-09-04 | Weather | 410 | 520 | FUSE | P19533 | P19533 | 0 | 2019 | 2003
031104E7101 | 0221-F | Before | 5.5945 | 17.4164 | 1 | Tier 3 | 2018-05-29 | 2003-11-04 | Miscellaneous | 206 | 532 | POLE | P713311 | P713311 | 0 | 2018 | 2003
031105E5027 | 1030-C | Before | 6.6521 | 16.3589 | 2 | Tier 3 | 2017-05-08 | 2003-11-05 | Customer Contact | 710 | 532 | POLE | P112347 | P112347 | 0 | 2017 | 2003
031119E5045 | 448CCC CC | Before | 1.4466 | 21.5644 | 1 | Tier 3 | 2022-07-21 | 2003-11-19 | Foreign Object | 308 | 510 | OH CONDUCTOR | P43126 | P43126 | 0 | 2022 | 2003
031226E5126 | 0222-Z | Before | 6.6438 | 16.3671 | 4 | Tier 3 | 2017-05-11 | 2003-12-26 | Miscellaneous | 206 | 532 | POLE | P17854 | P17854 | 0 | 2017 | 2003
031226E7704 | 0222-Z | Before | 6.6438 | 16.3671 | 4 | Tier 3 | 2017-05-11 | 2003-12-26 | Equipment | 532 |  | POLE | P17854 | P17854 | 0 | 2017 | 2003
040205E7701 | 0974-B | Before | 6.0767 | 16.9342 | 2 | Tier 3 | 2017-12-04 | 2004-02-05 | Customer Contact | 710 | 532 | POLE | P378653 | P378653 | 0 | 2017 | 2004
040401E7803 | 0078-E | Before | 7.7781 | 15.2329 | 2 | Tier 3 | 2016-03-23 | 2004-04-01 | Weather | 412 | 510 | OH CONDUCTOR | P673002 | P673002 | 0 | 2016 | 2004
040713E7601 | 0212-A | Before | 4.0137 | 18.9973 | 2 | Tier 2 | 2019-12-27 | 2004-07-13 | Miscellaneous | 206 | 532 | POLE | P19585 | P19585 | 0 | 2019 | 2004
040813E7706 | C237 PH 2 M RECONDUCTOR | Before | 8.3479 | 14.663 | 1 | Tier 3 | 2015-08-28 | 2004-08-13 | Weather | 410 | 550 | TRANSFORMER | P215620 | P215620 | 0 | 2015 | 2004
040822E5005 | 0971-E | Before | 6.8164 | 16.1945 | 1 | Tier 2 | 2017-03-09 | 2004-08-22 | Foreign Object | 308 | 510 | OH CONDUCTOR | P117511 | P117511 | 0 | 2017 | 2004
040822E5005 | 0971-E | Before | 6.8164 | 16.1945 | 1 | Tier 3 | 2017-03-09 | 2004-08-22 | Foreign Object | 308 | 510 | OH CONDUCTOR | P117511 | P117511 | 0 | 2017 | 2004
041020E5090 | C973 PH 2 #A RECOND | Before | 8.4877 | 14.5233 | 2 | Tier 3 | 2015-07-08 | 2004-10-20 | Weather | 412 | 522 | FUSE | P219920 | P219920 | 0 | 2015 | 2004
041026E7602 | 0175-E | Before | 7.1836 | 15.8274 | 1 | Tier 3 | 2016-10-26 | 2004-10-26 | Customer Contact | 710 | 532 | POLE | P710852 | P710852 | 0 | 2016 | 2004
041027E5012 | 0230-D | Before | 4.9342 | 18.0767 | 2 | Tier 2 | 2019-01-25 | 2004-10-27 | Weather | 426 | 513 | OH CONDUCTOR | P114200 | P114200 | 0 | 2019 | 2004
041101E5103 | 0078-E | Before | 7.7781 | 15.2329 | 1 | Tier 3 | 2016-03-23 | 2004-11-01 | Equipment | 554 |  | CROSSARM | P172724 | P172724 | 0 | 2016 | 2004
041210E7702 | PE1 PH 4#C POLE CHGOUT/RE | Before | 8.7315 | 14.2795 | 2 | Tier 3 | 2015-04-10 | 2004-12-10 | Equipment | 554 |  | CROSSARM | P310033 | P310033 | 0 | 2015 | 2004
041217E7102 | C442 PH 4 BPOLE CHGOUT R1 | Before | 8.7342 | 14.2767 | 2 | Tier 3 | 2015-04-09 | 2004-12-17 | Weather | 412 | 515 | JUMPER | P178017 | P178017 | 0 | 2015 | 2004
050224E7601 | 0237-C | Before | 7.4658 | 15.5452 | 2 | Tier 3 | 2016-07-15 | 2005-02-24 | Weather | 410 | 518 | CUTOUT | P17664 | P17664 | 0 | 2016 | 2005
050225E5102 | 0215-A | Before | 5.5178 | 17.4932 | 3 | Tier 2 | 2018-06-26 | 2005-02-25 | Customer Contact | 710 | 515 | JUMPER | P211169 | P211169 | 0 | 2018 | 2005
050312E7102 | 0175-C | Before | 6.7589 | 16.2521 | 2 | Tier 3 | 2017-03-30 | 2005-03-12 | Foreign Object | 314 |  | FUSE | P815212 | P815212 | 0 | 2017 | 2005
050317E7101 | 0212-B | Before | 4.0137 | 18.9973 | 2 | Tier 3 | 2019-12-27 | 2005-03-17 | Foreign Object | 308 | 510 | OH CONDUCTOR | P19529 | P19529 | 0 | 2019 | 2005
050319E5003 | 0079-A | Before | 7.789 | 15.2219 | 1 | Tier 3 | 2016-03-19 | 2005-03-19 | Equipment | 532 |  | POLE | P774744 | P774744 | 0 | 2016 | 2005
050328E5056 | 0212-U | Before | 2.5534 | 20.4575 | 1 | Tier 2 | 2021-06-12 | 2005-03-28 | Equipment | 518 |  | SWITCH | P218009 | P218009 | 0 | 2021 | 2005
050328E5056 | 0212-V | Before | 3.6849 | 19.326 | 2 | Tier 2 | 2020-04-25 | 2005-03-28 | Equipment | 518 |  | SWITCH | P218009 | P218009 | 0 | 2020 | 2005
050507E5001 | 0222-FF | Before | 1.7452 | 21.2658 | 2 | Tier 3 | 2022-04-03 | 2005-05-07 | Customer Contact | 710 | 532 | POLE | P412779 | P412779 | 0 | 2022 | 2005
050515E5001 | 1030-F | Before | 6.3726 | 16.6384 | 2 | Tier 3 | 2017-08-18 | 2005-05-15 | Customer Contact | 710 | 532 | POLE | P212424 | P212424 | 0 | 2017 | 2005
050614E5033 | 0971-E | Before | 6.8164 | 16.1945 | 1 | Tier 2 | 2017-03-09 | 2005-06-14 | Customer Contact | 702 | 532 | POLE | P117511 | P117511 | 0 | 2017 | 2005
050614E5033 | 0971-E | Before | 6.8164 | 16.1945 | 1 | Tier 3 | 2017-03-09 | 2005-06-14 | Customer Contact | 702 | 532 | POLE | P117511 | P117511 | 0 | 2017 | 2005
050703E5025 | 0908-F | Before | 3.3589 | 19.6521 | 2 | Tier 2 | 2020-08-22 | 2005-07-03 | Tree Contact | 322 | 510 | OH CONDUCTOR | P412314 | P412314 | 0 | 2020 | 2005
050712E7601 | C237 PH 2 E RECONDUCTOR | Before | 8.5315 | 14.4795 | 2 | Tier 3 | 2015-06-22 | 2005-07-12 | Equipment | 554 | 214 | CROSSARM | P412285 | P412285 | 0 | 2015 | 2005
050725E7103 | C220 PH 2 O RECONDUCTOR | Before | 8.1288 | 14.8822 | 2 | Tier 3 | 2015-11-16 | 2005-07-25 | Equipment | 532 | 214 | POLE | P310513 | P310513 | 0 | 2015 | 2005
050811E7109 | 0220-N | Before | 7.1836 | 15.8274 | 2 | Tier 3 | 2016-10-26 | 2005-08-11 | Equipment | 518 |  | CUTOUT | P18010 | P18010 | 0 | 2016 | 2005
050811E7109 | 0220-Q | Before | 6.6685 | 16.3425 | 1 | Tier 3 | 2017-05-02 | 2005-08-11 | Equipment | 518 |  | CUTOUT | P18010 | P18010 | 0 | 2017 | 2005
050825E7601 | 0176-J | Before | 6.6274 | 16.3836 | 1 | Tier 3 | 2017-05-17 | 2005-08-25 | Equipment | 554 |  | CROSSARM | P211064 | P211064 | 0 | 2017 | 2005
050827E5058 | 0222-K | Before | 7.4658 | 15.5452 | 2 | Tier 3 | 2016-07-15 | 2005-08-27 | Customer Contact | 710 | 510 | POLE | P17696 | P17696 | 0 | 2016 | 2005
050827E5058 | C222 PH 1 I RECONDUC R7 | Before | 8.389 | 14.6219 | 1 | Tier 3 | 2015-08-13 | 2005-08-27 | Customer Contact | 710 | 510 | POLE | P17696 | P17696 | 0 | 2015 | 2005
050829E5002 | 0222-R | Before | 7.7315 | 15.2795 | 2 | Tier 3 | 2016-04-09 | 2005-08-29 | Customer Contact | 710 | 532 | POLE | P513476 | P513476 | 0 | 2016 | 2005
050907E5020 | 0445-R | Before | 2.0164 | 20.9945 | 2 | Tier 2 | 2021-12-25 | 2005-09-07 | Customer Contact | 710 | 532 | POLE | P41351 | P41351 | 0 | 2021 | 2005
050914E5018 | 0175-B | Before | 6.7041 | 16.3068 | 1 | Tier 2 | 2017-04-19 | 2005-09-14 | Equipment | 515 |  | CONNECTOR | Z16573 | Z16573 | 0 | 2017 | 2005
050914E7104 | 0175-B | Before | 6.7041 | 16.3068 | 1 | Tier 2 | 2017-04-19 | 2005-09-14 | Equipment | 515 |  | CONNECTOR | Z16573 | Z16573 | 0 | 2017 | 2005
050920E7605 | 0220-K | Before | 7.2219 | 15.789 | 1 | Tier 3 | 2016-10-12 | 2005-09-20 | Weather | 404 | 518 | CUTOUT | P212271 | P212271 | 0 | 2016 | 2005
050920E7605 | C220 PH 2 I RECONDUCT R8 | Before | 8.3397 | 14.6712 | 2 | Tier 3 | 2015-08-31 | 2005-09-20 | Weather | 404 | 518 | CUTOUT | P212271 | P212271 | 0 | 2015 | 2005
051004E5032 | C442 PH 4 GPOLE CHGOUT R1 | Before | 8.0712 | 14.9397 | 2 | Tier 3 | 2015-12-07 | 2005-10-04 | Foreign Object | 304 | 534 | POTHEAD | P173190 | P173190 | 0 | 2015 | 2005
051106E7103 | 0971-A | Before | 6.6027 | 16.4082 | 2 | Tier 3 | 2017-05-26 | 2005-11-06 | Customer Contact | 710 | 532 | POLE | P319998 | P319998 | 0 | 2017 | 2005
051110E7602 | 0220-N | Before | 7.1836 | 15.8274 | 2 | Tier 3 | 2016-10-26 | 2005-11-10 | Equipment | 518 |  | CUTOUT | P18010 | P18010 | 0 | 2016 | 2005
051110E7602 | 0220-Q | Before | 6.6685 | 16.3425 | 1 | Tier 3 | 2017-05-02 | 2005-11-10 | Equipment | 518 |  | CUTOUT | P18010 | P18010 | 0 | 2017 | 2005
051113E7101 | C239:2013 RIRAT RELIABILITY | Before | 8.4356 | 14.5753 | 1 | Tier 3 | 2015-07-27 | 2005-11-13 | Customer Contact | 710 | 532 | POLE | P319768 | P319768 | 0 | 2015 | 2005
060123E5034 | C445 2012 CFSP WS BRANCH R1 | Before | 8.0329 | 14.9781 | 2 | Tier 2 | 2015-12-21 | 2006-01-23 | Equipment | 513 |  | OH CONDUCTOR | P41589 | P41589 | 0 | 2015 | 2006
060126E7601 | C237 PH 2 J RECONDUCTOR | Before | 8.4329 | 14.5781 | 2 | Tier 3 | 2015-07-28 | 2006-01-26 | Customer Contact | 710 | 532 | POLE | P212975 | P212975 | 0 | 2015 | 2006
060228E5009 | 0212-C-PH-02 | Before | 3.0904 | 19.9205 | 2 | Tier 3 | 2020-11-28 | 2006-02-28 | Foreign Object | 308 | 510 | OH CONDUCTOR | P112481 | P112481 | 0 | 2020 | 2006
060322E5031 | 0230-J | Before | 0.89315 | 22.1178 | 2 | Tier 2 | 2023-02-08 | 2006-03-22 | Tree Contact | 318 | 510 | OH CONDUCTOR | P210305 | P210305 | 0 | 2023 | 2006
060715E5011 | 0520-F | Before | 5.4384 | 17.5726 | 2 | Tier 2 | 2018-07-25 | 2006-07-15 | Equipment | 520 |  | FUSE | P512483 | P512483 | 0 | 2018 | 2006
060905E5038 | C233 LONG SPAN EVAL P61 R18 | Before | 9.0301 | 13.9808 | 1 | Tier 2 | 2014-12-22 | 2006-09-05 | Equipment | 515 |  | JUMPER | P610466 | P610466 | 0 | 2014 | 2006
061020E5005 | CNF-TL629A | Before | 3.2849 | 19.726 | 2 | Tier 3 | 2020-09-18 | 2006-10-20 | Equipment | 518 |  | CUTOUT | Z173131 | Z173131 | 0 | 2020 | 2006
061020E5005 | CNF-TL629A | Before | 3.2849 | 19.726 | 2 | Tier 3 | 2020-09-18 | 2006-10-20 | Equipment | 518 |  | CUTOUT | Z173131 | Z173131 | 0 | 2020 | 2006
061031E7703 | 0974-C | Before | 6.2274 | 16.7836 | 2 | Tier 3 | 2017-10-10 | 2006-10-31 | Customer Contact | 710 | 532 | POLE | P378632 | P378632 | 0 | 2017 | 2006
061203E5024 | 0222-Y | Before | 7.1178 | 15.8932 | 4 | Tier 3 | 2016-11-19 | 2006-12-03 | Equipment | 515 | 513 | JUMPER | P17833 | P17833 | 0 | 2016 | 2006
061228E5004 | 0212-C-PH-02 | Before | 3.0904 | 19.9205 | 2 | Tier 3 | 2020-11-28 | 2006-12-28 | Foreign Object | 308 | 510 | OH CONDUCTOR | P112479 | P112479 | 0 | 2020 | 2006
070111E7601 | C67,BAR:LG SPAN/DESIMIL R3 | Before | 9.3699 | 13.6411 | 2 | Tier 3 | 2014-08-20 | 2007-01-12 | Equipment | 530 | 532 | INSULATOR | P372221 | P372221 | 0 | 2014 | 2007
070125E5001 | 0176-C | Before | 6.8932 | 16.1178 | 2 | Tier 3 | 2017-02-09 | 2007-01-25 | Equipment | 520 |  | FUSE | P218274 | P218274 | 0 | 2017 | 2007
070207E7801 | 0221-S | Before | 5.3342 | 17.6767 | 2 | Tier 3 | 2018-09-01 | 2007-02-07 | Customer Contact | 710 | 532 | POLE | P110886 | P110886 | 0 | 2018 | 2007
070311E5023 | C442 PH 4 GPOLE CHGOUT R1 | Before | 8.0712 | 14.9397 | 2 | Tier 3 | 2015-12-07 | 2007-03-11 | Foreign Object | 304 | 534 | POTHEAD | P173190 | P173190 | 0 | 2015 | 2007
070313E7802 | C222 PH4 SEC2 CPOLE CHGOU | Before | 8.6767 | 14.3342 | 2 | Tier 3 | 2015-04-30 | 2007-03-13 | Equipment | 554 | 214 | CROSSARM | P111080 | P111080 | 0 | 2015 | 2007
070329E5034 | 0157-G | Before | 2.5726 | 20.4384 | 2 | Tier 3 | 2021-06-05 | 2007-03-29 | Equipment | 502 |  | LIGHTNING ARRESTER | P175982 | P175982 | 0 | 2021 | 2007
070516E7801 | C237 PH 2 D RECONDUCT R1 | Before | 8.4329 | 14.5781 | 2 | Tier 3 | 2015-07-28 | 2007-05-16 | Equipment | 554 | 214 | CROSSARM | P17608 | P17608 | 0 | 2015 | 2007
070518E5048 | 0350-E | Before | 4.4192 | 18.5918 | 2 | Tier 2 | 2019-08-01 | 2007-05-18 | Equipment | 515 |  | CONNECTOR | P213206 | P213206 | 0 | 2019 | 2007
070621E5004 | 1030-O | Before | 6.6521 | 16.3589 | 1 | Tier 3 | 2017-05-08 | 2007-06-21 | Foreign Object | 308 | 532 | POLE | P813145 | P813145 | 0 | 2017 | 2007
070729E5015 | 0217-D | Before | 4.0356 | 18.9753 | 3 | Tier 3 | 2019-12-19 | 2007-07-29 | Customer Contact | 710 | 532 | POLE | P217465 | P217465 | 0 | 2019 | 2007
070809E7802 | 0222-FF | Before | 1.7452 | 21.2658 | 2 | Tier 3 | 2022-04-03 | 2007-08-09 | Customer Contact | 710 | 532 | POLE | P412779 | P412779 | 0 | 2022 | 2007
070816E7701 | 0230-D | Before | 4.9342 | 18.0767 | 2 | Tier 2 | 2019-01-25 | 2007-08-16 | Customer Contact | 710 | 532 | POLE | P17079 | P17079 | 0 | 2019 | 2007
070825E5039 | 1030-L | Before | 6.7781 | 16.2329 | 2 | Tier 3 | 2017-03-23 | 2007-08-25 | Foreign Object | 314 | 510 | OH CONDUCTOR | P615314 | P615314 | 0 | 2017 | 2007
070825E5039 | 1030-Q | Before | 6.5507 | 16.4603 | 1 | Tier 3 | 2017-06-14 | 2007-08-25 | Foreign Object | 314 | 510 | OH CONDUCTOR | P615314 | P615314 | 0 | 2017 | 2007
070901E5077 | 0212-B | Before | 4.0137 | 18.9973 | 3 | Tier 3 | 2019-12-27 | 2007-09-01 | Equipment | 522 |  | FUSE | P19533 | P19533 | 0 | 2019 | 2007
070901E5099 | 0520-L | Before | 5.5671 | 17.4438 | 2 | Tier 2 | 2018-06-08 | 2007-09-01 | Equipment | 522 |  | FUSE | P30973 | P30973 | 0 | 2018 | 2007
070901E5220 | CNF-TL629A | Before | 3.2849 | 19.726 | 1 | Tier 3 | 2020-09-18 | 2007-09-01 | Weather | 410 | 518 | CUTOUT | Z178329 | Z178329 | 0 | 2020 | 2007
070911E5020 | 0217-E | Before | 4.0356 | 18.9753 | 2 | Tier 3 | 2019-12-19 | 2007-09-11 | Equipment | 518 |  | CUTOUT | P214799 | P214799 | 0 | 2019 | 2007
071021E5099 | 0445-N | Before | 4.6274 | 18.3836 | 2 | Tier 2 | 2019-05-17 | 2007-10-21 | Weather | 412 | 510 | OH CONDUCTOR | P41222 | P41222 | 0 | 2019 | 2007
071022E5009 | 1030-B | Before | 7.4521 | 15.5589 | 2 | Tier 3 | 2016-07-20 | 2007-10-22 | Weather | 404 | 532 | POLE | P613213 | P613213 | 0 | 2016 | 2007
071022E5038 | C441 BRLINE CFSP W/S(P1 R1 | Before | 8.0849 | 14.926 | 1 | Tier 3 | 2015-12-02 | 2007-10-22 | Weather | 412 | 513 | OH CONDUCTOR | P40884 | P40884 | 0 | 2015 | 2007
071022E7806 | 0230-F | Before | 5.4219 | 17.589 | 2 | Tier 2 | 2018-07-31 | 2007-10-22 | Miscellaneous | 206 | 520 | FUSE | P318812 | P318812 | 0 | 2018 | 2007
071023E7508 | 0236-B | Before | 7.2027 | 15.8082 | 2 | Tier 3 | 2016-10-19 | 2007-10-23 | Miscellaneous | 206 | 532 | POLE | P711836 | P711836 | 0 | 2016 | 2007
071123E5001 | 0974-C | Before | 6.2274 | 16.7836 | 2 | Tier 3 | 2017-10-10 | 2007-11-23 | Customer Contact | 710 | 532 | POLE | P378630 | P378630 | 0 | 2017 | 2007
071130E5007 | 0212-P | Before | 3.1096 | 19.9014 | 2 | Tier 2 | 2020-11-21 | 2007-11-30 | Equipment | 554 |  | CROSSARM | P210177 | P210177 | 0 | 2020 | 2007
080212E7701 | 0222-FF | Before | 1.7452 | 21.2658 | 2 | Tier 3 | 2022-04-03 | 2008-02-12 | Customer Contact | 710 | 532 | POLE | P416132 | P416132 | 0 | 2022 | 2008
080212E7702 | 0222-FF | Before | 1.7452 | 21.2658 | 2 | Tier 3 | 2022-04-03 | 2008-02-12 | Customer Contact | 710 | 532 | POLE | P416132 | P416132 | 0 | 2022 | 2008
080303E5003 | 0222-X | Before | 7.1671 | 15.8438 | 4 | Tier 3 | 2016-11-01 | 2008-03-03 | Equipment | 530 | 513 | INSULATOR | P17806 | P17806 | 0 | 2016 | 2008
080309E7701 | 1030-C | Before | 6.6521 | 16.3589 | 1 | Tier 3 | 2017-05-08 | 2008-03-09 | Foreign Object | 314 | 510 | OH CONDUCTOR | P112214 | P112214 | 0 | 2017 | 2008
080320E7802 | 1030-M | Before | 6.9753 | 16.0356 | 1 | Tier 3 | 2017-01-10 | 2008-03-20 | Customer Contact | 702 | 526 | GUY WIRE | P215484 | P215484 | 0 | 2017 | 2008
080522E7801 | 0237-G | Before | 5.8384 | 17.1726 | 1 | Tier 3 | 2018-03-01 | 2008-05-22 | Weather | 410 | 534 | POTHEAD | P616310 | P616310 | 0 | 2018 | 2008
080606E7701 | 0971-F | Before | 5.8384 | 17.1726 | 2 | Tier 3 | 2018-03-01 | 2008-06-06 | Foreign Object | 308 | 515 | JUMPER | P116816 | P116816 | 0 | 2018 | 2008
080620E7702 | 0212-C-PH-02 | Before | 3.0904 | 19.9205 | 2 | Tier 3 | 2020-11-28 | 2008-06-20 | Equipment | 513 | 214 | OH CONDUCTOR | P112482 | P112482 | 0 | 2020 | 2008
080622E5002 | 0230-B | Before | 4.9753 | 18.0356 | 1 | Tier 2 | 2019-01-10 | 2008-06-22 | Customer Contact | 710 | 532 | POLE | P18310 | P18310 | 0 | 2019 | 2008
080706E7801 | 0182-COUNTRY_CLUB | Before | 2.4247 | 20.5863 | 1 | Tier 2 | 2021-07-29 | 2008-07-06 | Equipment | 515 | 513 | CONNECTOR | P113385 | P113385 | 0 | 2021 | 2008
080709E7602 | 0445-R | Before | 2.0164 | 20.9945 | 3 | Tier 2 | 2021-12-25 | 2008-07-09 | Equipment | 515 |  | JUMPER | P41340 | P41340 | 0 | 2021 | 2008
080904E7601 | 0974-B | Before | 6.0767 | 16.9342 | 2 | Tier 3 | 2017-12-04 | 2008-09-04 | Customer Contact | 710 | 532 | POLE | P378647 | P378647 | 0 | 2017 | 2008
080917E7802 | 0221-A | Before | 5.7425 | 17.2685 | 2 | Tier 3 | 2018-04-05 | 2008-09-17 | Equipment | 530 | 554 | CROSSARM | P412637 | P412637 | 0 | 2018 | 2008
081013E7601 | C79 PH4 SEC 2 K POLE R7 | Before | 8.5479 | 14.463 | 2 | Tier 3 | 2015-06-16 | 2008-10-13 | Weather | 426 | 513 | OH CONDUCTOR | P173870 | P173870 | 0 | 2015 | 2008
081020E5006 | 0520-G | Before | 6.4356 | 16.5753 | 2 | Tier 2 | 2017-07-26 | 2008-10-20 | Foreign Object | 308 | 510 | OH CONDUCTOR | P227472 | P227472 | 0 | 2017 | 2008
081104E7701 | 1030-J | Before | 6.1123 | 16.8986 | 2 | Tier 3 | 2017-11-21 | 2008-11-04 | Customer Contact | 710 | 532 | POLE | P816321 | P816321 | 0 | 2017 | 2008
081210E5071 | C222 PH4 SEC2 CPOLE CHGOU | Before | 8.6767 | 14.3342 | 2 | Tier 3 | 2015-04-30 | 2008-12-10 | Equipment | 518 |  | CUTOUT | P211287 | P211287 | 0 | 2015 | 2008
081213E5039 | 0444-A-PH-02 | Before | 2.5534 | 20.4575 | 2 | Tier 2 | 2021-06-12 | 2008-12-13 | Weather | 412 | 532 | POLE | P41776 | P41776 | 0 | 2021 | 2008
081215E5037 | 0237-Q | Before | 7.5836 | 15.4274 | 1 | Tier 2 | 2016-06-02 | 2008-12-15 | Equipment | 510 |  | OH CONDUCTOR | P616240 | P616240 | 0 | 2016 | 2008
090416E5035 | 0908-D | Before | 4.1753 | 18.8356 | 1 | Tier 2 | 2019-10-29 | 2009-04-16 | Customer Contact | 710 | 532 | POLE | P412416 | P412416 | 0 | 2019 | 2009
090416E5035 | 0908-D | Before | 4.1753 | 18.8356 | 2 | Tier 2 | 2019-10-29 | 2009-04-16 | Customer Contact | 710 | 532 | POLE | P412416 | P412416 | 0 | 2019 | 2009
090602E5034 | C73 PH 4 APOLE CHGOUT/ R9 | Before | 8.7918 | 14.2192 | 1 | Tier 3 | 2015-03-19 | 2009-06-02 | Customer Contact | 710 | 532 | POLE | P372539 | P372539 | 0 | 2015 | 2009
090602E7603 | 0157-D | Before | 2.2466 | 20.7644 | 1 | Tier 3 | 2021-10-02 | 2009-06-02 | Foreign Object | 308 | 520 | FUSE | P875813 | P875813 | 0 | 2021 | 2009
090625E5004 | 0520-L | Before | 5.5671 | 17.4438 | 1 | Tier 2 | 2018-06-08 | 2009-06-25 | Equipment | 515 |  | JUMPER | P119035 | P119035 | 0 | 2018 | 2009
090625E5004 | 0520-L | Before | 5.5671 | 17.4438 | 2 | Tier 2 | 2018-06-08 | 2009-06-25 | Equipment | 515 |  | JUMPER | P119035 | P119035 | 0 | 2018 | 2009
090808E5009 | 0972-B | Before | 6.6521 | 16.3589 | 2 | Tier 3 | 2017-05-08 | 2009-08-08 | Foreign Object | 308 | 516 | BUSHING | P216301 | P216301 | 0 | 2017 | 2009
091019E7702 | 0175-B | Before | 6.7041 | 16.3068 | 1 | Tier 2 | 2017-04-19 | 2009-10-19 | Crew Contact | 632 | 515 | JUMPER | P227903 | P227903 | 0 | 2017 | 2009
091019E7702 | 0175-B | Before | 6.7041 | 16.3068 | 1 | Tier 3 | 2017-04-19 | 2009-10-19 | Crew Contact | 632 | 515 | JUMPER | P227903 | P227903 | 0 | 2017 | 2009
091021E5068 | 0974-C | Before | 6.2274 | 16.7836 | 2 | Tier 3 | 2017-10-10 | 2009-10-21 | Customer Contact | 710 | 520 | FUSE | P378634 | P378634 | 0 | 2017 | 2009
091029E5131 | 0157-W | Before | 3.8384 | 19.1726 | 2 | Tier 3 | 2020-02-29 | 2009-10-29 | Customer Contact | 710 | 526 | GUY WIRE | P474547 | P474547 | 0 | 2020 | 2009
091113E7601 | 0157-V | Before | 2.8027 | 20.2082 | 4 | Tier 3 | 2021-03-13 | 2009-11-13 | Equipment | 532 | 206 | POLE | P271560 | P271560 | 0 | 2021 | 2009
091130E7801 | 0212-B | Before | 4.0137 | 18.9973 | 2 | Tier 3 | 2019-12-27 | 2009-11-30 | Foreign Object | 308 | 510 | OH CONDUCTOR | P19529 | P19529 | 0 | 2019 | 2009
091207E5191 | 0215-A | Before | 5.5178 | 17.4932 | 2 | Tier 2 | 2018-06-26 | 2009-12-07 | Weather | 426 | 510 | OH CONDUCTOR | P211170 | P211170 | 0 | 2018 | 2009
091230E7801 | 0212-B | Before | 4.0137 | 18.9973 | 2 | Tier 3 | 2019-12-27 | 2009-12-30 | Foreign Object | 308 | 510 | OH CONDUCTOR | P19529 | P19529 | 0 | 2019 | 2009
100119E5323 | C240 PH 2 E RECONDUCT R1 | Before | 8.0685 | 14.9425 | 2 | Tier 3 | 2015-12-08 | 2010-01-19 | Weather | 412 | 532 | POLE | P176372 | P176372 | 0 | 2015 | 2010
100119E7502 | 0222-AA | Before | 6.4164 | 16.5945 | 1 | Tier 3 | 2017-08-02 | 2010-01-19 | Weather | 404 | 518 | CUTOUT | P316929 | P316929 | 0 | 2017 | 2010
100119E7502 | C222 PH 2 #T RECONDU R11 | Before | 8.1562 | 14.8548 | 1 | Tier 3 | 2015-11-06 | 2010-01-19 | Weather | 404 | 518 | CUTOUT | P316929 | P316929 | 0 | 2015 | 2010
100121E5283 | 0222-AA | Before | 6.4164 | 16.5945 | 1 | Tier 3 | 2017-08-02 | 2010-01-21 | Weather | 408 | 518 | CUTOUT | P316929 | P316929 | 0 | 2017 | 2010
100121E5283 | C222 PH 2 #T RECONDU R11 | Before | 8.1562 | 14.8548 | 1 | Tier 3 | 2015-11-06 | 2010-01-21 | Weather | 408 | 518 | CUTOUT | P316929 | P316929 | 0 | 2015 | 2010
100121E7808 | 0220-K | Before | 7.2219 | 15.789 | 1 | Tier 3 | 2016-10-12 | 2010-01-21 | Weather | 408 | 532 | POLE | P212271 | P212271 | 0 | 2016 | 2010
100121E7808 | C220 PH 2 I RECONDUCT R8 | Before | 8.3397 | 14.6712 | 2 | Tier 3 | 2015-08-31 | 2010-01-21 | Weather | 408 | 532 | POLE | P212271 | P212271 | 0 | 2015 | 2010
100307E5034 | C444 BRANCHLN CFSP P4 R1 | Before | 8.0493 | 14.9616 | 2 | Tier 2 | 2015-12-15 | 2010-03-07 | Customer Contact | 710 | 532 | POLE | P108912 | P108912 | 0 | 2015 | 2010
100312E5005 | 0971-Q | Before | 2.074 | 20.937 | 1 | Tier 3 | 2021-12-04 | 2010-03-12 | Equipment | 515 |  | JUMPER | P210705 | P210705 | 0 | 2021 | 2010
100314E5034 | 0520-H | Before | 5.8767 | 17.1342 | 2 | Tier 2 | 2018-02-15 | 2010-03-14 | Customer Contact | 710 | 532 | POLE | P216053 | P216053 | 0 | 2018 | 2010
100317E7801 | 0217-B | Before | 5.3644 | 17.6466 | 1 | Tier 2 | 2018-08-21 | 2010-03-17 | Foreign Object | 304 | 502 | LIGHTNING ARRESTER | P513018 | P513018 | 0 | 2018 | 2010
100404E5016 | 0520-L | Before | 5.5671 | 17.4438 | 1 | Tier 2 | 2018-06-08 | 2010-04-04 | Equipment | 520 |  | FUSE | P119038 | P119038 | 0 | 2018 | 2010
100515E7801 | 0908-I | Before | 3.589 | 19.4219 | 1 | Tier 2 | 2020-05-30 | 2010-05-15 | Foreign Object | 302 | 532 | POLE | P318834 | P318834 | 0 | 2020 | 2010
100531E7401 | 0157-T | Before | 4.0548 | 18.9562 | 1 | Tier 3 | 2019-12-12 | 2010-05-31 | Foreign Object | 315 | 510 | OH CONDUCTOR | P475949 | P475949 | 0 | 2019 | 2010
100603E7701 | 1030-E | Before | 6.1233 | 16.8877 | 1 | Tier 3 | 2017-11-17 | 2010-06-03 | Foreign Object | 304 | 520 | FUSE | P511082 | P511082 | 0 | 2017 | 2010
100715E5064 | CNF-TL629A | Before | 3.2849 | 19.726 | 1 | Tier 3 | 2020-09-18 | 2010-07-15 | Weather | 410 | 502 | LIGHTNING ARRESTER | Z178329 | Z178329 | 0 | 2020 | 2010
100718E5051 | 0971-A | Before | 6.6027 | 16.4082 | 1 | Tier 2 | 2017-05-26 | 2010-07-18 | Equipment | 520 |  | FUSE | P717097 | P717097 | 0 | 2017 | 2010
100904E5053 | 0217-F | Before | 5.6329 | 17.3781 | 1 | Tier 3 | 2018-05-15 | 2010-09-04 | Equipment | 513 |  | OH CONDUCTOR | P513062 | P513062 | 0 | 2018 | 2010
100923E9901 | C236 PH 2 D RECONDUCTOR | Before | 7.5288 | 15.4822 | 1 | Tier 2 | 2016-06-22 | 2010-09-23 | Customer Contact | 710 | 532 | POLE | P513188 | P513188 | 0 | 2016 | 2010
100923E9901 | C236 PH 2 D RECONDUCTOR | Before | 7.5288 | 15.4822 | 1 | Tier 3 | 2016-06-22 | 2010-09-23 | Customer Contact | 710 | 532 | POLE | P513188 | P513188 | 0 | 2016 | 2010
101020E5143 | C973 PH 2 #A RECOND | Before | 8.4877 | 14.5233 | 2 | Tier 3 | 2015-07-08 | 2010-10-20 | Equipment | 515 | 532 | JUMPER | P219920 | P219920 | 0 | 2015 | 2010
101021E7811 | C221:ERI 2012 REBUILD | Before | 8.3452 | 14.6658 | 1 | Tier 3 | 2015-08-29 | 2010-10-21 | Customer Contact | 710 | 532 | POLE | P17895 | P17895 | 0 | 2015 | 2010
101022E7801 | C221:ERI 2012 REBUILD | Before | 8.3452 | 14.6658 | 1 | Tier 3 | 2015-08-29 | 2010-10-22 | Miscellaneous | 222 |  | POLE | P17895 | P17895 | 0 | 2015 | 2010
101022E7802 | C221:ERI 2012 REBUILD | Before | 8.3452 | 14.6658 | 1 | Tier 3 | 2015-08-29 | 2010-10-22 | Customer Contact | 710 | 532 | POLE | P17895 | P17895 | 0 | 2015 | 2010
101025E7201 | 0240-D | Before | 7.4521 | 15.5589 | 2 | Tier 3 | 2016-07-20 | 2010-10-25 | Equipment | 554 | 214 | CROSSARM | P777237 | P777237 | 0 | 2016 | 2010
101108E5008 | C79 PH4 SEC 2 E POLE R1 | Before | 8.589 | 14.4219 | 2 | Tier 3 | 2015-06-01 | 2010-11-08 | Equipment | 516 | 554 | BUSHING | P476493 | P476493 | 0 | 2015 | 2010
101220E5162 | 0350-F | Before | 4.2329 | 18.7781 | 1 | Tier 2 | 2019-10-08 | 2010-12-20 | Weather | 408 | 554 | CROSSARM | P517812 | P517812 | 0 | 2019 | 2010
110113E9901 | 0217-N | Before | 4.9068 | 18.1041 | 4 | Tier 2 | 2019-02-04 | 2011-01-13 | Crew Contact | 612 | 510 | OH CONDUCTOR | P214138 | P214138 | 0 | 2019 | 2011
110115E7802 | 1030-J | Before | 6.1123 | 16.8986 | 2 | Tier 3 | 2017-11-21 | 2011-01-15 | Customer Contact | 710 | 532 | POLE | P417818 | P417818 | 0 | 2017 | 2011
110125E9901 | 0971-G | Before | 6.7096 | 16.3014 | 2 | Tier 3 | 2017-04-17 | 2011-01-25 | Customer Contact | 710 | 532 | POLE | P112171 | P112171 | 0 | 2017 | 2011
110214E7801 | 1030-L | Before | 6.7781 | 16.2329 | 2 | Tier 3 | 2017-03-23 | 2011-02-14 | Equipment | 513 |  | OH CONDUCTOR | P615314 | P615314 | 0 | 2017 | 2011
110214E7801 | 1030-Q | Before | 6.5507 | 16.4603 | 1 | Tier 3 | 2017-06-14 | 2011-02-14 | Equipment | 513 |  | OH CONDUCTOR | P615314 | P615314 | 0 | 2017 | 2011
110219E7802 | 0217-C | Before | 5.8384 | 17.1726 | 2 | Tier 3 | 2018-03-01 | 2011-02-19 | Weather | 410 | 532 | POLE | P214788 | P214788 | 0 | 2018 | 2011
110309E5084 | 0350-I | Before | 5.3178 | 17.6932 | 2 | Tier 2 | 2018-09-07 | 2011-03-09 | Equipment | 513 | 214 | OH CONDUCTOR | P514507 | P514507 | 0 | 2018 | 2011
110526E7603 | 0445-G | Before | 5.5808 | 17.4301 | 1 | Tier 2 | 2018-06-03 | 2011-05-26 | Equipment | 515 | 214 | JUMPER | P138803 | P138803 | 0 | 2018 | 2011
110531E5030 | 1030-U | Before | 6.1233 | 16.8877 | 2 | Tier 2 | 2017-11-17 | 2011-05-31 | Equipment | 520 |  | FUSE | P511470 | P511470 | 0 | 2017 | 2011
110706E7602 | C79 FIRE RISK MITIGATION R2 | Before | 8.4658 | 14.5452 | 2 | Tier 3 | 2015-07-16 | 2011-07-06 | Equipment | 554 | 532 | CROSSARM | P275369 | P275369 | 0 | 2015 | 2011
110730E7602 | 1030-O | Before | 6.6521 | 16.3589 | 3 | Tier 3 | 2017-05-08 | 2011-07-30 | Foreign Object | 308 | 532 | POLE | P513923 | P513923 | 0 | 2017 | 2011
110807E7601 | C78 PH4 BPOLE CHGOUT/R R8 | Before | 8.7781 | 14.2329 | 2 | Tier 3 | 2015-03-24 | 2011-08-07 | Customer Contact | 710 | 532 | POLE | P572043 | P572043 | 0 | 2015 | 2011
110915E5086 | 0212-W-FT-02 | Before | 3.6877 | 19.3233 | 1 | Tier 2 | 2020-04-24 | 2011-09-15 | Weather | 410 | 532 | POLE | P310528 | P310528 | 0 | 2020 | 2011
110915E5086 | 0212-X | Before | 2.5151 | 20.4959 | 1 | Tier 2 | 2021-06-26 | 2011-09-15 | Weather | 410 | 532 | POLE | P310528 | P310528 | 0 | 2021 | 2011
111016E9901 | 0212-B | Before | 4.0137 | 18.9973 | 2 | Tier 3 | 2019-12-27 | 2011-10-16 | Foreign Object | 308 | 510 | OH CONDUCTOR | P19522 | P19522 | 0 | 2019 | 2011
111112E7801 | C1023/C354_NEW_12KV_RECON | Before | 2.0795 | 20.9315 | 2 | Tier 2 | 2021-12-02 | 2011-11-12 | Equipment | 518 |  | CUTOUT | P813837 | P813837 | 0 | 2021 | 2011
111121E5011 | PE1 PH 4 A POLE CHGO R11 | Before | 8.5096 | 14.5014 | 3 | Tier 3 | 2015-06-30 | 2011-11-21 | Foreign Object | 308 | 510 | OH CONDUCTOR | P216435 | P216435 | 0 | 2015 | 2011
111212E9901 | 0157-W | Before | 3.8384 | 19.1726 | 2 | Tier 3 | 2020-02-29 | 2011-12-12 | Customer Contact | 710 | 532 | POLE | P474547 | P474547 | 0 | 2020 | 2011
120125E7601 | C1215 MAINLINE CFSP W/S R1 | Before | 8.6712 | 14.3397 | 2 | Tier 3 | 2015-05-02 | 2012-01-25 | Equipment | 532 | 214 | POLE | P40838 | P40838 | 0 | 2015 | 2012
120227E9906 | C445 2012 CFSP WS BRANCH R1 | Before | 8.0329 | 14.9781 | 2 | Tier 2 | 2015-12-21 | 2012-02-27 | Weather | 412 | 513 | OH CONDUCTOR | P41586 | P41586 | 0 | 2015 | 2012
120314E7801 | 0971-E | Before | 6.8164 | 16.1945 | 1 | Tier 3 | 2017-03-09 | 2012-03-13 | Equipment | 515 |  | JUMPER | P518556 | P518556 | 0 | 2017 | 2012
120318E5033 | 0078-E | Before | 7.7781 | 15.2329 | 1 | Tier 3 | 2016-03-23 | 2012-03-18 | Weather | 412 | 510 | OH CONDUCTOR | P172716 | P172716 | 0 | 2016 | 2012
120319E7605 | 79N | Before | 1.5616 | 21.4493 | 2 | Tier 3 | 2022-06-09 | 2012-03-19 | Weather | 408 | 520 | FUSE | P273555 | P273555 | 0 | 2022 | 2012
120513E9904 | 0908-D | Before | 4.1753 | 18.8356 | 2 | Tier 2 | 2019-10-29 | 2012-05-13 | Equipment | 518 |  | CUTOUT | P115164 | P115164 | 0 | 2019 | 2012
120528E8106 | 0445-N | Before | 4.6274 | 18.3836 | 2 | Tier 2 | 2019-05-17 | 2012-05-28 | Customer Contact | 710 | 532 | POLE | P41243 | P41243 | 0 | 2019 | 2012
120604E8102 | 0221-V | Before | 7.0877 | 15.9233 | 3 | Tier 3 | 2016-11-30 | 2012-06-04 | Equipment | 528 |  | MISC EQUIPMENT | P717419 | P717419 | 0 | 2016 | 2012
120613E5067 | C222 PH4 SEC2 DPOLE CH R1 | Before | 9.0055 | 14.0055 | 2 | Tier 3 | 2014-12-31 | 2012-06-13 | Equipment | 522 |  | FUSE | P114679 | P114679 | 0 | 2014 | 2012
120627E8101 | 0445-O | Before | 3.3397 | 19.6712 | 2 | Tier 2 | 2020-08-29 | 2012-06-27 | Equipment | 532 | 214 | POLE | P41261 | P41261 | 0 | 2020 | 2012
120725E8103 | C222 PH 1 P RECONDUC R7 | Before | 8.589 | 14.4219 | 1 | Tier 3 | 2015-06-01 | 2012-07-25 | Foreign Object | 308 | 502 | LIGHTNING ARRESTER | P419138 | P419138 | 0 | 2015 | 2012
120810E8101 | 1030-U | Before | 6.1233 | 16.8877 | 2 | Tier 2 | 2017-11-17 | 2012-08-10 | Customer Contact | 710 | 532 | POLE | P211295 | P211295 | 0 | 2017 | 2012
120830E5044 | 0157-W | Before | 3.8384 | 19.1726 | 2 | Tier 3 | 2020-02-29 | 2012-08-30 | Customer Contact | 710 | 526 | GUY WIRE | P474547 | P474547 | 0 | 2020 | 2012
120910E5216 | 1030-F | Before | 6.3726 | 16.6384 | 3 | Tier 3 | 2017-08-18 | 2012-09-10 | Weather | 410 | 513 | OH CONDUCTOR | P612957 | P612957 | 0 | 2017 | 2012
121011E3026 | 0358-C | Before | 7.6082 | 15.4027 | 1 | Tier 3 | 2016-05-24 | 2012-10-11 | Equipment | 522 |  | FUSE | P162173 | P162173 | 0 | 2016 | 2012
121107E5250 | 0230-D | Before | 4.9342 | 18.0767 | 1 | Tier 2 | 2019-01-25 | 2012-11-07 | Customer Contact | 710 | 532 | POLE | P416259 | P416259 | 0 | 2019 | 2012
121225E7812 | 0212-B | Before | 4.0137 | 18.9973 | 2 | Tier 3 | 2019-12-27 | 2012-12-25 | Equipment | 513 |  | OH CONDUCTOR | P19517 | P19517 | 0 | 2019 | 2012
130126E9767 | 0240-C | Before | 7.8548 | 15.1562 | 1 | Tier 3 | 2016-02-24 | 2013-01-26 | Equipment | 502 |  | LIGHTNING ARRESTER | P166383 | P166383 | 0 | 2016 | 2013
130201E10180 | CRB1 | Before | 3.0329 | 19.9781 | 2 | Tier 3 | 2020-12-19 | 2013-02-01 | Equipment | 510 |  | OH CONDUCTOR | P17219 | P17219 | 0 | 2020 | 2013
130201E10192 | CRB1 | Before | 3.0329 | 19.9781 | 2 | Tier 3 | 2020-12-19 | 2013-02-01 | Equipment | 510 |  | OH CONDUCTOR | P17219 | P17219 | 0 | 2020 | 2013
130205E10436 | C222 FIRE RISK MITIG PRJPH | Before | 8.8877 | 14.1233 | 2 | Tier 3 | 2015-02-12 | 2013-02-05 | Equipment | 530 | 510 | INSULATOR | P17756 | P17756 | 0 | 2015 | 2013
130224E11602 | 0217-M | Before | 4.8301 | 18.1808 | 1 | Tier 2 | 2019-03-04 | 2013-02-24 | Foreign Object | 312 | 518 | CUTOUT | P310492 | P310492 | 0 | 2019 | 2013
130502E16735 | 0520-F | Before | 5.4384 | 17.5726 | 2 | Tier 2 | 2018-07-25 | 2013-05-02 | Equipment | 532 |  | POLE | P109613 | P109613 | 0 | 2018 | 2013
130506E16797 | 0212-A | Before | 4.0137 | 18.9973 | 2 | Tier 2 | 2019-12-27 | 2013-05-06 | Equipment | 554 |  | CROSSARM | P19587 | P19587 | 0 | 2019 | 2013
130506E17006 | 0212-A | Before | 4.0137 | 18.9973 | 2 | Tier 2 | 2019-12-27 | 2013-05-06 | Equipment | 554 | 214 | CROSSARM | P19587 | P19587 | 0 | 2019 | 2013
130516E17710 | 0212-F | Before | 3.4548 | 19.5562 | 2 | Tier 2 | 2020-07-18 | 2013-05-16 | Equipment | 554 | 214 | CROSSARM | P217019 | P217019 | 0 | 2020 | 2013
130622E20100 | 0175-B | Before | 6.7041 | 16.3068 | 2 | Tier 3 | 2017-04-19 | 2013-06-22 | Foreign Object | 308 | 510 | OH CONDUCTOR | P511105 | P511105 | 0 | 2017 | 2013
130627E20500 | 0212-U | Before | 2.5534 | 20.4575 | 2 | Tier 2 | 2021-06-12 | 2013-06-27 | Equipment | 522 |  | FUSE | P217945 | P217945 | 0 | 2021 | 2013
130804E22850 | 79F | Before | 3.3808 | 19.6301 | 2 | Tier 3 | 2020-08-14 | 2013-08-04 | Equipment | 513 |  | OH CONDUCTOR | P475946 | P475946 | 0 | 2020 | 2013
130901E24800 | C73 PH 4 EPOLE CHGOUT R11 | Before | 8.7041 | 14.3068 | 2 | Tier 3 | 2015-04-20 | 2013-09-01 | Foreign Object | 314 | 520 | FUSE | P275857 | P275857 | 0 | 2015 | 2013
131028E28835 | 0221-A | Before | 5.7425 | 17.2685 | 2 | Tier 3 | 2018-04-05 | 2013-10-28 | Equipment | 502 |  | LIGHTNING ARRESTER | P412623 | P412623 | 0 | 2018 | 2013
131103E29248 | 0212-U | Before | 2.5534 | 20.4575 | 2 | Tier 2 | 2021-06-12 | 2013-11-03 | Equipment | 520 |  | FUSE | P217945 | P217945 | 0 | 2021 | 2013
131111E29747 | 0222-K | Before | 7.4658 | 15.5452 | 2 | Tier 3 | 2016-07-15 | 2013-11-11 | Customer Contact | 710 | 532 | POLE | P17691 | P17691 | 0 | 2016 | 2013
131227E32428 | 0217-Q | Before | 4.5507 | 18.4603 | 2 | Tier 2 | 2019-06-14 | 2013-12-27 | Equipment | 532 | 214 | POLE | P318007 | P318007 | 0 | 2019 | 2013
140125E34233 | 0157-X | Before | 1.6986 | 21.3123 | 1 | Tier 3 | 2022-04-20 | 2014-01-25 | Equipment | 502 |  | LIGHTNING ARRESTER | P572245 | P572245 | 0 | 2022 | 2014
140208E35334 | 0230-D | Before | 4.9342 | 18.0767 | 1 | Tier 2 | 2019-01-25 | 2014-02-08 | Customer Contact | 710 | 532 | POLE | P416259 | P416259 | 0 | 2019 | 2014
140228E36996 | 0215-B | Before | 5.5671 | 17.4438 | 1 | Tier 2 | 2018-06-08 | 2014-02-28 | Equipment | 515 |  | JUMPER | P190447 | P190447 | 0 | 2018 | 2014
140309E37633 | C79 FIRE RISK MITIGATION R2 | Before | 8.4658 | 14.5452 | 2 | Tier 3 | 2015-07-16 | 2014-03-09 | Tree Contact | 322 | 532 | POLE | P275379 | P275379 | 0 | 2015 | 2014
140309E37641 | C79 FIRE RISK MITIGATION R2 | Before | 8.4658 | 14.5452 | 2 | Tier 3 | 2015-07-16 | 2014-03-09 | Tree Contact | 322 | 532 | POLE | P275379 | P275379 | 0 | 2015 | 2014
140429E41740 | 0217-J | Before | 4.5507 | 18.4603 | 2 | Tier 2 | 2019-06-14 | 2014-04-29 | Equipment | 515 |  | JUMPER | P312927 | P312927 | 0 | 2019 | 2014
140430E41750 | CNF-TL629A | Before | 3.2849 | 19.726 | 1 | Tier 3 | 2020-09-18 | 2014-04-30 | Weather | 426 | 510 | OH CONDUCTOR | Z173079 | Z173079 | 0 | 2020 | 2014
140513E42675 | PE1 PH 4 A POLE CHGO R11 | Before | 8.5096 | 14.5014 | 3 | Tier 3 | 2015-06-30 | 2014-05-13 | Equipment | 515 |  | JUMPER | P19715 | P19715 | 0 | 2015 | 2014
140605E44439 | 0971-J | Before | 6.6027 | 16.4082 | 2 | Tier 3 | 2017-05-26 | 2014-06-05 | Foreign Object | 314 | 520 | POLE | P111589 | P111589 | 0 | 2017 | 2014
140627E46005 | 0221-S | Before | 5.3342 | 17.6767 | 2 | Tier 3 | 2018-09-01 | 2014-06-27 | Undetermined | 100 |  |  | P119294 | P119294 | 0 | 2018 | 2014
140702E46429 | 0239.1-A-FT | Before | 2.8877 | 20.1233 | 1 | Tier 3 | 2021-02-10 | 2014-07-02 | Equipment | 512 |  | JUMPER | P213067 | P213067 | 0 | 2021 | 2014
140820E49991 | 0230-E | Before | 5.5699 | 17.4411 | 1 | Tier 2 | 2018-06-07 | 2014-08-20 | Weather | 410 | 502 | LIGHTNING ARRESTER | P610754 | P610754 | 0 | 2018 | 2014
140823E50305 | 0974-B | Before | 6.0767 | 16.9342 | 2 | Tier 3 | 2017-12-04 | 2014-08-23 | Customer Contact | 710 | 532 | POLE | P249955 | P249955 | 0 | 2017 | 2014
140914E51711 | 0215-C | Before | 4.3233 | 18.6877 | 2 | Tier 2 | 2019-09-05 | 2014-09-14 | Weather | 408 | 518 | CUTOUT | P117608 | P117608 | 0 | 2019 | 2014
141014E54117 | C79 PH4 SEC 2 E POLE R1 | Before | 8.589 | 14.4219 | 2 | Tier 3 | 2015-06-01 | 2014-10-14 | Equipment | 518 |  | CUTOUT | P374626 | P374626 | 0 | 2015 | 2014
141028E55164 | 0222-HH | Before | 3.6466 | 19.3644 | 2 | Tier 3 | 2020-05-09 | 2014-10-28 | Equipment | 554 | 214 | CROSSARM | P117218 | P117218 | 0 | 2020 | 2014
141028E55164 | C222 PH4 SEC2 DPOLE CH R1 | Before | 9.0055 | 14.0055 | 2 | Tier 3 | 2014-12-31 | 2014-10-28 | Equipment | 554 | 214 | CROSSARM | P117218 | P117218 | 0 | 2014 | 2014
141105E55783 | C79 PH4 SEC 2 #G POLE R6 | Before | 8.4438 | 14.5671 | 2 | Tier 3 | 2015-07-24 | 2014-11-05 | Weather | 412 | 510 | OH CONDUCTOR | P172817 | P172817 | 0 | 2015 | 2014
141119E56836 | C444 BRANCHLN CFSP P4 R1 | Before | 8.0493 | 14.9616 | 1 | Tier 2 | 2015-12-15 | 2014-11-19 | Weather | 408 | 506 | CONNECTOR | P41967 | P41967 | 0 | 2015 | 2014
141119E56836 | C444 BRANCHLN PH2 P4196 R1 | Before | 8.7836 | 14.2274 | 3 | Tier 2 | 2015-03-22 | 2014-11-19 | Weather | 408 | 506 | CONNECTOR | P41967 | P41967 | 0 | 2015 | 2014
141216E58576 | 0237-C | Before | 7.4658 | 15.5452 | 2 | Tier 3 | 2016-07-15 | 2014-12-16 | Foreign Object | 308 | 520 | FUSE | P17664 | P17664 | 0 | 2016 | 2014
141220E58903 | 0217-J | Before | 4.5507 | 18.4603 | 3 | Tier 2 | 2019-06-14 | 2014-12-20 | Equipment | 515 |  | JUMPER | P312919 | P312919 | 0 | 2019 | 2014
150115E60127 | C222 PH4 SEC2 CPOLE CHGOU | Before | 8.6767 | 14.3342 | 2 | Tier 3 | 2015-04-30 | 2015-01-15 | Equipment | 515 |  | JUMPER | P111072 | P111072 | 0 | 2015 | 2015
150124E60653 | 0217-R | Before | 4.3014 | 18.7096 | 1 | Tier 2 | 2019-09-13 | 2015-01-24 | Equipment | 515 |  | JUMPER | P215656 | P215656 | 0 | 2019 | 2015
150124E60660 | 0217-J | Before | 4.5507 | 18.4603 | 2 | Tier 2 | 2019-06-14 | 2015-01-24 | Equipment | 510 |  | OH CONDUCTOR | P312927 | P312927 | 0 | 2019 | 2015
150124E60677 | 0217-J | Before | 4.5507 | 18.4603 | 2 | Tier 2 | 2019-06-14 | 2015-01-24 | Equipment | 510 |  | OH CONDUCTOR | P312927 | P312927 | 0 | 2019 | 2015
150215E62471 | 0974-D | Before | 6.1836 | 16.8274 | 2 | Tier 3 | 2017-10-26 | 2015-02-15 | Customer Contact | 710 | 532 | POLE | P876235 | P876235 | 0 | 2017 | 2015
150217E62559 | CRA1 PH 2 A RECONDUCTOR | Before | 8.2603 | 14.7507 | 2 | Tier 2 | 2015-09-29 | 2015-02-17 | Customer Contact | 710 | 532 | POLE | P115629 | P115629 | 0 | 2015 | 2015
150309E63983 | 0079-M | Before | 7.7753 | 15.2356 | 1 | Tier 3 | 2016-03-24 | 2015-03-09 | Customer Contact | 710 | 532 | POLE | P172834 | P172834 | 0 | 2016 | 2015
150424E67686 | 0974-B | Before | 6.0767 | 16.9342 | 2 | Tier 3 | 2017-12-04 | 2015-04-24 | Customer Contact | 710 | 532 | POLE | P249955 | P249955 | 0 | 2017 | 2015
150508E68794 | 0217-M | Before | 4.8301 | 18.1808 | 1 | Tier 2 | 2019-03-04 | 2015-05-08 | Customer Contact | 710 | 532 | POLE | P18658 | P18658 | 0 | 2019 | 2015
150513E69137 | 1030-C | Before | 6.6521 | 16.3589 | 1 | Tier 3 | 2017-05-08 | 2015-05-13 | Customer Contact | 710 | 532 | POLE | P112204 | P112204 | 0 | 2017 | 2015
150604E70693 | 0220-C | Before | 7.7342 | 15.2767 | 2 | Tier 3 | 2016-04-08 | 2015-06-04 | Crew Contact | 602 | 510 | OH CONDUCTOR | P102678 | P102678 | 0 | 2016 | 2015
150615E71432 | C444 BRANCHLN CFSP P4 R1 | Before | 8.0493 | 14.9616 | 2 | Tier 2 | 2015-12-15 | 2015-06-15 | Foreign Object | 308 | 510 | OH CONDUCTOR | P46574 | P46574 | 0 | 2015 | 2015
150702E72836 | 0217-X (ASD) | Before | 4.074 | 18.937 | 1 | Tier 2 | 2019-12-05 | 2015-07-02 | Weather | 404 | 516 | DEADEND | P711658 | P711658 | 0 | 2019 | 2015
150707E72990 | 0908-F | Before | 3.3589 | 19.6521 | 2 | Tier 2 | 2020-08-22 | 2015-07-07 | Equipment | 515 |  | JUMPER | P112872 | P112872 | 0 | 2020 | 2015
150813E76133 | 0212-A | Before | 4.0137 | 18.9973 | 1 | Tier 2 | 2019-12-27 | 2015-08-13 | Equipment | 515 |  | JUMPER | P19586 | P19586 | 0 | 2019 | 2015
150813E76133 | 0212-A | Before | 4.0137 | 18.9973 | 2 | Tier 2 | 2019-12-27 | 2015-08-13 | Equipment | 515 |  | JUMPER | P19586 | P19586 | 0 | 2019 | 2015
150907E77919 | 0176-C | Before | 6.8932 | 16.1178 | 2 | Tier 3 | 2017-02-09 | 2015-09-07 | Foreign Object | 315 | 510 | OH CONDUCTOR | P115222 | P115222 | 0 | 2017 | 2015
150907E77919 | 0176-D | Before | 4.9753 | 18.0356 | 1 | Tier 3 | 2019-01-10 | 2015-09-07 | Foreign Object | 315 | 510 | OH CONDUCTOR | P115222 | P115222 | 0 | 2019 | 2015
150908E77978 | C222 PH 1 I RECONDUC R7 | After | 8.389 | 14.6219 | 2 | Tier 3 | 2015-08-13 | 2015-09-08 | Equipment | 515 |  | JUMPER | P312752 | P312752 | 0 | 2015 | 2015
151004E80028 | 0176-A | Before | 6.7397 | 16.2712 | 2 | Tier 3 | 2017-04-06 | 2015-10-04 | Equipment | 518 |  | CUTOUT | P217600 | P217600 | 0 | 2017 | 2015
151102E81991 | 0350-L | Before | 4.2685 | 18.7425 | 1 | Tier 2 | 2019-09-25 | 2015-11-02 | Equipment | 554 |  | CROSSARM | P215143 | P215143 | 0 | 2019 | 2015
151222E84988 | C237 PH 2 H RECONDUCT R8 | After | 8.3863 | 14.6247 | 1 | Tier 3 | 2015-08-14 | 2015-12-22 | Weather | 404 | 510 | OH CONDUCTOR | P17960 | P17960 | 0 | 2015 | 2015
160101E85337 | 0520-D | Before | 6.5315 | 16.4795 | 1 | Tier 2 | 2017-06-21 | 2016-01-01 | Equipment | 522 |  | FUSE | P216064 | P216064 | 0 | 2017 | 2016
160107E85634 | C442 PH 4 FPOLE CHGOUT R1 | Before | 7.6575 | 15.3534 | 1 | Tier 3 | 2016-05-06 | 2016-01-07 | Tree Contact | 322 | 532 | POLE | P178493 | P178493 | 0 | 2016 | 2016
160108E85723 | 0176-C | Before | 6.8932 | 16.1178 | 2 | Tier 3 | 2017-02-09 | 2016-01-08 | Equipment | 522 |  | FUSE | P212520 | P212520 | 0 | 2017 | 2016
160131E87303 | 1030-N | Before | 6.3836 | 16.6274 | 2 | Tier 3 | 2017-08-14 | 2016-01-31 | Foreign Object | 315 | 510 | OH CONDUCTOR | P117525 | P117525 | 0 | 2017 | 2016
160213E88450 | 0971-M | Before | 5.8384 | 17.1726 | 1 | Tier 3 | 2018-03-01 | 2016-02-13 | Foreign Object | 308 | 510 | OH CONDUCTOR | P614155 | P614155 | 0 | 2018 | 2016
160227E89496 | 0217-D | Before | 4.0356 | 18.9753 | 2 | Tier 3 | 2019-12-19 | 2016-02-27 | Equipment | 522 |  | FUSE | P217466 | P217466 | 0 | 2019 | 2016
160324E91711 | 0221-A | Before | 5.7425 | 17.2685 | 1 | Tier 3 | 2018-04-05 | 2016-03-24 | Equipment | 518 | 214 | CUTOUT | P412648 | P412648 | 0 | 2018 | 2016
160328E91923 | 0222-FF | Before | 1.7452 | 21.2658 | 1 | Tier 3 | 2022-04-03 | 2016-03-28 | Equipment | 554 |  | CROSSARM | P416133 | P416133 | 0 | 2022 | 2016
160328E91923 | 0222-FF | Before | 1.7452 | 21.2658 | 1 | Tier 3 | 2022-04-03 | 2016-03-28 | Equipment | 554 |  | CROSSARM | P416133 | P416133 | 0 | 2022 | 2016
160328E91923 | 0222-FF-PH-02 | Before | 1.7863 | 21.2247 | 1 | Tier 3 | 2022-03-19 | 2016-03-28 | Equipment | 554 |  | CROSSARM | P416133 | P416133 | 0 | 2022 | 2016
160410E92844 | C236 PH 2 D RECONDUCTOR | Before | 7.5288 | 15.4822 | 2 | Tier 3 | 2016-06-22 | 2016-04-10 | Weather | 404 | 532 | POLE | P716395 | P716395 | 0 | 2016 | 2016
160519E96169 | 0222-W | Before | 7.5233 | 15.4877 | 1 | Tier 3 | 2016-06-24 | 2016-05-19 | Crew Contact | 612 | 510 | OH CONDUCTOR | P17835 | P17835 | 0 | 2016 | 2016
160519E96169 | 0222-Y | Before | 7.1178 | 15.8932 | 2 | Tier 3 | 2016-11-19 | 2016-05-19 | Crew Contact | 612 | 510 | OH CONDUCTOR | P17835 | P17835 | 0 | 2016 | 2016
160519E96169 | 0222-Z | Before | 6.6438 | 16.3671 | 2 | Tier 3 | 2017-05-11 | 2016-05-19 | Crew Contact | 612 | 510 | OH CONDUCTOR | P17835 | P17835 | 0 | 2017 | 2016
160711E100085 | 0221-A | Before | 5.7425 | 17.2685 | 1 | Tier 3 | 2018-04-05 | 2016-07-11 | Equipment | 502 | 214 | LIGHTNING ARRESTER | P412648 | P412648 | 0 | 2018 | 2016
160712E100093 | C220 PH 4 G POLE CHGO R2 | After | 8.1836 | 14.8274 | 2 | Tier 3 | 2015-10-27 | 2016-07-12 | Foreign Object | 308 | 510 | OH CONDUCTOR | P218742 | P218742 | 0 | 2015 | 2016
160723E101115 | 0237-N | Before | 7.3616 | 15.6493 | 2 | Tier 3 | 2016-08-22 | 2016-07-23 | Tree Contact | 322 | 510 | OH CONDUCTOR | P14085 | P14085 | 0 | 2016 | 2016
160725E101152 | 0445-Q | Before | 2.0356 | 20.9753 | 1 | Tier 2 | 2021-12-18 | 2016-07-25 | Foreign Object | 308 | 510 | OH CONDUCTOR | P41372 | P41372 | 0 | 2021 | 2016
160731E101668 | 448RRR | Before | 2.4384 | 20.5726 | 2 | Tier 3 | 2021-07-24 | 2016-07-31 | Weather | 410 | 502 | LIGHTNING ARRESTER | P207238 | P207238 | 0 | 2021 | 2016
160809E102395 | 0217-J | Before | 4.5507 | 18.4603 | 2 | Tier 2 | 2019-06-14 | 2016-08-09 | Equipment | 515 |  | JUMPER | P312924 | P312924 | 0 | 2019 | 2016
160812E102647 | C442 PH 4 GPOLE CHGOUT R1 | After | 8.0712 | 14.9397 | 2 | Tier 3 | 2015-12-07 | 2016-08-12 | Customer Contact | 710 | 532 | POLE | P173190 | P173190 | 0 | 2015 | 2016
160915E105170 | 0221-V | Before | 7.0877 | 15.9233 | 3 | Tier 3 | 2016-11-30 | 2016-09-15 | Equipment | 532 | 513 | POLE | P717419 | P717419 | 0 | 2016 | 2016
160919E105445 | 448RRR | Before | 2.4384 | 20.5726 | 2 | Tier 3 | 2021-07-24 | 2016-09-19 | Equipment | 502 |  | LIGHTNING ARRESTER | P207238 | P207238 | 0 | 2021 | 2016
160920E105457 | 448RRR | Before | 2.4384 | 20.5726 | 2 | Tier 3 | 2021-07-24 | 2016-09-20 | Equipment | 502 |  | LIGHTNING ARRESTER | P207238 | P207238 | 0 | 2021 | 2016
161009E106862 | 0350-M | Before | 4.2685 | 18.7425 | 1 | Tier 2 | 2019-09-25 | 2016-10-09 | Equipment | 532 | 214 | POLE | P711846 | P711846 | 0 | 2019 | 2016
161011E107034 | 1030-R | Before | 6.3836 | 16.6274 | 2 | Tier 3 | 2017-08-14 | 2016-10-11 | Equipment | 513 |  | OH CONDUCTOR | P410563 | P410563 | 0 | 2017 | 2016
161024E107928 | 0237-F | After | 7.937 | 15.074 | 2 | Tier 3 | 2016-01-25 | 2016-10-24 | Weather | 410 | 550 | TRANSFORMER | P514111 | P514111 | 0 | 2016 | 2016
161024E108033 | 0520-F | Before | 5.4384 | 17.5726 | 2 | Tier 2 | 2018-07-25 | 2016-10-24 | Equipment | 550 |  | LIGHTNING ARRESTER | P512491 | P512491 | 0 | 2018 | 2016
161113E109399 | C1023/C354_RFS_FREEWAY_X | Before | 2.6301 | 20.3808 | 2 | Tier 2 | 2021-05-15 | 2016-11-13 | Miscellaneous | 206 | 214 | POLE | P810206 | P810206 | 0 | 2021 | 2016
161120E109928 | C1023/C354_NEW_12KV_RECON | Before | 2.0795 | 20.9315 | 2 | Tier 2 | 2021-12-02 | 2016-11-20 | Tree Contact | 322 | 510 | OH CONDUCTOR | P246460 | P246460 | 0 | 2021 | 2016
161124E110161 | 0212-A | Before | 4.0137 | 18.9973 | 1 | Tier 2 | 2019-12-27 | 2016-11-24 | Equipment | 515 | 412 | JUMPER | P19586 | P19586 | 0 | 2019 | 2016
161124E110161 | 0212-A | Before | 4.0137 | 18.9973 | 2 | Tier 2 | 2019-12-27 | 2016-11-24 | Equipment | 515 | 412 | JUMPER | P19586 | P19586 | 0 | 2019 | 2016
161203E110710 | 0157-T | Before | 4.0548 | 18.9562 | 1 | Tier 3 | 2019-12-12 | 2016-12-03 | Equipment | 522 |  | FUSE | P475949 | P475949 | 0 | 2019 | 2016
161212E111361 | 0212-B | Before | 4.0137 | 18.9973 | 2 | Tier 3 | 2019-12-27 | 2016-12-12 | Foreign Object | 308 | 510 | OH CONDUCTOR | P19529 | P19529 | 0 | 2019 | 2016
161214E111502 | 0212-B | Before | 4.0137 | 18.9973 | 2 | Tier 3 | 2019-12-27 | 2016-12-14 | Foreign Object | 308 | 510 | OH CONDUCTOR | P19529 | P19529 | 0 | 2019 | 2016
161224E112199 | 0221-M | After | 7.2384 | 15.7726 | 2 | Tier 3 | 2016-10-06 | 2016-12-24 | Undetermined | 100 |  | FUSE | P211371 | P211371 | 0 | 2016 | 2016
161228E112311 | 0971-A | Before | 6.6027 | 16.4082 | 1 | Tier 2 | 2017-05-26 | 2016-12-28 | Equipment | 522 |  | FUSE | P717097 | P717097 | 0 | 2017 | 2016
170108E113004 | 0175-C | Before | 6.7589 | 16.2521 | 2 | Tier 3 | 2017-03-30 | 2017-01-08 | Equipment | 522 |  | FUSE | P114287 | P114287 | 0 | 2017 | 2017
170121E113928 | 0221-G | Before | 5.9205 | 17.0904 | 2 | Tier 3 | 2018-01-30 | 2017-01-21 | Weather | 404 | 515 | JUMPER | P18802J | P18802J | 0 | 2018 | 2017
170122E114565 | 0221-G | Before | 5.9205 | 17.0904 | 2 | Tier 3 | 2018-01-30 | 2017-01-22 | Equipment | 515 |  | JUMPER | P18802J | P18802J | 0 | 2018 | 2017
170123E114041 | 0971-I | Before | 6.5068 | 16.5041 | 2 | Tier 3 | 2017-06-30 | 2017-01-23 | Equipment | 532 | 214 | POLE | P113596 | P113596 | 0 | 2017 | 2017
170123E114065 | 448YY | Before | 2.2 | 20.811 | 2 | Tier 3 | 2021-10-19 | 2017-01-23 | Equipment | 532 | 214 | POLE | P163225 | P163225 | 0 | 2021 | 2017
170127E114472 | 448T | Before | 0.69589 | 22.3151 | 2 | Tier 3 | 2023-04-21 | 2017-01-27 | Equipment | 528 |  | MISC EQUIPMENT | P43717 | P43717 | 0 | 2023 | 2017
170128E114540 | 448YY | Before | 2.2 | 20.811 | 1 | Tier 3 | 2021-10-19 | 2017-01-28 | Equipment | 502 |  | LIGHTNING ARRESTER | P163226 | P163226 | 0 | 2021 | 2017
170210E115554 | C220 PH 4 G POLE CHGO R2 | After | 8.1836 | 14.8274 | 1 | Tier 3 | 2015-10-27 | 2017-02-10 | Foreign Object | 315 | 522 | FUSE | P413246 | P413246 | 0 | 2015 | 2017
170304E117218 | 0217-R | Before | 4.3014 | 18.7096 | 2 | Tier 2 | 2019-09-13 | 2017-03-04 | Customer Contact | 710 | 532 | POLE | P14990 | P14990 | 0 | 2019 | 2017
170401E119385 | 0350-F | Before | 4.2329 | 18.7781 | 3 | Tier 2 | 2019-10-08 | 2017-04-01 | Equipment | 522 |  | FUSE | P213217 | P213217 | 0 | 2019 | 2017
170404E119606 | 0215-B | Before | 5.5671 | 17.4438 | 2 | Tier 2 | 2018-06-08 | 2017-04-04 | Customer Contact | 710 | 532 | POLE | P817313 | P817313 | 0 | 2018 | 2017
170407E119861 | C1215 MAINLINE CFSP W/S R1 | After | 8.6712 | 14.3397 | 2 | Tier 3 | 2015-05-02 | 2017-04-07 | Undetermined | 100 |  |  | P40838 | P40838 | 0 | 2015 | 2017
170416E120281 | 0185-CAMINITO_A_CASA | Before | 1.1973 | 21.8137 | 1 | Tier 2 | 2022-10-20 | 2017-04-16 | Customer Contact | 710 | 526 | GUY WIRE | P211576 | P211576 | 0 | 2022 | 2017
170506E121812 | 1030-T | After | 7.3699 | 15.6411 | 2 | Tier 3 | 2016-08-19 | 2017-05-06 | Customer Contact | 710 | 532 | POLE | P617984 | P617984 | 0 | 2016 | 2017
170510E122046 | 0079-M | After | 7.7753 | 15.2356 | 1 | Tier 3 | 2016-03-24 | 2017-05-10 | Customer Contact | 710 | 532 | POLE | P172834 | P172834 | 0 | 2016 | 2017
170524E122956 | 0974-B | Before | 6.0767 | 16.9342 | 3 | Tier 3 | 2017-12-04 | 2017-05-24 | Equipment | 554 |  | CROSSARM | P378657 | P378657 | 0 | 2017 | 2017
170626E125242 | 0157-G | Before | 2.5726 | 20.4384 | 2 | Tier 3 | 2021-06-05 | 2017-06-26 | Equipment | 515 |  | JUMPER | P176095 | P176095 | 0 | 2021 | 2017
170707E126155 | 0358-C | After | 7.6082 | 15.4027 | 2 | Tier 3 | 2016-05-24 | 2017-07-07 | Equipment | 554 | 518 | CROSSARM | P175474 | P175474 | 0 | 2016 | 2017
170707E126242 | 0350-G | Before | 5.2658 | 17.7452 | 1 | Tier 2 | 2018-09-26 | 2017-07-07 | Undetermined | 100 |  |  | P514665 | P514665 | 0 | 2018 | 2017
170713E126544 | C221:ERI 2012 REBUILD IM R9 | After | 10.1945 | 12.8164 | 2 | Tier 3 | 2013-10-23 | 2017-07-13 | Equipment | 554 | 214 | CROSSARM | P18540 | P18540 | 0 | 2013 | 2017
170713E126544 | C221:ERI 2012 REBUILD IM R9 | After | 10.1945 | 12.8164 | 6 | Tier 3 | 2013-10-23 | 2017-07-13 | Equipment | 554 | 218 | CROSSARM | P18540 | P18540 | 0 | 2013 | 2017
170806E128346 | 0157-W | Before | 3.8384 | 19.1726 | 1 | Tier 3 | 2020-02-29 | 2017-08-06 | Foreign Object | 314 | 510 | OH CONDUCTOR | P577691 | P577691 | 0 | 2020 | 2017
171014E133931 | 0212-C-PH-02 | Before | 3.0904 | 19.9205 | 1 | Tier 3 | 2020-11-28 | 2017-10-14 | Customer Contact | 710 | 518 | CUTOUT | P616190 | P616190 | 0 | 2020 | 2017
171014E133931 | 0212-C-PH-03 | Before | 3.0904 | 19.9205 | 1 | Tier 3 | 2020-11-28 | 2017-10-14 | Customer Contact | 710 | 518 | CUTOUT | P616190 | P616190 | 0 | 2020 | 2017
171110E135863 | 0974-B | Before | 6.0767 | 16.9342 | 3 | Tier 3 | 2017-12-04 | 2017-11-10 | Equipment | 515 |  | CONNECTOR | P378660 | P378660 | 0 | 2017 | 2017
171203E137181 | 0212-E | Before | 3.474 | 19.537 | 2 | Tier 2 | 2020-07-11 | 2017-12-03 | Equipment | 542 | 214 | REGULATOR | P216490 | P216490 | 0 | 2020 | 2017
171206E137424 | 0217-G | Before | 5.337 | 17.674 | 3 | Tier 2 | 2018-08-31 | 2017-12-06 | Equipment | 532 |  | POLE | P317486 | P317486 | 0 | 2018 | 2017
180109E139564 | 0222-K | After | 7.4658 | 15.5452 | 2 | Tier 3 | 2016-07-15 | 2018-01-09 | Weather | 404 | 532 | POLE | P17676 | P17676 | 0 | 2016 | 2018
180127E141039 | 0908-E | Before | 4.3041 | 18.7068 | 1 | Tier 2 | 2019-09-12 | 2018-01-27 | Customer Contact | 710 | 532 | POLE | P116880 | P116880 | 0 | 2019 | 2018
180127E141039 | 0908-E | Before | 4.3041 | 18.7068 | 2 | Tier 2 | 2019-09-12 | 2018-01-27 | Customer Contact | 710 | 532 | POLE | P116880 | P116880 | 0 | 2019 | 2018
180219E142807 | 0079-A | After | 7.789 | 15.2219 | 3 | Tier 3 | 2016-03-19 | 2018-02-19 | Equipment | 515 |  | JUMPER | P275911 | P275911 | 0 | 2016 | 2018
180224E143336 | 0221-P | After | 5.8767 | 17.1342 | 3 | Tier 3 | 2018-02-15 | 2018-02-24 | Undetermined | 100 |  | CONNECTOR | P112452 | P112452 | 0 | 2018 | 2018
180413E147307 | 0444-A | Before | 2.5589 | 20.4521 | 2 | Tier 2 | 2021-06-10 | 2018-04-13 | Equipment | 515 |  | JUMPER | P42045 | P42045 | 0 | 2021 | 2018
180418E147695 | 0079-A | After | 7.789 | 15.2219 | 1 | Tier 3 | 2016-03-19 | 2018-04-18 | Undetermined | 100 |  | JUMPER | P273588 | P273588 | 0 | 2016 | 2018
180425E148889 | 0221-A | After | 5.7425 | 17.2685 | 2 | Tier 3 | 2018-04-05 | 2018-04-25 | Equipment | 554 |  | CROSSARM | P412624 | P412624 | 0 | 2018 | 2018
180601E151051 | 0221-F | After | 5.5945 | 17.4164 | 2 | Tier 3 | 2018-05-29 | 2018-06-01 | Customer Contact | 710 | 532 | POLE | P117926 | P117926 | 0 | 2018 | 2018
180612E151825 | C1215 MAINLINE CFSP W/S R1 | After | 8.6712 | 14.3397 | 2 | Tier 3 | 2015-05-02 | 2018-06-12 | Foreign Object | 308 | 544 | SWITCH | P44708 | P44708 | 0 | 2015 | 2018
180614E151981 | 1030-C | After | 6.6521 | 16.3589 | 1 | Tier 3 | 2017-05-08 | 2018-06-14 | Customer Contact | 710 | 532 | POLE | P112206 | P112206 | 0 | 2017 | 2018
180629E153296 | 0237-F | After | 7.937 | 15.074 | 2 | Tier 3 | 2016-01-25 | 2018-06-29 | Equipment | 520 |  | FUSE | P317990 | P317990 | 0 | 2016 | 2018
180711E154157 | 0217-H | Before | 4.7425 | 18.2685 | 2 | Tier 2 | 2019-04-05 | 2018-07-11 | Crew Contact | 632 | 510 | OH CONDUCTOR | P211139 | P211139 | 0 | 2019 | 2018
180720E154896 | 0230-B | Before | 4.9753 | 18.0356 | 2 | Tier 2 | 2019-01-10 | 2018-07-20 | Crew Contact | 612 |  | OH CONDUCTOR | P116147 | P116147 | 0 | 2019 | 2018
180726E155295 | 0442-M | After | 7.6932 | 15.3178 | 1 | Tier 3 | 2016-04-23 | 2018-07-26 | Foreign Object | 308 | 502 | LIGHTNING ARRESTER | P276274 | P276274 | 0 | 2016 | 2018
180913E159143 | 0221-L | After | 7.0438 | 15.9671 | 2 | Tier 3 | 2016-12-16 | 2018-09-13 | Equipment | 520 |  | FUSE | P211409 | P211409 | 0 | 2016 | 2018
180918E159433 | 0221-Y-PH1-SLAUGHTER | After | 5.4384 | 17.5726 | 1 | Tier 3 | 2018-07-25 | 2018-09-18 | Equipment | 502 |  | LIGHTNING ARRESTER | P110715 | P110715 | 0 | 2018 | 2018
181012E161307 | 0176-A | After | 6.7397 | 16.2712 | 3 | Tier 3 | 2017-04-06 | 2018-10-12 | Weather | 410 |  |  | P515477 | P515477 | 0 | 2017 | 2018
181015E161463 | C445 2012 CFSP WS BRANCH R1 | After | 8.0329 | 14.9781 | 2 | Tier 2 | 2015-12-21 | 2018-10-15 | Equipment | 518 |  | CUTOUT | P41541 | P41541 | 0 | 2015 | 2018
181206E164866 | 0358-C | After | 7.6082 | 15.4027 | 1 | Tier 3 | 2016-05-24 | 2018-12-06 | Weather | 404 | 554 | CROSSARM | P103145 | P103145 | 0 | 2016 | 2018
181209E165022 | C358 PH 2 A RECONDUCTOR | After | 8.2192 | 14.7918 | 1 | Tier 3 | 2015-10-14 | 2018-12-09 | Equipment | 520 |  | FUSE | P176532 | P176532 | 0 | 2015 | 2018
181211E165145 | 0908-A | Before | 5.0301 | 17.9808 | 2 | Tier 2 | 2018-12-21 | 2018-12-11 | Crew Contact | 602 | 510 | OH CONDUCTOR | P319235 | P319235 | 0 | 2018 | 2018
190121E167608 | 0240-G | After | 5.2493 | 17.7616 | 1 | Tier 3 | 2018-10-02 | 2019-01-21 | Foreign Object | 308 | 510 | OH CONDUCTOR | P76578 | P76578 | 0 | 2018 | 2019
190126E168083 | 0212-D | Before | 3.2822 | 19.7288 | 3 | Tier 3 | 2020-09-19 | 2019-01-26 | Equipment | 518 |  | CUTOUT | P112513 | P112513 | 0 | 2020 | 2019
190215E169766 | 0212-B | Before | 4.0137 | 18.9973 | 2 | Tier 3 | 2019-12-27 | 2019-02-15 | Foreign Object | 308 | 510 | OH CONDUCTOR | P19529 | P19529 | 0 | 2019 | 2019
190306E171047 | 0176-A | After | 6.7397 | 16.2712 | 3 | Tier 3 | 2017-04-06 | 2019-03-06 | Weather | 410 |  |  | P515477 | P515477 | 0 | 2017 | 2019
190306E171048 | 0972-C | After | 6.8055 | 16.2055 | 3 | Tier 3 | 2017-03-13 | 2019-03-06 | Weather | 410 |  |  | P13274 | P13274 | 0 | 2017 | 2019
190314E171585 | 0222-EE | Before | 3.1863 | 19.8247 | 2 | Tier 3 | 2020-10-24 | 2019-03-14 | Foreign Object | 304 | 510 | OH CONDUCTOR | P219588 | P219588 | 0 | 2020 | 2019
190406E173394 | 0175-D | After | 6.8932 | 16.1178 | 2 | Tier 3 | 2017-02-09 | 2019-04-06 | Undetermined | 100 |  |  | P612464 | P612464 | 0 | 2017 | 2019
190410E173619 | 0445-J | Before | 3.6082 | 19.4027 | 2 | Tier 2 | 2020-05-23 | 2019-04-10 | Equipment | 513 |  | OH CONDUCTOR | P45801 | P45801 | 0 | 2020 | 2019
190410E173636 | 0217-J | Before | 4.5507 | 18.4603 | 2 | Tier 2 | 2019-06-14 | 2019-04-10 | Foreign Object | 314 | 510 | OH CONDUCTOR | P312915 | P312915 | 0 | 2019 | 2019
190422E174540 | 1030-F | After | 6.3726 | 16.6384 | 2 | Tier 3 | 2017-08-18 | 2019-04-22 | Customer Contact | 710 | 532 | POLE | P212405 | P212405 | 0 | 2017 | 2019
190507E175686 | 0157-H | Before | 3.3014 | 19.7096 | 1 | Tier 3 | 2020-09-12 | 2019-05-07 | Foreign Object | 308 | 502 | LIGHTNING ARRESTER | P175952 | P175952 | 0 | 2020 | 2019
190507E175686 | 0157-H | Before | 3.3014 | 19.7096 | 2 | Tier 3 | 2020-09-12 | 2019-05-07 | Foreign Object | 308 | 502 | LIGHTNING ARRESTER | P175952 | P175952 | 0 | 2020 | 2019
190512E176081 | 0222-AA | After | 6.4164 | 16.5945 | 2 | Tier 3 | 2017-08-02 | 2019-05-12 | Foreign Object | 315 | 532 | POLE | P17874 | P17874 | 0 | 2017 | 2019
190530E177367 | 0221-A | After | 5.7425 | 17.2685 | 1 | Tier 3 | 2018-04-05 | 2019-05-30 | Equipment | 515 |  | JUMPER | P412648 | P412648 | 0 | 2018 | 2019
190611E178155 | 0236-B | After | 7.2027 | 15.8082 | 2 | Tier 3 | 2016-10-19 | 2019-06-11 | Customer Contact | 710 | 532 | POLE | P212838 | P212838 | 0 | 2016 | 2019
190620E178960 | CNF-TL629A | Before | 3.2849 | 19.726 | 1 | Tier 3 | 2020-09-18 | 2019-06-20 | Equipment | 554 |  | CROSSARM | Z173103 | Z173103 | 0 | 2020 | 2019
190624E179238 | 0217-AD | Before | 3.6849 | 19.326 | 1 | Tier 3 | 2020-04-25 | 2019-06-24 | Equipment | 532 |  | POLE | P514950 | P514950 | 0 | 2020 | 2019
190624E179238 | 0217-D | Before | 4.0356 | 18.9753 | 3 | Tier 3 | 2019-12-19 | 2019-06-24 | Equipment | 532 |  | POLE | P514950 | P514950 | 0 | 2019 | 2019
190704E179925 | 0212-A | Before | 4.0137 | 18.9973 | 1 | Tier 2 | 2019-12-27 | 2019-07-04 | Undetermined | 100 |  |  | P253196 | P253196 | 0 | 2019 | 2019
190705E179942 | 0212-J | Before | 2.1315 | 20.8795 | 2 | Tier 2 | 2021-11-13 | 2019-07-05 | Equipment | 515 |  | JUMPER | P216907 | P216907 | 0 | 2021 | 2019
190724E181355 | C222 FIRE RISK MITIG PRO R1 | After | 8.9014 | 14.1096 | 2 | Tier 3 | 2015-02-07 | 2019-07-24 | Equipment | 530 |  | INSULATOR | P17786 | P17786 | 0 | 2015 | 2019
190724E181355 | C222 FIRE RISK MITIG PRO R1 | After | 8.9014 | 14.1096 | 2 | Tier 3 | 2015-02-07 | 2019-07-24 | Equipment | 530 |  | INSULATOR | P17786 | P17786 | 0 | 2015 | 2019
190904E184396 | 0971-J | After | 6.6027 | 16.4082 | 3 | Tier 3 | 2017-05-26 | 2019-09-04 | Equipment | 515 |  | JUMPER | P111573 | P111573 | 0 | 2017 | 2019
191126E191432 | 0222-FF-PH-02 | Before | 1.7863 | 21.2247 | 1 | Tier 3 | 2022-03-19 | 2019-11-26 | Equipment | 554 |  | CROSSARM | P619525 | P619525 | 0 | 2022 | 2019
191128E191563 | 0212-A | Before | 4.0137 | 18.9973 | 2 | Tier 2 | 2019-12-27 | 2019-11-28 | Equipment | 515 |  | LINE DISC | P19585 | P19585 | 0 | 2019 | 2019
191220E193462 | CNF-TL629A | Before | 3.2849 | 19.726 | 1 | Tier 3 | 2020-09-18 | 2019-12-20 | Equipment | 515 |  | JUMPER | Z172747 | Z172747 | 0 | 2020 | 2019
191220E193462 | CNF-TL629A | Before | 3.2849 | 19.726 | 1 | Tier 3 | 2020-09-18 | 2019-12-20 | Equipment | 515 | 218 | JUMPER | Z172747 | Z172747 | 0 | 2020 | 2019
200210E196515 | 0908-H | Before | 3.7233 | 19.2877 | 1 | Tier 2 | 2020-04-11 | 2020-02-10 | Equipment | 528 |  | MISC EQUIPMENT | P213993 | P213993 | 0 | 2020 | 2020
200210E196559 | 0908-H | Before | 3.7233 | 19.2877 | 1 | Tier 2 | 2020-04-11 | 2020-02-10 | Equipment | 528 |  | MISC EQUIPMENT | P213993 | P213993 | 0 | 2020 | 2020
200226E197846 | CNF-TL629A | Before | 3.2849 | 19.726 | 2 | Tier 3 | 2020-09-18 | 2020-02-26 | Equipment | 515 |  | JUMPER | P164041 | P164041 | 0 | 2020 | 2020
200303E198364 | 0908-F | Before | 3.3589 | 19.6521 | 2 | Tier 2 | 2020-08-22 | 2020-03-03 | Foreign Object | 315 | 510 | OH CONDUCTOR | P112872 | P112872 | 0 | 2020 | 2020
200323E199904 | 0350-F | After | 4.2329 | 18.7781 | 1 | Tier 2 | 2019-10-08 | 2020-03-23 | Equipment | 502 |  | LIGHTNING ARRESTER | P417375 | P417375 | 0 | 2019 | 2020
200324E199920 | 0222-Z | After | 6.6438 | 16.3671 | 4 | Tier 3 | 2017-05-11 | 2020-03-24 | Equipment | 518 |  | CUTOUT | P117857 | P117857 | 0 | 2017 | 2020
200401E200765 | 0222-K | After | 7.4658 | 15.5452 | 1 | Tier 3 | 2016-07-15 | 2020-04-01 | Third Party Contact | 710 | 532 | POLE | P17697 | P17697 | 0 | 2016 | 2020
200428E203022 | 0222-II | Before | 3.2438 | 19.7671 | 3 | Tier 3 | 2020-10-03 | 2020-04-28 | Equipment | 532 |  | POLE | P212776 | P212776 | 0 | 2020 | 2020
200428E203051 | 448YY | Before | 2.2 | 20.811 | 1 | Tier 3 | 2021-10-19 | 2020-04-28 | Equipment | 550 |  | TRANSFORMER | P163226 | P163226 | 0 | 2021 | 2020
200701E208687 | 0176-L | Before | 2.5151 | 20.4959 | 3 | Tier 3 | 2021-06-26 | 2020-07-01 | Equipment | 515 | 214 | CONNECTOR | P119412 | P119412 | 0 | 2021 | 2020
200712E209371 | 0222-FF | Before | 1.7452 | 21.2658 | 2 | Tier 3 | 2022-04-03 | 2020-07-12 | Equipment | 532 |  | POLE | P412778 | P412778 | 0 | 2022 | 2020
200730E211164 | 0237-O | After | 7.5836 | 15.4274 | 3 | Tier 3 | 2016-06-02 | 2020-07-30 | Weather | 404 | 522 | FUSE | P112131 | P112131 | 0 | 2016 | 2020
200731E211253 | 0445-O | Before | 3.3397 | 19.6712 | 2 | Tier 2 | 2020-08-29 | 2020-07-31 | SDGE/Contractor Contact | 632 | 515 | CONNECTOR | P41254 | P41254 | 0 | 2020 | 2020
200821E213004 | 0157-D | Before | 2.2466 | 20.7644 | 1 | Tier 3 | 2021-10-02 | 2020-08-21 | SDGE/Contractor Contact | 632 | 510 | OH CONDUCTOR | P167768 | P167768 | 0 | 2021 | 2020
200826E213445 | 0442-D | After | 8.1151 | 14.8959 | 1 | Tier 3 | 2015-11-21 | 2020-08-26 | Equipment | 522 |  | FUSE | P173170 | P173170 | 0 | 2015 | 2020
200828E213714 | C1215 CWLONG SPAN/DESI R12 | After | 9.3041 | 13.7068 | 1 | Tier 3 | 2014-09-13 | 2020-08-28 | Foreign Object | 308 | 508 | OH CONDUCTOR | P40906 | P40906 | 0 | 2014 | 2020
200906E214500 | C233 LONG SPAN EVAL P61 R18 | After | 9.0301 | 13.9808 | 1 | Tier 2 | 2014-12-22 | 2020-09-06 | Equipment | 536 |  | SERVICE RESTORER | P227574 | P227574 | 0 | 2014 | 2020
201017E218058 | 0350-F | After | 4.2329 | 18.7781 | 3 | Tier 2 | 2019-10-08 | 2020-10-17 | Foreign Object | 308 | 502 | LIGHTNING ARRESTER | P213217 | P213217 | 0 | 2019 | 2020
201028E219072 | C222 PH 1 #Q RECONDUC R3 | After | 8.3342 | 14.6767 | 1 | Tier 3 | 2015-09-02 | 2020-10-28 | SDGE/Contractor Contact |  |  |  | P318201 | P318201 | 0 | 2015 | 2020
201106E219939 | C79 PH 2 R RECONDUCTOR | After | 8.2027 | 14.8082 | 1 | Tier 3 | 2015-10-20 | 2020-11-06 | Equipment | 518 |  | CUTOUT | P376431 | P376431 | 0 | 2015 | 2020
201106E219939 | CNF-C79B | Before | 2.2411 | 20.7699 | 1 | Tier 3 | 2021-10-04 | 2020-11-06 | Equipment | 518 |  | CUTOUT | P376431 | P376431 | 0 | 2021 | 2020
201126E221302 | 0237-I | After | 4.0247 | 18.9863 | 2 | Tier 3 | 2019-12-23 | 2020-11-26 | Equipment | 522 |  | FUSE | P113838 | P113838 | 0 | 2019 | 2020
201205E222501 | 0222-BB | After | 7.7671 | 15.2438 | 1 | Tier 3 | 2016-03-27 | 2020-12-05 | Equipment | 522 |  | FUSE | P17908 | P17908 | 0 | 2016 | 2020
201205E222501 | Track 2 530000154309 | Before | 2.9233 | 20.0877 | 1 | Tier 3 | 2021-01-28 | 2020-12-05 | Equipment | 522 |  | FUSE | P17908 | P17908 | 0 | 2021 | 2020
201205E222502 | 0222-BB | After | 7.7671 | 15.2438 | 1 | Tier 3 | 2016-03-27 | 2020-12-05 | Equipment | 522 |  | FUSE | P17908 | P17908 | 0 | 2016 | 2020
201205E222502 | Track 2 530000154309 | Before | 2.9233 | 20.0877 | 1 | Tier 3 | 2021-01-28 | 2020-12-05 | Equipment | 522 |  | FUSE | P17908 | P17908 | 0 | 2021 | 2020
210115E224155 | C442 PH 4 BPOLE CHGOUT R1 | After | 8.7342 | 14.2767 | 2 | Tier 3 | 2015-04-09 | 2021-01-15 | Equipment | 518 |  | CUTOUT | P178017 | P178017 | 0 | 2015 | 2021
210119E224360 | 0445-E | After | 3.6466 | 19.3644 | 2 | Tier 2 | 2020-05-09 | 2021-01-19 | Equipment | 508 | 510 | OH CONDUCTOR | P46204 | P46204 | 0 | 2020 | 2021
210119E224531 | 0445-E | After | 3.6466 | 19.3644 | 2 | Tier 2 | 2020-05-09 | 2021-01-19 | Equipment | 510 | 508 | OH CONDUCTOR | P46204 | P46204 | 0 | 2020 | 2021
210127E225156 | 0221-A | After | 5.7425 | 17.2685 | 1 | Tier 3 | 2018-04-05 | 2021-01-27 | Weather | 408 | 534 | POTHEAD | P412648 | P412648 | 0 | 2018 | 2021
210222E227032 | 0221-F | After | 5.5945 | 17.4164 | 2 | Tier 3 | 2018-05-29 | 2021-02-22 | Undetermined | 100 |  |  | P110709 | P110709 | 0 | 2018 | 2021
210222E227032 | 0221-F | After | 5.5945 | 17.4164 | 2 | Tier 3 | 2018-05-29 | 2021-02-22 | Undetermined | 100 | 218 |  | P110709 | P110709 | 0 | 2018 | 2021
210318E228965 | 1030-N | After | 6.3836 | 16.6274 | 2 | Tier 3 | 2017-08-14 | 2021-03-18 | Third Party Contact | 710 | 532 | POLE | P510234 | P510234 | 0 | 2017 | 2021
210323E229340 | 0974-B | After | 6.0767 | 16.9342 | 2 | Tier 3 | 2017-12-04 | 2021-03-23 | Third Party Contact | 710 | 532 | POLE | P249955 | P249955 | 0 | 2017 | 2021
210405E230409 | CNF-TL629A | After | 3.2849 | 19.726 | 2 | Tier 3 | 2020-09-18 | 2021-04-05 | Foreign Object | 308 | 510 | OH CONDUCTOR | P40410 | P40410 | 0 | 2020 | 2021
210409E230782 | 448W | Before | 2.4986 | 20.5123 | 1 | Tier 3 | 2021-07-02 | 2021-04-09 | Foreign Object | 308 | 532 | POLE | P46064 | P46064 | 0 | 2021 | 2021
210409E230782 | 448X | Before | 2.5041 | 20.5068 | 1 | Tier 3 | 2021-06-30 | 2021-04-09 | Foreign Object | 308 | 532 | POLE | P46064 | P46064 | 0 | 2021 | 2021
210603E234826 | 1030-B | After | 7.4521 | 15.5589 | 2 | Tier 3 | 2016-07-20 | 2021-06-03 | SDGE/Contractor Contact | 632 |  |  | P133549 | P133549 | 0 | 2016 | 2021
210608E235079 | C73 PH 4 APOLE CHGOUT/ R9 | After | 8.7918 | 14.2192 | 2 | Tier 3 | 2015-03-19 | 2021-06-08 | Third Party Contact | 710 | 532 | POLE | P372538 | P372538 | 0 | 2015 | 2021
210625E236536 | 0215-A | After | 5.5178 | 17.4932 | 2 | Tier 2 | 2018-06-26 | 2021-06-25 | Equipment | 518 |  | CUTOUT | P211171 | P211171 | 0 | 2018 | 2021
210722E238579 | 0358-D | After | 8.1534 | 14.8575 | 1 | Tier 3 | 2015-11-07 | 2021-07-22 | Third Party Contact | 702 | 526 | GUY WIRE | P376464 | P376464 | 0 | 2015 | 2021
210724E238722 | 0157-D | Before | 2.2466 | 20.7644 | 2 | Tier 3 | 2021-10-02 | 2021-07-24 | Foreign Object | 308 | 502 | LIGHTNING ARRESTER | P74739 | P74739 | 0 | 2021 | 2021
210726E238738 | 0236-B | After | 7.2027 | 15.8082 | 2 | Tier 3 | 2016-10-19 | 2021-07-26 | Undetermined | 100 |  |  | P711836 | P711836 | 0 | 2016 | 2021
210806E239774 | C222 PH 1 J RECONDUC R6 | After | 8.2548 | 14.7562 | 1 | Tier 3 | 2015-10-01 | 2021-08-06 | Third Party Contact | 710 | 532 | POLE | P17700 | P17700 | 0 | 2015 | 2021
210815E240343 | 0974-B | After | 6.0767 | 16.9342 | 2 | Tier 3 | 2017-12-04 | 2021-08-15 | Third Party Contact | 710 | 532 | POLE | P249955 | P249955 | 0 | 2017 | 2021
210829E241340 | 0222-UU | Before | 2.2082 | 20.8027 | 1 | Tier 3 | 2021-10-16 | 2021-08-29 | Equipment | 532 |  | POLE | P117907 | P117907 | 0 | 2021 | 2021
210829E241340 | 0222-UU | Before | 2.2082 | 20.8027 | 1 | Tier 3 | 2021-10-16 | 2021-08-29 | Equipment | 532 |  | POLE | P117907 | P117907 | 0 | 2021 | 2021
210829E241363 | 0972-D | After | 6.7836 | 16.2274 | 1 | Tier 2 | 2017-03-21 | 2021-08-29 | Weather | 410 |  |  | P615151 | P615151 | 0 | 2017 | 2021
210829E241370 | 0971-J | After | 6.6027 | 16.4082 | 2 | Tier 3 | 2017-05-26 | 2021-08-29 | Weather | 410 |  |  | P111590 | P111590 | 0 | 2017 | 2021
210829E241370 | 0971-K | After | 6.5068 | 16.5041 | 1 | Tier 3 | 2017-06-30 | 2021-08-29 | Weather | 410 |  |  | P111590 | P111590 | 0 | 2017 | 2021
210927E243361 | C358 PH 2 A RECONDUCTOR | After | 8.2192 | 14.7918 | 1 | Tier 3 | 2015-10-14 | 2021-09-27 | Foreign Object | 314 | 510 | OH CONDUCTOR | P176522 | P176522 | 0 | 2015 | 2021
210927E243361 | C358 PH 2 B RECONDUCTOR | After | 8.3918 | 14.6192 | 2 | Tier 3 | 2015-08-12 | 2021-09-27 | Foreign Object | 314 | 510 | OH CONDUCTOR | P176522 | P176522 | 0 | 2015 | 2021
211115E247014 | 0445-Q | Before | 2.0356 | 20.9753 | 1 | Tier 2 | 2021-12-18 | 2021-11-15 | Undetermined | 100 |  |  | P41365 | P41365 | 0 | 2021 | 2021
211115E247014 | 0445-Q | Before | 2.0356 | 20.9753 | 1 | Tier 2 | 2021-12-18 | 2021-11-15 | Undetermined | 100 |  |  | P41365 | P41365 | 0 | 2021 | 2021
220221E253353 | C237 PH 2 J RECONDUCTOR | After | 8.4329 | 14.5781 | 2 | Tier 3 | 2015-07-28 | 2022-02-21 | Equipment | 515 |  | JUMPER | P212981 | P212981 | 0 | 2015 | 2022
220314E255005 | C445 2012 CFSP WS BRANCH R1 | After | 8.0329 | 14.9781 | 2 | Tier 2 | 2015-12-21 | 2022-03-14 | Foreign Object | 308 | 510 | OH CONDUCTOR | P41541 | P41541 | 0 | 2015 | 2022
220315E255103 | 0212-GG | After | 2.3863 | 20.6247 | 2 | Tier 2 | 2021-08-12 | 2022-03-15 | Foreign Object | 308 | 515 | JUMPER | P216518 | P216518 | 0 | 2021 | 2022
220407E256919 | CNF-C79B | After | 2.2411 | 20.7699 | 2 | Tier 3 | 2021-10-04 | 2022-04-07 | Equipment | 515 | 214 | JUMPER | P258571 | P258571 | 0 | 2021 | 2022
220414E257452 | 0221-A | After | 5.7425 | 17.2685 | 2 | Tier 3 | 2018-04-05 | 2022-04-14 | Equipment | 515 | 214 | JUMPER | P412620 | P412620 | 0 | 2018 | 2022
220609E261405 | 0079-M | After | 7.7753 | 15.2356 | 1 | Tier 3 | 2016-03-24 | 2022-06-09 | Third Party Contact | 710 | 532 | POLE | P172834 | P172834 | 0 | 2016 | 2022
220815E266089 | 1030-M | After | 6.9753 | 16.0356 | 2 | Tier 3 | 2017-01-10 | 2022-08-15 | Foreign Object | 308 | 510 | Conductor, OH | P317390 | P317390 | 0 | 2017 | 2022
220903E267574 | 0212-J | After | 2.1315 | 20.8795 | 2 | Tier 2 | 2021-11-13 | 2022-09-03 | Foreign Object | 308 | 510 | Conductor, OH | P137809 | P137809 | 0 | 2021 | 2022
220909E268141 | C441 PH 4 POLE REPLACE R2 | After | 9.189 | 13.8219 | 2 | Tier 3 | 2014-10-25 | 2022-09-09 | Weather | 412 | 510 | Wire Slap | P40493 | P40493 | 0 | 2014 | 2022
221208E274398 | C221 PH4 #B POLE REPLA R1 | After | 8.5945 | 14.4164 | 1 | Tier 3 | 2015-05-30 | 2022-12-08 | Equipment | 502 |  | Arrestor | P416905 | P416905 | 0 | 2015 | 2022
230126E277236 | 0221-K | After | 7.3973 | 15.6137 | 2 | Tier 3 | 2016-08-09 | 2023-01-26 | Weather | 426 | 554 | Cross Arm | P115698 | P115698 | 0 | 2016 | 2023
230222E279185 | 0079-A | After | 7.789 | 15.2219 | 3 | Tier 3 | 2016-03-19 | 2023-02-22 | Equipment | 515 | 214 | JUMPER | P273682 | P273682 | 0 | 2016 | 2023
230222E279185 | 0079-A | After | 7.789 | 15.2219 | 1 | Tier 3 | 2016-03-19 | 2023-02-22 | Equipment | 515 | 214 | JUMPER | P273682 | P273682 | 0 | 2016 | 2023
230224E279432 | 0520-G | After | 6.4356 | 16.5753 | 1 | Tier 2 | 2017-07-26 | 2023-02-24 | Third Party Contact | 710 | 532 | POLE | P325509 | P325509 | 0 | 2017 | 2023
230226E279483 | 0445-M | After | 3.7041 | 19.3068 | 2 | Tier 2 | 2020-04-18 | 2023-02-26 | Weather | 408 | 510 | Wire Slap | P41201 | P41201 | 0 | 2020 | 2023
230226E279484 | 0445-M | After | 3.7041 | 19.3068 | 2 | Tier 2 | 2020-04-18 | 2023-02-26 | Weather | 408 | 510 | Wire Slap | P41201 | P41201 | 0 | 2020 | 2023
230309E280427 | C237 PH 2 J RECONDUCTOR | After | 8.4329 | 14.5781 | 2 | Tier 3 | 2015-07-28 | 2023-03-09 | Third Party Contact | 710 | 532 | POLE | P14093 | P14093 | 0 | 2015 | 2023
230605E286408 | C79 PH 1 #O RECONDUCTOR | After | 8.1589 | 14.8521 | 2 | Tier 3 | 2015-11-05 | 2023-06-05 | Equipment | 530 | 214 | Insulator/Pin | P173223 | P173223 | 0 | 2015 | 2023
230621E287502 | 0222-PP | After | 2.1123 | 20.8986 | 2 | Tier 3 | 2021-11-20 | 2023-06-21 | Equipment | 566 |  | Disconnect | P519711 | P519711 | 0 | 2021 | 2023
230621E287502 | 0222-PP | After | 2.1123 | 20.8986 | 2 | Tier 3 | 2021-11-20 | 2023-06-21 | Equipment | 566 |  | Disconnect | P519711 | P519711 | 0 | 2021 | 2023
230621E287502 | 0222-PP | After | 2.1123 | 20.8986 | 2 | Tier 3 | 2021-11-20 | 2023-06-21 | Equipment | 566 | 218 | Disconnect | P519711 | P519711 | 0 | 2021 | 2023
230621E287502 | 0222-PP | After | 2.1123 | 20.8986 | 2 | Tier 3 | 2021-11-20 | 2023-06-21 | Equipment | 566 | 218 | Disconnect | P519711 | P519711 | 0 | 2021 | 2023
230716E289058 | 0221-A | After | 5.7425 | 17.2685 | 1 | Tier 3 | 2018-04-05 | 2023-07-16 | Equipment | 510 | 214 | Conductor, OH | P412619 | P412619 | 0 | 2018 | 2023
230716E289058 | 0221-D-VOLCAN MTN | After | 3.3205 | 19.6904 | 1 | Tier 3 | 2020-09-05 | 2023-07-16 | Equipment | 510 | 214 | Conductor, OH | P412619 | P412619 | 0 | 2020 | 2023
230815E291321 | 0078-D | After | 6.3397 | 16.6712 | 2 | Tier 3 | 2017-08-30 | 2023-08-15 | Equipment | 502 |  | Arrestor | P172679 | P172679 | 0 | 2017 | 2023
230815E291321 | 0078-D | After | 6.3397 | 16.6712 | 2 | Tier 3 | 2017-08-30 | 2023-08-15 | Equipment | 502 | 214 | Arrestor | P172679 | P172679 | 0 | 2017 | 2023
230817E291532 | 0220-C | After | 7.7342 | 15.2767 | 1 | Tier 3 | 2016-04-08 | 2023-08-17 | Foreign Object | 308 | 544 | SWITCH | P19512 | P19512 | 0 | 2016 | 2023
230820E291695 | 0212-A | After | 4.0137 | 18.9973 | 2 | Tier 2 | 2019-12-27 | 2023-08-20 | Weather | 408 | 214 | Disconnect | P19585 | P19585 | 0 | 2019 | 2023
230821E291782 | C220 PH 2 O RECONDUCTOR | After | 8.1288 | 14.8822 | 1 | Tier 3 | 2015-11-16 | 2023-08-21 | Equipment | 522 |  | FUSE | P19481 | P19481 | 0 | 2015 | 2023
230821E291782 | C220 PH 4 B POLE CHGO R3 | After | 8.6027 | 14.4082 | 2 | Tier 3 | 2015-05-27 | 2023-08-21 | Equipment | 522 |  | FUSE | P19481 | P19481 | 0 | 2015 | 2023
230918E293963 | 0237-S | After | 7.3315 | 15.6795 | 2 | Tier 2 | 2016-09-02 | 2023-09-18 | Equipment | 522 |  | FUSE | P111991 | P111991 | 0 | 2016 | 2023
231010E295870 | 0973-B | After | 7.2164 | 15.7945 | 1 | Tier 3 | 2016-10-14 | 2023-10-10 | Foreign Object | 308 | 532 | POLE | P612986 | P612986 | 0 | 2016 | 2023
231028E297174 | 0237-F | After | 7.937 | 15.074 | 1 | Tier 3 | 2016-01-25 | 2023-10-28 | Equipment | 554 | 214 | Cross Arm | P131129 | P131129 | 0 | 2016 | 2023
231115E298491 | C222 FIRE RISK MITIG PROJP | After | 10.0411 | 12.9699 | 1 | Tier 3 | 2013-12-18 | 2023-11-15 | Weather | 410 | 502 | Arrestor | P251241 | P251241 | 0 | 2013 | 2023
240109E301776 | 0217-M | After | 4.8301 | 18.1808 | 2 | Tier 2 | 2019-03-04 | 2024-01-09 | Equipment | 518 |  | Cut Out | P18659 | P18659 | 0 | 2019 | 2024
240122E302701 | C220 PH 2 M RECONDUCTOR | After | 8.1726 | 14.8384 | 1 | Tier 3 | 2015-10-31 | 2024-01-22 | Weather | 410 | 502 | Arrestor | P130985 | P130985 | 0 | 2015 | 2024
240123E302772 | 0079-M | After | 7.7753 | 15.2356 | 1 | Tier 3 | 2016-03-24 | 2024-01-23 | Equipment | 508 | 544 | SWITCH | P254129 | P254129 | 0 | 2016 | 2024
240212E304339 | 0221-A | After | 5.7425 | 17.2685 | 2 | Tier 3 | 2018-04-05 | 2024-02-12 | Equipment | 515 | 214 | JUMPER | P412620 | P412620 | 0 | 2018 | 2024
240309E306429 | 0971-E | After | 6.8164 | 16.1945 | 1 | Tier 2 | 2017-03-09 | 2024-03-09 | Equipment Failure | 518 | 214 |  | P117503 | P117503 | 0 | 2017 | 2024
210715E237971 | C1023/C354_NEW_12KV_RECON | Before | 2.0795 | 20.9315 | 2 | Tier 2 | 2021-12-02 | 2021-07-15 | Third Party Contact | 710 | 550 | TRANSFORMER | P816758 | P816758 | 1023-247 | 2021 | 2021
090705E5003 | 0212-J | Before | 2.1315 | 20.8795 | 2 | Tier 2 | 2021-11-13 | 2009-07-05 | Foreign Object | 308 | 536 | SERVICE RESTORER | P411536 | P411536 | 212-5R | 2021 | 2009
130628E20504 | 0212-W | Before | 3.6849 | 19.326 | 2 | Tier 2 | 2020-04-25 | 2013-06-28 | Equipment | 504 |  | CAP BANK | P218047 | P218047 | 212-6610CW | 2020 | 2013
020210E7501 | 0220-N | Before | 7.1836 | 15.8274 | 1 | Tier 3 | 2016-10-26 | 2002-02-10 | Weather | 412 | 510 |  | P17776 | P17776 | 220-1 | 2016 | 2002
020210E7501 | C222 FIRE RISK MITIG PRO R1 | Before | 8.9014 | 14.1096 | 1 | Tier 3 | 2015-02-07 | 2002-02-10 | Weather | 412 | 510 |  | P17776 | P17776 | 220-1 | 2015 | 2002
020210E7501 | C222 FIRE RISK MITIG PRO R1 | Before | 8.9014 | 14.1096 | 2 | Tier 3 | 2015-02-07 | 2002-02-10 | Weather | 412 | 510 |  | P17776 | P17776 | 220-1 | 2015 | 2002
240315E306974 | C220 PH 4 F POLE CHGO R2 | After | 9.0493 | 13.9616 | 1 | Tier 3 | 2014-12-15 | 2024-03-15 | Foreign Object | 308 | 550 |  | P311359 | P311359 | 220-27 | 2014 | 2024
060816E7701 | 0220-Q | Before | 6.6685 | 16.3425 | 2 | Tier 3 | 2017-05-02 | 2006-08-16 | Foreign Object | 308 | 550 | TRANSFORMER | P413693 | P413693 | 220-52 | 2017 | 2006
050714E5004 | C220 PH 2 I RECONDUCT R8 | Before | 8.3397 | 14.6712 | 1 | Tier 3 | 2015-08-31 | 2005-07-14 | Foreign Object | 308 | 550 | TRANSFORMER | P511483 | P511483 | 220-54 | 2015 | 2005
240208E304172 | 0221-A | After | 5.7425 | 17.2685 | 1 | Tier 3 | 2018-04-05 | 2024-02-08 | Weather Related |  |  |  | P412643 | P412643 | 221-152 | 2018 | 2024
110828E9902 | 0221-I | Before | 6.6247 | 16.3863 | 2 | Tier 3 | 2017-05-18 | 2011-08-28 | Equipment | 540 | 214 | REGULATOR | P100597 | P100597 | 221-212G1 | 2017 | 2011
140228E36876 | C222 PH 1 F RECONDUCTOR | Before | 7.811 | 15.2 | 2 | Tier 3 | 2016-03-11 | 2014-02-28 | Weather | 404 | 208 | SERVICE RESTORER | P227946 | P227946 | 221-31R | 2016 | 2014
140714E47175 | 0222-PP | Before | 2.1123 | 20.8986 | 2 | Tier 3 | 2021-11-20 | 2014-07-14 | Weather | 410 | 538 | SERVICE RESTORER | P519711 | P519711 | 222-7R | 2021 | 2014
140714E47175 | 0222-PP | Before | 2.1123 | 20.8986 | 2 | Tier 3 | 2021-11-20 | 2014-07-14 | Weather | 410 | 538 | SERVICE RESTORER | P519711 | P519711 | 222-7R | 2021 | 2014
201026E218739 | 0222-PP | Before | 2.1123 | 20.8986 | 2 | Tier 3 | 2021-11-20 | 2020-10-26 | SDGE/Contractor Contact | 612 | 536 | SERVICE RESTORER | P519711 | P519711 | 222-7R | 2021 | 2020
201026E218739 | 0222-PP | Before | 2.1123 | 20.8986 | 2 | Tier 3 | 2021-11-20 | 2020-10-26 | SDGE/Contractor Contact | 612 | 536 | SERVICE RESTORER | P519711 | P519711 | 222-7R | 2021 | 2020
200612E207106 | C237 PH 2 D RECONDUCT R1 | After | 8.4329 | 14.5781 | 2 | Tier 3 | 2015-07-28 | 2020-06-12 | Foreign Object | 308 | 518 | CUTOUT | P203753 | P203753 | 237-1164 | 2015 | 2020
071105E5010 | 0240-D | Before | 7.4521 | 15.5589 | 2 | Tier 3 | 2016-07-20 | 2007-11-05 | Equipment | 504 |  | CAP BANK | P875195 | P875195 | 240-790CW | 2016 | 2007
110705E5030 | C444,BU:2011 CFSP RCNDCT R8 | Before | 10.2767 | 12.7342 | 2 | Tier 2 | 2013-09-23 | 2011-07-05 | Foreign Object | 308 | 510 | OH CONDUCTOR | P42128 | P42128 | 444-3R | 2013 | 2011
120813E8123 | C444 BRANCHLN CFSP P4 R1 | Before | 8.0493 | 14.9616 | 2 | Tier 2 | 2015-12-15 | 2012-08-13 | Equipment | 552 |  | BOOSTER STA | P46574 | P46574 | 444-75B | 2015 | 2012
200724E210572 | 0445-E | After | 3.6466 | 19.3644 | 1 | Tier 2 | 2020-05-09 | 2020-07-24 | Miscellaneous | 226 |  |  | P41083 | P41083 | 445-24R | 2020 | 2020
060908E5007 | 0445-N | Before | 4.6274 | 18.3836 | 1 | Tier 2 | 2019-05-17 | 2006-09-08 | Equipment | 536 |  | SERVICE RESTORER | P41245 | P41245 | 445-3R | 2019 | 2006
060908E5007 | 0445-O | Before | 3.3397 | 19.6712 | 1 | Tier 2 | 2020-08-29 | 2006-09-08 | Equipment | 536 |  | SERVICE RESTORER | P41245 | P41245 | 445-3R | 2020 | 2006
061010E5034 | 0445-N | Before | 4.6274 | 18.3836 | 1 | Tier 2 | 2019-05-17 | 2006-10-10 | Equipment | 536 |  | SERVICE RESTORER | P41245 | P41245 | 445-3R(WEST | 2019 | 2006
061010E5034 | 0445-O | Before | 3.3397 | 19.6712 | 1 | Tier 2 | 2020-08-29 | 2006-10-10 | Equipment | 536 |  | SERVICE RESTORER | P41245 | P41245 | 445-3R(WEST | 2020 | 2006
050919E7104 | 0445-E | Before | 3.6466 | 19.3644 | 2 | Tier 2 | 2020-05-09 | 2005-09-19 | Equipment | 540 |  | REGULATOR | P161896 | P161896 | 445-613G | 2020 | 2005
060302E5012 | 0445-E | Before | 3.6466 | 19.3644 | 2 | Tier 2 | 2020-05-09 | 2006-03-02 | Equipment | 536 |  | SERVICE RESTORER | P41726 | P41726 | 445-647R | 2020 | 2006
101019E9907 | 0520-F | Before | 5.4384 | 17.5726 | 2 | Tier 2 | 2018-07-25 | 2010-10-19 | Weather | 410 | 208 | SERVICE RESTORER | P228375 | P228375 | 520-33R | 2018 | 2010
131006E27276 | 0972-C | Before | 6.8055 | 16.2055 | 2 | Tier 3 | 2017-03-13 | 2013-10-06 | Equipment | 518 | 218 | CUTOUT | P13273 | P13273 | 972-919CW | 2017 | 2013
131006E27276 | 0972-C | Before | 6.8055 | 16.2055 | 2 | Tier 3 | 2017-03-13 | 2013-10-06 | Equipment | 518 | 504 | CUTOUT | P13273 | P13273 | 972-919CW | 2017 | 2013
210927E243432 | 0222-Z | After | 6.6438 | 16.3671 | 4 | Tier 3 | 2017-05-11 | 2021-09-27 | Equipment | 512 |  | UG CABLE | P330114 | P330114 | D111986 | 2017 | 2021
201206E221925 | 0176-E | After | 6.6986 | 16.3123 | 2 | Tier 2 | 2017-04-21 | 2020-12-06 | Equipment | 512 |  | UG CABLE | P115202 | P115202 | D136723 | 2017 | 2020
140127E34337 | C1023/C354_NEW_12KV_RECON | Before | 2.0795 | 20.9315 | 1 | Tier 2 | 2021-12-02 | 2014-01-27 | Customer Contact | 702 | 512 | UG CABLE | P32537 | P32537 | D153467 | 2021 | 2014
191107E189805 | 0079-P | After | 8.0795 | 14.9315 | 1 | Tier 3 | 2015-12-04 | 2019-11-07 | Equipment | 512 |  | UG CABLE | P273610 | P273610 | D200733 | 2015 | 2019
191107E189805 | 0079-P | After | 8.0795 | 14.9315 | 1 | Tier 3 | 2015-12-04 | 2019-11-07 | Equipment | 512 | 218 | UG CABLE | P273610 | P273610 | D200733 | 2015 | 2019
180616E152189 | C73 PH 4 EPOLE CHGOUT R11 | After | 8.7041 | 14.3068 | 1 | Tier 3 | 2015-04-20 | 2018-06-16 | Equipment | 512 |  | UG CABLE | P275841 | P275841 | D2342086710 | 2015 | 2018
061117E7501 | C442 PH 4 BPOLE CHGOUT R1 | Before | 8.7342 | 14.2767 | 2 | Tier 3 | 2015-04-09 | 2006-11-17 | Equipment | 512 |  | UG CABLE | P178017 | P178017 | D2457991540 | 2015 | 2006
081005E7802 | 0176-L | Before | 2.5151 | 20.4959 | 2 | Tier 3 | 2021-06-26 | 2008-10-04 | Equipment | 512 |  | UG CABLE | P617472 | P617472 | D2982577765 | 2021 | 2008
090701E7701 | C222 FIRE RISK MITIG PRJPH | Before | 8.8877 | 14.1233 | 2 | Tier 3 | 2015-02-12 | 2009-07-01 | Equipment | 512 |  | UG CABLE | P17708 | P17708 | D3290085200 | 2015 | 2009
131001E27013 | 0908-D | Before | 4.1753 | 18.8356 | 2 | Tier 2 | 2019-10-29 | 2013-10-01 | Equipment | 512 |  | UG CABLE | P115164 | P115164 | D3923076905 | 2019 | 2013
111107E9901 | 0908-G | Before | 0.99178 | 22.0192 | 2 | Tier 2 | 2023-01-03 | 2011-11-07 | Equipment | 512 |  | UG CABLE | P213266 | P213266 | D3996076910 | 2023 | 2011
120823E5054 | 0908-G | Before | 0.99178 | 22.0192 | 2 | Tier 2 | 2023-01-03 | 2012-08-23 | Equipment | 512 |  | UG CABLE | P213271 | P213271 | D4005276959 | 2023 | 2012
210519E233865 | 0230-I | Before | 2.611 | 20.4 | 1 | Tier 2 | 2021-05-22 | 2021-05-19 | SDGE/Contractor Contact | 622 | 512 | UG CABLE | P219748 | P219748 | D4290070950 | 2021 | 2021
080712E7801 | 0230-C | Before | 4.9753 | 18.0356 | 2 | Tier 2 | 2019-01-10 | 2008-07-12 | Equipment | 512 |  | UG CABLE | P316594 | P316594 | D4401571860 | 2019 | 2008
130314E12882 | 0230-A | Before | 5.7616 | 17.2493 | 2 | Tier 2 | 2018-03-29 | 2013-03-14 | Equipment | 512 |  | UG CABLE | P513743 | P513743 | D4462070860 | 2018 | 2013
040824E7701 | 0520-C | Before | 6.3753 | 16.6356 | 1 | Tier 2 | 2017-08-17 | 2004-08-24 | Equipment | 512 |  | UG CABLE | P616732 | P616732 | D4536034400 | 2017 | 2004
021022E7501 | 0971-J | Before | 6.6027 | 16.4082 | 2 | Tier 3 | 2017-05-26 | 2002-10-22 | Equipment | 512 |  | UG CABLE | P111589 | P111589 | D7614476147 | 2017 | 2002
220725E264525 | 0212-Q | After | 1.7863 | 21.2247 | 2 | Tier 2 | 2022-03-19 | 2022-07-25 | Foreign Object | 308 | 522 | FUSE | P249968 | P249968 | F2480940 | 2022 | 2022
210324E229410 | CNF-TL629A | After | 3.2849 | 19.726 | 2 | Tier 3 | 2020-09-18 | 2021-03-24 | Equipment | 512 |  | UG CABLE | P258382 | P258382 | H135207 | 2020 | 2021
130904E24996 | C79 PH 2 R RECONDUCTOR | Before | 8.2027 | 14.8082 | 2 | Tier 3 | 2015-10-20 | 2013-09-04 | Equipment | 512 |  | UG CABLE | P870360 | P870360 | H2499786539 | 2015 | 2013
020530E5018 | 0237-C | Before | 7.4658 | 15.5452 | 2 | Tier 3 | 2016-07-15 | 2002-05-30 | Equipment | 512 |  | UG CABLE | P17649 | P17649 | H3319683711 | 2016 | 2002
101001E7801 | 0221-A | Before | 5.7425 | 17.2685 | 1 | Tier 3 | 2018-04-05 | 2010-10-01 | Equipment | 512 |  | UG CABLE | P412648 | P412648 | H3434189401 | 2018 | 2010
030830E7102 | 0215-B | Before | 5.5671 | 17.4438 | 2 | Tier 2 | 2018-06-08 | 2003-08-30 | Equipment | 512 |  | UG CABLE | P817313 | P817313 | H3944577597 | 2018 | 2003
180907E158599 | 0908-G | Before | 0.99178 | 22.0192 | 2 | Tier 2 | 2023-01-03 | 2018-09-07 | Equipment | 512 |  | UG CABLE | P213267 | P213267 | H4019076790 | 2023 | 2018
130628E20568 | CRB1 | Before | 3.0329 | 19.9781 | 2 | Tier 3 | 2020-12-19 | 2013-06-28 | Weather | 404 | 208 | SERVICE RESTORER | P610290 | P610290 | RB1-30R | 2020 | 2013
140213E35735 | CRB1 | Before | 3.0329 | 19.9781 | 2 | Tier 3 | 2020-12-19 | 2014-02-13 | Miscellaneous | 226 | 536 | SERVICE RESTORER | P610290 | P610290 | RB1-30R | 2020 | 2014
050920E5155 | 0217-P | Before | 4.7425 | 18.2685 | 2 | Tier 2 | 2019-04-05 | 2005-09-20 | Weather | 410 | 550 | TRANSFORMER | P311685 | P311685 | Sta.0217-181 | 2019 | 2005
110228E9901 | C221 PH4 D POLE REPLA R2 | Before | 7.6137 | 15.3973 | 1 | Tier 3 | 2016-05-22 | 2011-02-27 | Equipment | 502 | 510 | LIGHTNING ARRESTER | P416950 | P416950 | Sta.0221-28 | 2016 | 2011
091202E5056 | 0237-P | Before | 7.6438 | 15.3671 | 1 | Tier 2 | 2016-05-11 | 2009-12-02 | Foreign Object | 304 | 550 | TRANSFORMER | P14694 | P14694 | STA.0237-706 | 2016 | 2009
100120E7106 | 0444-A-PH-02 | Before | 2.5534 | 20.4575 | 2 | Tier 2 | 2021-06-12 | 2010-01-20 | Equipment | 550 | 214 | TRANSFORMER | P41777 | P41777 | STA.0444-140 | 2021 | 2010
100120E7106 | 0444-A-PH-02 | Before | 2.5534 | 20.4575 | 1 | Tier 2 | 2021-06-12 | 2010-01-20 | Equipment | 550 | 214 | TRANSFORMER | P41777 | P41777 | STA.0444-140 | 2021 | 2010
080708E7802 | 1030-U | Before | 6.1233 | 16.8877 | 1 | Tier 2 | 2017-11-17 | 2008-07-08 | Foreign Object | 308 | 550 | TRANSFORMER | P614962 | P614962 | STA01030-111 | 2017 | 2008
111116E5010 | 1030-U | Before | 6.1233 | 16.8877 | 2 | Tier 2 | 2017-11-17 | 2011-11-16 | Foreign Object | 308 | 550 | TRANSFORMER | P514153 | P514153 | STA01030-1147 | 2017 | 2011
160408E92805 | 1030-I | Before | 7.3753 | 15.6356 | 2 | Tier 3 | 2016-08-17 | 2016-04-08 | Foreign Object | 308 | 550 | TRANSFORMER | P615716 | P615716 | STA01030-206 | 2016 | 2016
121213E7239 | 1030-O | Before | 6.6521 | 16.3589 | 2 | Tier 3 | 2017-05-08 | 2012-12-13 | Equipment | 550 |  | TRANSFORMER | P117175 | P117175 | STA01030-564 | 2017 | 2012
070424E5054 | 1030-O | Before | 6.6521 | 16.3589 | 2 | Tier 3 | 2017-05-08 | 2007-04-24 | Equipment | 550 |  | TRANSFORMER | P117176 | P117176 | STA01030-585 | 2017 | 2007
230423E283458 | 1030-J | After | 6.1123 | 16.8986 | 2 | Tier 3 | 2017-11-21 | 2023-04-23 | Third Party Contact | 710 | 550 | TRANSFORMER | P210011 | P210011 | STA01030-602 | 2017 | 2023
060702E5005 | 1030-C | Before | 6.6521 | 16.3589 | 1 | Tier 3 | 2017-05-08 | 2006-07-02 | Foreign Object | 308 | 550 | TRANSFORMER | P610613 | P610613 | STA01030-738 | 2017 | 2006
220309E254661 | C1215 CWLONG SPAN/DESI R12 | After | 9.3041 | 13.7068 | 1 | Tier 3 | 2014-09-13 | 2022-03-09 | Foreign Object | 308 | 550 | TRANSFORMER | P40906 | P40906 | STA01215-102 | 2014 | 2022
120801E5080 | 0157-B | Before | 2.2466 | 20.7644 | 2 | Tier 3 | 2021-10-02 | 2012-08-01 | Foreign Object | 308 | 550 | TRANSFORMER | P74672 | P74672 | STA0157-1128 | 2021 | 2012
210427E232210 | 0157-B | Before | 2.2466 | 20.7644 | 1 | Tier 3 | 2021-10-02 | 2021-04-27 | Foreign Object | 308 | 550 | TRANSFORMER | P477059 | P477059 | STA0157-1145 | 2021 | 2021
061014E5034 | 0157-V | Before | 2.8027 | 20.2082 | 2 | Tier 3 | 2021-03-13 | 2006-10-14 | Foreign Object | 308 | 550 | TRANSFORMER | P271571 | P271571 | STA0157-338 | 2021 | 2006
100602E7602 | 0157-T | Before | 4.0548 | 18.9562 | 2 | Tier 3 | 2019-12-12 | 2010-06-02 | Equipment | 550 |  | TRANSFORMER | P475953 | P475953 | STA0157-841 | 2019 | 2010
181004E160561 | 0175-D | After | 6.8932 | 16.1178 | 2 | Tier 3 | 2017-02-09 | 2018-10-04 | Equipment | 550 |  | TRANSFORMER | P612459 | P612459 | STA0175-107 | 2017 | 2018
070322E7702 | 0175-B | Before | 6.7041 | 16.3068 | 1 | Tier 3 | 2017-04-19 | 2007-03-22 | Weather | 410 | 550 | TRANSFORMER | P114273 | P114273 | STA0175-16 | 2017 | 2007
150718E74018 | 0176-J | Before | 6.6274 | 16.3836 | 1 | Tier 3 | 2017-05-17 | 2015-07-18 | Weather | 410 | 550 | TRANSFORMER | P211064 | P211064 | STA0176-210 | 2017 | 2015
140228E36965 | 0176-H | Before | 4.9753 | 18.0356 | 1 | Tier 3 | 2019-01-10 | 2014-02-28 | Weather | 410 | 550 | TRANSFORMER | P613757 | P613757 | STA0176-358 | 2019 | 2014
190914E185215 | 0176-I-FT-02 | Before | 2.3068 | 20.7041 | 1 | Tier 3 | 2021-09-10 | 2019-09-14 | Foreign Object | 308 | 550 | TRANSFORMER | P610772 | P610772 | STA0176-373 | 2021 | 2019
100816E5031 | 0212-E | Before | 3.474 | 19.537 | 2 | Tier 2 | 2020-07-11 | 2010-08-16 | Foreign Object | 308 | 504 | CAP BANK | P216485 | P216485 | STA0212-247CF | 2020 | 2010
060623E7501 | 0212-I | Before | 3.6082 | 19.4027 | 2 | Tier 2 | 2020-05-23 | 2006-06-23 | Foreign Object | 304 | 550 | TRANSFORMER | P818827 | P818827 | STA0212-292 | 2020 | 2006
201017E218045 | 0212-U | Before | 2.5534 | 20.4575 | 1 | Tier 2 | 2021-06-12 | 2020-10-17 | Foreign Object | 304 | 550 | TRANSFORMER | P811482 | P811482 | STA0212-338 | 2021 | 2020
060123E5007 | 0215-A | Before | 5.5178 | 17.4932 | 1 | Tier 2 | 2018-06-26 | 2006-01-23 | Foreign Object | 308 | 550 | TRANSFORMER | P215818 | P215818 | STA0215-165 | 2018 | 2006
070108E7801 | 0215-C | Before | 4.3233 | 18.6877 | 1 | Tier 3 | 2019-09-05 | 2007-01-08 | Equipment | 550 |  | TRANSFORMER | P610672 | P610672 | STA0215-17 | 2019 | 2007
050224E5095 | 0215-B | Before | 5.5671 | 17.4438 | 1 | Tier 2 | 2018-06-08 | 2005-02-24 | Weather | 410 | 550 | TRANSFORMER | P36016 | P36016 | STA0215-712 | 2018 | 2005
160821E103302 | 0217-M | Before | 4.8301 | 18.1808 | 1 | Tier 2 | 2019-03-04 | 2016-08-21 | Equipment | 550 |  | TRANSFORMER | P515056 | P515056 | STA0217-178 | 2019 | 2016
080220E7701 | 0217-R | Before | 4.3014 | 18.7096 | 1 | Tier 2 | 2019-09-13 | 2008-02-20 | Equipment | 550 | 214 | TRANSFORMER | P14991 | P14991 | STA0217-224 | 2019 | 2008
090211E7802 | 0217-B | Before | 5.3644 | 17.6466 | 1 | Tier 2 | 2018-08-21 | 2009-02-11 | Equipment | 502 | 214 | LIGHTNING ARRESTER | P415032 | P415032 | STA0217-49 | 2018 | 2009
090125E5008 | 0217-D | Before | 4.0356 | 18.9753 | 2 | Tier 3 | 2019-12-19 | 2009-01-25 | Foreign Object | 308 | 550 | TRANSFORMER | P136241 | P136241 | STA0217-534 | 2019 | 2009
050926E7102 | 0217-H | Before | 4.7425 | 18.2685 | 1 | Tier 2 | 2019-04-05 | 2005-09-26 | Equipment | 550 |  | TRANSFORMER | P311538 | P311538 | STA0217-55 | 2019 | 2005
220621E262220 | C220 PH 2 I RECONDUCT R8 | After | 8.3397 | 14.6712 | 2 | Tier 3 | 2015-08-31 | 2022-06-21 | Foreign Object | 308 | 550 | TRANSFORMER | P212277 | P212277 | STA0220-20 | 2015 | 2022
210924E243248 | C220 PH 4 D POLE CHGOUT | After | 9.0493 | 13.9616 | 1 | Tier 3 | 2014-12-15 | 2021-09-24 | Weather | 410 | 502 | LIGHTNING ARRESTER | P219489 | P219489 | STA0220-33 | 2014 | 2021
050923E5020 | C220 PH 2 L RECONDUCT R1 | Before | 8.4521 | 14.5589 | 2 | Tier 3 | 2015-07-21 | 2005-09-23 | Equipment | 550 |  | TRANSFORMER | P212292 | P212292 | STA0220-59 | 2015 | 2005
230728E290026 | 0221-R | After | 5.4192 | 17.5918 | 2 | Tier 3 | 2018-08-01 | 2023-07-28 | Equipment | 550 |  | TRANSFORMER | P119733 | P119733 | STA0221-174 | 2018 | 2023
060903E7801 | C221 PH4 D POLE REPLA R2 | Before | 7.6137 | 15.3973 | 1 | Tier 3 | 2016-05-22 | 2006-09-03 | Weather | 410 |  | LIGHTNING ARRESTER | P416950 | P416950 | STA0221-28 | 2016 | 2006
190601E177485 | C221 PH4 D POLE REPLA R2 | After | 7.6137 | 15.3973 | 1 | Tier 3 | 2016-05-22 | 2019-06-01 | Equipment | 550 |  | TRANSFORMER | P416950 | P416950 | STA0221-28 | 2016 | 2019
210208E226035 | C221 PH4 D POLE REPLA R2 | After | 7.6137 | 15.3973 | 1 | Tier 3 | 2016-05-22 | 2021-02-08 | Equipment | 502 |  | LIGHTNING ARRESTER | P416950 | P416950 | STA0221-28 | 2016 | 2021
221011E270413 | C221 PH4 D POLE REPLA R2 | After | 7.6137 | 15.3973 | 1 | Tier 3 | 2016-05-22 | 2022-10-11 | Weather | 410 | 502 | Arrestor | P416950 | P416950 | STA0221-28 | 2016 | 2022
080919E5006 | 0221-K | Before | 7.3973 | 15.6137 | 1 | Tier 3 | 2016-08-09 | 2008-09-19 | Foreign Object | 308 | 550 | TRANSFORMER | P712166 | P712166 | Sta0221-307 | 2016 | 2008
200330E200509 | 0221-R | After | 5.4192 | 17.5918 | 1 | Tier 3 | 2018-08-01 | 2020-03-30 | Foreign Object | 308 | 550 | TRANSFORMER | P205399 | P205399 | STA0221-508 | 2018 | 2020
160920E105462 | 0221-F | Before | 5.5945 | 17.4164 | 2 | Tier 3 | 2018-05-29 | 2016-09-20 | Equipment | 550 |  | TRANSFORMER | P117927 | P117927 | STA0221-661 | 2018 | 2016
110713E9904 | 0221-Y-PH1-SLAUGHTER | Before | 5.4384 | 17.5726 | 1 | Tier 3 | 2018-07-25 | 2011-07-13 | Foreign Object | 308 | 550 | TRANSFORMER | P110715 | P110715 | STA0221-667 | 2018 | 2011
171124E136694 | 0222-EE | Before | 3.1863 | 19.8247 | 1 | Tier 3 | 2020-10-24 | 2017-11-24 | Foreign Object | 308 | 550 | TRANSFORMER | P112551 | P112551 | STA0222-401 | 2020 | 2017
060421E5038 | C222 PH4 SEC2 CPOLE CHGOU | Before | 8.6767 | 14.3342 | 2 | Tier 3 | 2015-04-30 | 2006-04-21 | Equipment | 554 |  | CROSSARM | P111079 | P111079 | STA0222-496 | 2015 | 2006
180424E148172 | 0222-FF-PH-02 | Before | 1.7863 | 21.2247 | 1 | Tier 3 | 2022-03-19 | 2018-04-24 | Foreign Object | 308 | 550 | TRANSFORMER | P612053 | P612053 | STA0222-555 | 2022 | 2018
080807E7701 | C222 PH 1 P RECONDUC R7 | Before | 8.589 | 14.4219 | 1 | Tier 3 | 2015-06-01 | 2008-08-07 | Equipment | 550 |  | TRANSFORMER | P413864 | P413864 | STA0222-60 | 2015 | 2008
180816E157045 | 0222-II | Before | 3.2438 | 19.7671 | 2 | Tier 3 | 2020-10-03 | 2018-08-16 | Foreign Object | 308 | 550 | TRANSFORMER | P217750 | P217750 | STA0222-653 | 2020 | 2018
040704E5021 | 0222-R | Before | 7.7315 | 15.2795 | 2 | Tier 3 | 2016-04-09 | 2004-07-04 | Customer Contact | 710 | 532 | POLE | P416783 | P416783 | STA0222-66 | 2016 | 2004
081121E5014 | 0230-C | Before | 4.9753 | 18.0356 | 2 | Tier 2 | 2019-01-10 | 2008-11-21 | Customer Contact | 710 | 532 | POLE | P519650 | P519650 | STA0230-1376 | 2019 | 2008
150605E70841 | 0230-B | Before | 4.9753 | 18.0356 | 2 | Tier 2 | 2019-01-10 | 2015-06-05 | Equipment | 522 |  | TRANSFORMER | P17068 | P17068 | STA0230-611 | 2019 | 2015
220307E254439 | C236 PH 2 D RECONDUCTOR | After | 7.5288 | 15.4822 | 2 | Tier 2 | 2016-06-22 | 2022-03-07 | Equipment | 550 |  | TRANSFORMER | P216162 | P216162 | STA0236-673 | 2016 | 2022
130523E18204 | 0237-O | Before | 7.5836 | 15.4274 | 3 | Tier 3 | 2016-06-02 | 2013-05-23 | Equipment | 502 | 550 | LIGHTNING ARRESTER | P211225 | P211225 | STA0237-1145 | 2016 | 2013
130408E14668 | C237 PH 2 A RECONDUCTOR | Before | 8.3671 | 14.6438 | 2 | Tier 3 | 2015-08-21 | 2013-04-08 | Foreign Object | 308 | 550 | TRANSFORMER | P116580 | P116580 | STA0237-131 | 2015 | 2013
140817E49761 | C237 PH 2 J RECONDUCTOR | Before | 8.4329 | 14.5781 | 2 | Tier 3 | 2015-07-28 | 2014-08-17 | Foreign Object | 308 | 550 | TRANSFORMER | P312944 | P312944 | STA0237-272 | 2015 | 2014
230413E282689 | 0237-G | After | 5.8384 | 17.1726 | 1 | Tier 3 | 2018-03-01 | 2023-04-13 | Foreign Object | 308 | 550 | TRANSFORMER | P115161 | P115161 | STA0237-280 | 2018 | 2023
040813E7602 | C237 PH 2 M RECONDUCTOR | Before | 8.3479 | 14.663 | 1 | Tier 3 | 2015-08-28 | 2004-08-13 | Weather | 410 | 550 | TRANSFORMER | P313103 | P313103 | STA0237-371 | 2015 | 2004
070609E5012 | 0237-O | Before | 7.5836 | 15.4274 | 2 | Tier 3 | 2016-06-02 | 2007-06-09 | Foreign Object | 308 | 502 | LIGHTNING ARRESTER | P217178 | P217178 | STA0237-993 | 2016 | 2007
140103E32713 | 0240-G | Before | 5.2493 | 17.7616 | 2 | Tier 3 | 2018-10-02 | 2014-01-03 | Foreign Object | 304 | 550 | TRANSFORMER | P475826 | P475826 | STA0240-149 | 2018 | 2014
220909E268116 | C240 PH 2 E RECONDUCT R1 | After | 8.0685 | 14.9425 | 2 | Tier 3 | 2015-12-08 | 2022-09-09 | Weather | 426 | 550 | TRANSFORMER | P272423 | P272423 | STA0240-385 | 2015 | 2022
201105E219782 | C240 PH 2 E RECONDUCT R1 | After | 8.0685 | 14.9425 | 2 | Tier 3 | 2015-12-08 | 2020-11-05 | Foreign Object | 308 | 550 | TRANSFORMER | P176372 | P176372 | STA0240-388 | 2015 | 2020
070722E7801 | 0350-D | Before | 4.0356 | 18.9753 | 1 | Tier 2 | 2019-12-19 | 2007-07-22 | Foreign Object | 308 | 550 | TRANSFORMER | P410323 | P410323 | STA0350-113 | 2019 | 2007
050422E5002 | 0350-A | Before | 5.6329 | 17.3781 | 2 | Tier 2 | 2018-05-15 | 2005-04-22 | Equipment | 550 |  | TRANSFORMER | P418717 | P418717 | STA0350-1829 | 2018 | 2005
140301E37051 | 0350-K | Before | 4.9397 | 18.0712 | 2 | Tier 2 | 2019-01-23 | 2014-03-01 | Weather | 410 | 550 | TRANSFORMER | P715914 | P715914 | STA0350242 | 2019 | 2014
020904E5002 | 0358-D | Before | 8.1534 | 14.8575 | 2 | Tier 3 | 2015-11-07 | 2002-09-04 | Equipment | 550 |  | TRANSFORMER | P377592 | P377592 | STA0358-130 | 2015 | 2002
200615E207254 | C441 PH 4 POLE REPLACE R2 | After | 9.189 | 13.8219 | 2 | Tier 3 | 2014-10-25 | 2020-06-15 | Foreign Object | 308 | 550 | TRANSFORMER | P252396 | P252396 | STA0441-295 | 2014 | 2020
200619E207812 | C441 PH 4 POLE REPLACE R2 | After | 9.189 | 13.8219 | 2 | Tier 3 | 2014-10-25 | 2020-06-19 | Foreign Object | 308 | 550 | TRANSFORMER | P252396 | P252396 | STA0441-295 | 2014 | 2020
100730E5012 | C442 PH 2 J RECONDUCT R8 | Before | 8.0438 | 14.9671 | 2 | Tier 3 | 2015-12-17 | 2010-07-30 | Foreign Object | 308 | 524 | GROUNDING BANK | P678760 | P678760 | STA0442-268GB | 2015 | 2010
121018E3650 | CNF-TL629A | Before | 3.2849 | 19.726 | 1 | Tier 3 | 2020-09-18 | 2012-10-18 | Foreign Object | 304 | 550 | TRANSFORMER | P225447 | P225447 | STA0442-329 | 2020 | 2012
210731E239266 | C442 PH 4 GPOLE CHGOUT R1 | After | 8.0712 | 14.9397 | 2 | Tier 3 | 2015-12-07 | 2021-07-31 | Weather | 410 | 550 | TRANSFORMER | P372753 | P372753 | STA0442-89 | 2015 | 2021
070913E5008 | C442 PH 4 FPOLE CHGOUT R1 | Before | 7.6575 | 15.3534 | 2 | Tier 3 | 2016-05-06 | 2007-09-13 | Foreign Object | 304 | 550 | TRANSFORMER | P173191 | P173191 | STA0442-98 | 2016 | 2007
081130E5004 | 0444-B | Before | 2.5534 | 20.4575 | 2 | Tier 2 | 2021-06-12 | 2008-11-30 | Equipment | 550 |  | TRANSFORMER | P42062 | P42062 | STA0444-100 | 2021 | 2008
051019E5020 | 0444-A | Before | 2.5589 | 20.4521 | 1 | Tier 2 | 2021-06-10 | 2005-10-19 | Equipment | 550 |  | TRANSFORMER | P42085 | P42085 | STA0444-104 | 2021 | 2005
040702E7202 | C444 BRANCHLN CFSP P4 R1 | Before | 8.0493 | 14.9616 | 2 | Tier 2 | 2015-12-15 | 2004-07-02 | Foreign Object | 308 | 550 | BOOSTER STA | P46574 | P46574 | STA0444-75B | 2015 | 2004
190719E180997 | 0445-C | After | 5.4438 | 17.5671 | 1 | Tier 2 | 2018-07-23 | 2019-07-19 | Foreign Object | 308 | 550 | TRANSFORMER | P41320 | P41320 | STA0445-104 | 2018 | 2019
190719E180997 | 0445-R | Before | 2.0164 | 20.9945 | 2 | Tier 2 | 2021-12-25 | 2019-07-19 | Foreign Object | 308 | 550 | TRANSFORMER | P41320 | P41320 | STA0445-104 | 2021 | 2019
190419E174431 | 0445-J | Before | 3.6082 | 19.4027 | 2 | Tier 2 | 2020-05-23 | 2019-04-19 | Foreign Object | 308 | 550 | TRANSFORMER | P41575 | P41575 | STA0445-132 | 2020 | 2019
130626E20366 | 0445-J | Before | 3.6082 | 19.4027 | 1 | Tier 2 | 2020-05-23 | 2013-06-26 | Foreign Object | 308 | 550 | TRANSFORMER | P41583 | P41583 | STA0445-736 | 2020 | 2013
160701E99553 | 0445-F | Before | 5.5945 | 17.4164 | 2 | Tier 2 | 2018-05-29 | 2016-07-01 | Foreign Object | 308 | 550 | TRANSFORMER | P41619 | P41619 | STA0445-783 | 2018 | 2016
050815E7102 | 0445-C | Before | 5.4438 | 17.5671 | 2 | Tier 2 | 2018-07-23 | 2005-08-15 | Weather | 410 | 550 | TRANSFORMER | P41277 | P41277 | STA0445-96 | 2018 | 2005
130506E16890 | 448QQQ | Before | 2.3644 | 20.6466 | 2 | Tier 3 | 2021-08-20 | 2013-05-06 | Foreign Object | 308 | 515 | JUMPER | P45670 | P45670 | STA0448-399 | 2021 | 2013
210409E230843 | 448W | Before | 2.4986 | 20.5123 | 1 | Tier 3 | 2021-07-02 | 2021-04-09 | Foreign Object | 308 | 218 | TRANSFORMER | P46064 | P46064 | STA0448-429 | 2021 | 2021
210409E230843 | 448W | Before | 2.4986 | 20.5123 | 1 | Tier 3 | 2021-07-02 | 2021-04-09 | Foreign Object | 308 | 550 | TRANSFORMER | P46064 | P46064 | STA0448-429 | 2021 | 2021
210409E230843 | 448X | Before | 2.5041 | 20.5068 | 1 | Tier 3 | 2021-06-30 | 2021-04-09 | Foreign Object | 308 | 218 | TRANSFORMER | P46064 | P46064 | STA0448-429 | 2021 | 2021
210409E230843 | 448X | Before | 2.5041 | 20.5068 | 1 | Tier 3 | 2021-06-30 | 2021-04-09 | Foreign Object | 308 | 550 | TRANSFORMER | P46064 | P46064 | STA0448-429 | 2021 | 2021
140405E39927 | 448S | Before | 2.0685 | 20.9425 | 2 | Tier 3 | 2021-12-06 | 2014-04-05 | Foreign Object | 308 | 515 | JUMPER | P43701 | P43701 | STA0448-452 | 2021 | 2014
090102E5081 | 448RRR | Before | 2.4384 | 20.5726 | 1 | Tier 3 | 2021-07-24 | 2009-01-02 | Equipment | 550 |  | TRANSFORMER | P207241 | P207241 | STA0448-654 | 2021 | 2009
131026E28780 | C444 BRANCHLN CFSP W/S R1 | Before | 8.6055 | 14.4055 | 1 | Tier 2 | 2015-05-26 | 2013-10-26 | Equipment | 502 | 550 | LIGHTNING ARRESTER | P41948 | P41948 | STA0470-628 | 2015 | 2013
131026E28780 | C444 BRANCHLN PH1 P41936 | Before | 8.6219 | 14.389 | 2 | Tier 2 | 2015-05-20 | 2013-10-26 | Equipment | 502 | 550 | LIGHTNING ARRESTER | P41948 | P41948 | STA0470-628 | 2015 | 2013
070623E5024 | C73 PH 4 EPOLE CHGOUT R11 | Before | 8.7041 | 14.3068 | 2 | Tier 3 | 2015-04-20 | 2007-06-23 | Foreign Object | 308 | 550 | TRANSFORMER | P275862 | P275862 | STA073-116 | 2015 | 2007
120929E1244 | C73 PH 4 CPOLE CHGOUT R11 | Before | 8.0055 | 15.0055 | 1 | Tier 3 | 2015-12-31 | 2012-09-29 | Foreign Object | 308 | 550 | TRANSFORMER | P777024 | P777024 | STA073-148 | 2015 | 2012
140803E48739 | C73 PH 4 BPOLE CHGOUT/ R5 | Before | 9.0274 | 13.9836 | 1 | Tier 3 | 2014-12-23 | 2014-08-03 | Weather | 410 | 550 | TRANSFORMER | P276319 | P276319 | STA073-467 | 2014 | 2014
120811E5074 | C78 PH4 CPOLE CHGOUT/RECO | Before | 8.7781 | 14.2329 | 2 | Tier 3 | 2015-03-24 | 2012-08-11 | Weather | 410 | 550 | TRANSFORMER | P274663 | P274663 | STA078-139 | 2015 | 2012
171021E134415 | C78 PH4 CPOLE CHGOUT/RECO | After | 8.7781 | 14.2329 | 1 | Tier 3 | 2015-03-24 | 2017-10-21 | Foreign Object | 308 | 550 | TRANSFORMER | P377761 | P377761 | STA078-215 | 2015 | 2017
150508E68739 | 0078-D | Before | 6.3397 | 16.6712 | 2 | Tier 3 | 2017-08-30 | 2015-05-08 | Foreign Object | 308 | 550 | TRANSFORMER | P172681 | P172681 | STA078-258 | 2017 | 2015
150508E68908 | 0078-D | Before | 6.3397 | 16.6712 | 2 | Tier 3 | 2017-08-30 | 2015-05-08 | Equipment | 550 |  | TRANSFORMER | P172681 | P172681 | STA078-258 | 2017 | 2015
140924E52581 | 0078-D | Before | 6.3397 | 16.6712 | 2 | Tier 3 | 2017-08-30 | 2014-09-24 | Equipment | 550 |  | TRANSFORMER | P172684 | P172684 | STA078-92 | 2017 | 2014
120717E8105 | 0079-M | Before | 7.7753 | 15.2356 | 1 | Tier 3 | 2016-03-24 | 2012-07-17 | Equipment | 550 | 214 | TRANSFORMER | P274702 | P274702 | STA079-129 | 2016 | 2012
190420E174448 | 0079-A | After | 7.789 | 15.2219 | 1 | Tier 3 | 2016-03-19 | 2019-04-20 | Foreign Object | 308 | 550 | TRANSFORMER | P273684 | P273684 | STA079-518 | 2016 | 2019
151003E80017 | 79M | Before | 0.52603 | 22.4849 | 2 | Tier 3 | 2023-06-22 | 2015-10-03 | Foreign Object | 308 | 550 | TRANSFORMER | P273569 | P273569 | STA079-595 | 2023 | 2015
170614E124441 | 0908-D | Before | 4.1753 | 18.8356 | 1 | Tier 2 | 2019-10-29 | 2017-06-14 | Foreign Object | 314 | 550 | TRANSFORMER | P115165 | P115165 | STA0908-104 | 2019 | 2017
190601E177489 | 0908-I | Before | 3.589 | 19.4219 | 1 | Tier 2 | 2020-05-30 | 2019-06-01 | Foreign Object | 308 | 550 | TRANSFORMER | P213348 | P213348 | STA0908-1112 | 2020 | 2019
070627E5031 | 0908-C | Before | 4.8959 | 18.1151 | 1 | Tier 2 | 2019-02-08 | 2007-06-27 | Foreign Object | 308 | 550 | TRANSFORMER | P118746 | P118746 | STA0908-124 | 2019 | 2007
051224E5033 | 0908-A | Before | 5.0301 | 17.9808 | 2 | Tier 2 | 2018-12-21 | 2005-12-24 | Foreign Object | 308 | 550 | TRANSFORMER | P613782 | P613782 | STA0908-653 | 2018 | 2005
160929E106291 | 0971-J | Before | 6.6027 | 16.4082 | 1 | Tier 3 | 2017-05-26 | 2016-09-29 | Foreign Object | 308 | 550 | TRANSFORMER | P112744 | P112744 | STA0971-181 | 2017 | 2016
050730E5059 | 0971-F | Before | 5.8384 | 17.1726 | 1 | Tier 3 | 2018-03-01 | 2005-07-30 | Equipment | 554 | 513 | CROSSARM | P116820 | P116820 | STA0971-196 | 2018 | 2005
160618E98585 | 0971-Q | Before | 2.074 | 20.937 | 1 | Tier 3 | 2021-12-04 | 2016-06-19 | Equipment | 550 |  | TRANSFORMER | P419355 | P419355 | STA0971-458 | 2021 | 2016
120805E5009 | 0971-Q | Before | 2.074 | 20.937 | 2 | Tier 2 | 2021-12-04 | 2012-08-05 | Foreign Object | 304 | 550 | TRANSFORMER | P513310 | P513310 | STA0971-486 | 2021 | 2012
150718E73979 | 0971-D | Before | 6.2384 | 16.7726 | 2 | Tier 3 | 2017-10-06 | 2015-07-18 | Weather | 410 | 550 | TRANSFORMER | P611658 | P611658 | STA0971-613 | 2017 | 2015
130809E23257 | 0972-C | Before | 6.8055 | 16.2055 | 2 | Tier 3 | 2017-03-13 | 2013-08-09 | Equipment | 515 | 530 | CONNECTOR | P248911 | P248911 | STA0972-911G | 2017 | 2013
160416E93383 | 0974-C | Before | 6.2274 | 16.7836 | 2 | Tier 3 | 2017-10-10 | 2016-04-16 | Equipment | 550 |  | TRANSFORMER | P378630 | P378630 | STA0974-239 | 2017 | 2016
240215E304637 | 0222-PP | After | 2.1123 | 20.8986 | 4 | Tier 3 | 2021-11-20 | 2024-02-15 | Foreign Object | 318 | 550 |  | P812040 | P812040 | STA0PE1-98 | 2021 | 2024
240215E304637 | 0222-PP | After | 2.1123 | 20.8986 | 4 | Tier 3 | 2021-11-20 | 2024-02-15 | Foreign Object | 318 | 550 |  | P812040 | P812040 | STA0PE1-98 | 2021 | 2024
240215E304637 | 0222-PP | After | 2.1123 | 20.8986 | 4 | Tier 3 | 2021-11-20 | 2024-02-15 | Foreign Object | 318 | 550 | TRANSFORMER | P812040 | P812040 | STA0PE1-98 | 2021 | 2024
240215E304637 | 0222-PP | After | 2.1123 | 20.8986 | 4 | Tier 3 | 2021-11-20 | 2024-02-15 | Foreign Object | 318 | 550 | TRANSFORMER | P812040 | P812040 | STA0PE1-98 | 2021 | 2024
180101E138960 | CRB1 | Before | 3.0329 | 19.9781 | 2 | Tier 3 | 2020-12-19 | 2018-01-01 | Equipment | 550 |  | TRANSFORMER | P17227 | P17227 | STA0RB1-87 | 2020 | 2018
210608E235143 | C222 PH 1 F RECONDUCTOR | After | 7.811 | 15.2 | 3 | Tier 3 | 2016-03-11 | 2021-06-08 | Equipment | 544 |  | SWITCH | P136612 | P136612 | SWI0374-22 | 2016 | 2021
210608E235143 | C222 PH 1 F RECONDUCTOR | After | 7.811 | 15.2 | 2 | Tier 3 | 2016-03-11 | 2021-06-08 | Equipment | 544 |  | SWITCH | P136612 | P136612 | SWI0374-22 | 2016 | 2021
180607E151560 | 0221-V | After | 7.0877 | 15.9233 | 1 | Tier 3 | 2016-11-30 | 2018-06-07 | Crew Contact | 612 | 510 | OH CONDUCTOR | P717419 | P717419 | P257235 | 2016 | 2018
170721E127174 | 0520-B | Before | 6.3534 | 16.6575 | 1 | Tier 2 | 2017-08-25 | 2017-07-21 | Crew Contact | 632 | 510 | OH CONDUCTOR | P311990 | P311990 | P311992 | 2017 | 2017
090727E7701 | 0520-L | Before | 5.5671 | 17.4438 | 1 | Tier 2 | 2018-06-08 | 2009-07-27 | Crew Contact | 632 | 513 | CONNECTOR | P119033 | P119033 | P119034 | 2018 | 2009
101014E7803 | 1030-F | Before | 6.3726 | 16.6384 | 1 | Tier 3 | 2017-08-18 | 2010-10-14 | Crew Contact | 612 | 510 | OH CONDUCTOR | P203334 | P203334 | P212405 | 2017 | 2010
091128E5007 | C1023/C354_NEW_12KV_RECON | Before | 2.0795 | 20.9315 | 1 | Tier 2 | 2021-12-02 | 2009-11-28 | Crew Contact | 612 | 513 | OH CONDUCTOR | P418476 | P418476 | P512095 | 2021 | 2009
140615E45061 | 0157-G | Before | 2.5726 | 20.4384 | 1 | Tier 3 | 2021-06-05 | 2014-06-15 | Customer Contact | 702 | 510 | OH CONDUCTOR | P176095 | P176095 | P176094 | 2021 | 2014
041122E5035 | 0157-W | Before | 3.8384 | 19.1726 | 1 | Tier 3 | 2020-02-29 | 2004-11-22 | Customer Contact | 710 | 526 | OH CONDUCTOR | P474547 | P474547 | P474548 | 2020 | 2004
051116E5065 | 0157-W | Before | 3.8384 | 19.1726 | 1 | Tier 3 | 2020-02-29 | 2005-11-16 | Customer Contact | 702 | 513 | OH CONDUCTOR | P477375 | P477375 | P573516 | 2020 | 2005
070213E5055 | 0157-W | Before | 3.8384 | 19.1726 | 1 | Tier 3 | 2020-02-29 | 2007-02-13 | Customer Contact | 710 | 526 | GUY WIRE | P474547 | P474547 | P474548 | 2020 | 2007
110205E5044 | 0157-W | Before | 3.8384 | 19.1726 | 1 | Tier 3 | 2020-02-29 | 2011-02-05 | Customer Contact | 710 | 532 | POLE | P172225 | P172225 | P477375 | 2020 | 2011
150218E62627 | 0157-W | Before | 3.8384 | 19.1726 | 1 | Tier 3 | 2020-02-29 | 2015-02-18 | Customer Contact | 710 | 532 | POLE | P474547 | P474547 | P172225 | 2020 | 2015
120216E7601 | 0157-X | Before | 1.6986 | 21.3123 | 1 | Tier 3 | 2022-04-20 | 2012-02-15 | Customer Contact | 710 | 532 | POLE | P770762 | P770762 | P770306 | 2022 | 2012
130806E23022 | 0176-H | Before | 4.9753 | 18.0356 | 1 | Tier 3 | 2019-01-10 | 2013-08-06 | Customer Contact | 710 | 532 | POLE | P36362 | P36362 | P114967 | 2019 | 2013
180126E141026 | 0215-A | Before | 5.5178 | 17.4932 | 1 | Tier 2 | 2018-06-26 | 2018-01-26 | Customer Contact | 710 | 513 | OH CONDUCTOR | P211163 | P211163 | P211164 | 2018 | 2018
050908E7102 | 0217-K | Before | 4.7425 | 18.2685 | 1 | Tier 2 | 2019-04-05 | 2005-09-08 | Customer Contact | 710 | 510 | OH CONDUCTOR | P411356 | P411356 | P411357 | 2019 | 2005
061025E7802 | 0222-K | Before | 7.4658 | 15.5452 | 1 | Tier 3 | 2016-07-15 | 2006-10-25 | Customer Contact | 710 | 532 | POLE | P17684 | P17684 | P17682 | 2016 | 2006
150107E59579 | 0230-D | Before | 4.9342 | 18.0767 | 1 | Tier 2 | 2019-01-25 | 2015-01-07 | Customer Contact | 710 | 532 | POLE | P416259 | P416259 | P416258 | 2019 | 2015
110305E5073 | 0237-Q | Before | 7.5836 | 15.4274 | 1 | Tier 2 | 2016-06-02 | 2011-03-05 | Customer Contact | 710 | 532 | POLE | P418825 | P418825 | P19278 | 2016 | 2011
151118E83153 | 0445-U | Before | 4.3041 | 18.7068 | 1 | Tier 2 | 2019-09-12 | 2015-11-18 | Customer Contact | 702 | 513 | OH CONDUCTOR | P41897 | P41897 | P44952 | 2019 | 2015
190906E184668 | 0908-E | Before | 4.3041 | 18.7068 | 1 | Tier 2 | 2019-09-12 | 2019-09-06 | Customer Contact | 710 | 532 | POLE | P512396 | P512396 | P114616 | 2019 | 2019
050107E8203 | 0971-G | Before | 6.7096 | 16.3014 | 1 | Tier 3 | 2017-04-17 | 2005-01-07 | Customer Contact | 710 | 532 | POLE | P111562 | P111562 | P111563 | 2017 | 2005
061227E5022 | 0974-C | Before | 6.2274 | 16.7836 | 1 | Tier 3 | 2017-10-10 | 2006-12-27 | Customer Contact | 710 | 526 | GUY WIRE | P378630 | P378630 | P378632 | 2017 | 2006
150816E76296 | 0974-C | Before | 6.2274 | 16.7836 | 1 | Tier 3 | 2017-10-10 | 2015-08-16 | Customer Contact | 710 | 513 | OH CONDUCTOR | P672626 | P672626 | P378640 | 2017 | 2015
160407E92648 | 0974-C | Before | 6.2274 | 16.7836 | 1 | Tier 3 | 2017-10-10 | 2016-04-07 | Customer Contact | 710 | 532 | POLE | P192958 | P192958 | P165337 | 2017 | 2016
031114E5046 | 1030-C | Before | 6.6521 | 16.3589 | 1 | Tier 3 | 2017-05-08 | 2003-11-14 | Customer Contact | 702 | 510 | OH CONDUCTOR | P112206 | P112206 | P112347 | 2017 | 2003
090529E7801 | 1030-J | Before | 6.1123 | 16.8986 | 1 | Tier 3 | 2017-11-21 | 2009-05-29 | Customer Contact | 710 | 513 | OH CONDUCTOR | P114924 | P114924 | P816321 | 2017 | 2009
080804E7703 | C236 PH 2 C RECONDUCTOR | Before | 7.6603 | 15.3507 | 1 | Tier 3 | 2016-05-05 | 2008-08-04 | Customer Contact | 702 | 513 | OH CONDUCTOR | P112776 | P112776 | P112778 | 2016 | 2008
080804E7703 | C236 PH 2 D RECONDUCTOR | Before | 7.5288 | 15.4822 | 1 | Tier 3 | 2016-06-22 | 2008-08-04 | Customer Contact | 702 | 513 | OH CONDUCTOR | P112776 | P112776 | P112778 | 2016 | 2008
140324E38861 | C442 PH 4 EPOLE CHGOUT R7 | Before | 9.2082 | 13.8027 | 1 | Tier 3 | 2014-10-18 | 2014-03-24 | Customer Contact | 710 | 532 | POLE | P774670 | P774670 | P774671 | 2014 | 2014
101008E5006 | CRA1 PH 2 A RECONDUCTOR | Before | 8.2603 | 14.7507 | 1 | Tier 2 | 2015-09-29 | 2010-10-08 | Customer Contact | 710 | 532 | POLE | P115628 | P115628 | P115629 | 2015 | 2010
170327E124154 | 0078-G | Before | 6.337 | 16.674 | 1 | Tier 3 | 2017-08-31 | 2017-03-27 | Equipment | 513 | 314 | OH CONDUCTOR | P202826 | P202826 | P176556 | 2017 | 2017
031205E5048 | 0079-A | Before | 7.789 | 15.2219 | 1 | Tier 3 | 2016-03-19 | 2003-12-05 | Equipment | 513 |  | OH CONDUCTOR | P273665 | P273665 | P273667 | 2016 | 2003
031123E7801 | 0079-P | Before | 8.0795 | 14.9315 | 1 | Tier 3 | 2015-12-04 | 2003-11-23 | Equipment | 554 |  | CROSSARM | P778295 | P778295 | P778296 | 2015 | 2003
190507E175374 | 0157-D | Before | 2.2466 | 20.7644 | 1 | Tier 3 | 2021-10-02 | 2019-05-07 | Equipment | 532 |  | POLE | P74730 | P74730 | P74736 | 2021 | 2019
190615E178503 | 0157-D | Before | 2.2466 | 20.7644 | 1 | Tier 3 | 2021-10-02 | 2019-06-15 | Equipment | 513 |  | OH CONDUCTOR | P376680 | P376680 | P102829 | 2021 | 2019
190615E178503 | 0157-D | Before | 2.2466 | 20.7644 | 1 | Tier 3 | 2021-10-02 | 2019-06-15 | Equipment | 513 |  | OH CONDUCTOR | P376680 | P376680 | P102829 | 2021 | 2019
100822E7602 | 0157-G | Before | 2.5726 | 20.4384 | 1 | Tier 3 | 2021-06-05 | 2010-08-22 | Equipment | 513 | 515 | OH CONDUCTOR | P176094 | P176094 | P176095 | 2021 | 2010
110516E7601 | 0157-H | Before | 3.3014 | 19.7096 | 1 | Tier 3 | 2020-09-12 | 2011-05-16 | Equipment | 513 | 208 | OH CONDUCTOR | P175939 | P175939 | P676351 | 2020 | 2011
071202E5031 | 0176-A | Before | 6.7397 | 16.2712 | 1 | Tier 3 | 2017-04-06 | 2007-12-02 | Equipment | 513 |  | OH CONDUCTOR | P217599 | P217599 | P217600 | 2017 | 2007
071130E5011 | 0176-D | Before | 4.9753 | 18.0356 | 1 | Tier 3 | 2019-01-10 | 2007-11-30 | Equipment | 513 | 554 | OH CONDUCTOR | P115212 | P115212 | P418974 | 2019 | 2007
030101E5001 | 0212-B | Before | 4.0137 | 18.9973 | 1 | Tier 3 | 2019-12-27 | 2003-01-01 | Equipment | 513 |  | OH CONDUCTOR | P19531 | P19531 | P19532 | 2019 | 2003
030126E5007 | 0212-B | Before | 4.0137 | 18.9973 | 1 | Tier 3 | 2019-12-27 | 2003-01-26 | Equipment | 513 | 532 | OH CONDUCTOR | P19533 | P19533 | P19531 | 2019 | 2003
161216E111711 | 0212-B | Before | 4.0137 | 18.9973 | 1 | Tier 3 | 2019-12-27 | 2016-12-16 | Equipment | 510 |  | OH CONDUCTOR | P19530 | P19530 | P19529 | 2019 | 2016
040211E5002 | 0212-C-PH-02 | Before | 3.0904 | 19.9205 | 1 | Tier 3 | 2020-11-28 | 2004-02-11 | Equipment | 513 |  | OH CONDUCTOR | P112473 | P112473 | P112479 | 2020 | 2004
040211E5002 | 0212-C-PH-02 | Before | 3.0904 | 19.9205 | 1 | Tier 3 | 2020-11-28 | 2004-02-11 | Equipment | 513 |  | OH CONDUCTOR | P112473 | P112473 | P112479 | 2020 | 2004
190223E170324 | 0212-D | Before | 3.2822 | 19.7288 | 1 | Tier 3 | 2020-09-19 | 2019-02-23 | Equipment | 554 | 218 | CROSSARM | P317943 | P317943 | P317945 | 2020 | 2019
190223E170324 | 0212-D | Before | 3.2822 | 19.7288 | 1 | Tier 3 | 2020-09-19 | 2019-02-23 | Equipment | 554 | 513 | CROSSARM | P317943 | P317943 | P317945 | 2020 | 2019
090519E5051 | 0212-W | Before | 3.6849 | 19.326 | 1 | Tier 2 | 2020-04-25 | 2009-05-19 | Equipment | 515 | 513 | JUMPER | P218050 | P218050 | P218051 | 2020 | 2009
070921E7801 | 0217-E | Before | 4.0356 | 18.9753 | 1 | Tier 3 | 2019-12-19 | 2007-09-21 | Equipment | 513 |  | OH CONDUCTOR | P214799 | P214799 | P214800 | 2019 | 2007
130113E8876 | 0217-E | Before | 4.0356 | 18.9753 | 1 | Tier 3 | 2019-12-19 | 2013-01-13 | Equipment | 513 |  | OH CONDUCTOR | P214804 | P214804 | P217690 | 2019 | 2013
130113E8876 | 0217-E | Before | 4.0356 | 18.9753 | 1 | Tier 3 | 2019-12-19 | 2013-01-13 | Equipment | 513 |  | OH CONDUCTOR | P214804 | P214804 | P217690 | 2019 | 2013
120320E9901 | 0217-M | Before | 4.8301 | 18.1808 | 1 | Tier 2 | 2019-03-04 | 2012-03-20 | Equipment | 515 | 513 | CONNECTOR | P18659 | P18659 | P214133 | 2019 | 2012
090204E7801 | 0217-V | Before | 4.0329 | 18.9781 | 1 | Tier 2 | 2019-12-20 | 2009-02-04 | Equipment | 513 |  | OH CONDUCTOR | P213431 | P213431 | P19162 | 2019 | 2009
160107E85643 | 0221-A | Before | 5.7425 | 17.2685 | 1 | Tier 3 | 2018-04-05 | 2016-01-07 | Equipment | 513 |  | OH CONDUCTOR | P412625 | P412625 | P412626 | 2018 | 2016
160307E90203 | 0221-A | Before | 5.7425 | 17.2685 | 1 | Tier 3 | 2018-04-05 | 2016-03-07 | Equipment | 513 |  | OH CONDUCTOR | P412626 | P412626 | P412625 | 2018 | 2016
160329E91929 | 0221-A | Before | 5.7425 | 17.2685 | 1 | Tier 3 | 2018-04-05 | 2016-03-29 | Equipment | 513 |  | OH CONDUCTOR | P412626 | P412626 | P412625 | 2018 | 2016
110531E9902 | 0221-J | Before | 7.0055 | 16.0055 | 1 | Tier 3 | 2016-12-30 | 2011-05-31 | Equipment | 530 | 214 | CONNECTOR | P115684 | P115684 | P115686 | 2016 | 2011
131201E30934 | 0221-O | Before | 5.6466 | 17.3644 | 1 | Tier 3 | 2018-05-10 | 2013-12-01 | Equipment | 532 | 513 | POLE | P116279 | P116279 | P616116 | 2018 | 2013
131008E27441 | 0222-CC | Before | 3.4055 | 19.6055 | 1 | Tier 3 | 2020-08-05 | 2013-10-08 | Equipment | 515 | 513 | CONNECTOR | P17727 | P17727 | P17726 | 2020 | 2013
030610E5044 | 0222-N | Before | 7.3616 | 15.6493 | 1 | Tier 3 | 2016-08-22 | 2003-06-10 | Equipment | 515 | 513 | OH CONDUCTOR | P214038 | P214038 | P111819 | 2016 | 2003
130106E8388 | 0230-B | Before | 4.9753 | 18.0356 | 1 | Tier 2 | 2019-01-10 | 2013-01-06 | Equipment | 513 |  | OH CONDUCTOR | P316588 | P316588 | P517425 | 2019 | 2013
180402E146380 | 0230-B | Before | 4.9753 | 18.0356 | 1 | Tier 2 | 2019-01-10 | 2018-04-02 | Equipment | 516 | 513 | DEADEND | P316588 | P316588 | P316589 | 2019 | 2018
130106E8388 | 0230-C | Before | 4.9753 | 18.0356 | 1 | Tier 2 | 2019-01-10 | 2013-01-06 | Equipment | 513 |  | OH CONDUCTOR | P316588 | P316588 | P517425 | 2019 | 2013
180402E146380 | 0230-C | Before | 4.9753 | 18.0356 | 1 | Tier 2 | 2019-01-10 | 2018-04-02 | Equipment | 516 | 513 | DEADEND | P316588 | P316588 | P316589 | 2019 | 2018
051211E5006 | 0445-D | Before | 5.2603 | 17.7507 | 1 | Tier 2 | 2018-09-28 | 2005-12-11 | Equipment | 513 | 206 | OH CONDUCTOR | P41860 | P41860 | P41861 | 2018 | 2005
150901E77579 | 0445-K | Before | 4.6932 | 18.3178 | 1 | Tier 2 | 2019-04-23 | 2015-09-01 | Equipment | 513 | 214 | OH CONDUCTOR | P41145 | P41145 | P41146 | 2019 | 2015
050323E7103 | 0445-M | Before | 3.7041 | 19.3068 | 1 | Tier 2 | 2020-04-18 | 2005-03-23 | Equipment | 513 |  | OH CONDUCTOR | P41201 | P41201 | P41202 | 2020 | 2005
110111E5007 | 0445-Q | Before | 2.0356 | 20.9753 | 1 | Tier 2 | 2021-12-18 | 2011-01-11 | Equipment | 513 | 515 | OH CONDUCTOR | P41411 | P41411 | P41382 | 2021 | 2011
140627E45946 | 0520-I | Before | 5.8767 | 17.1342 | 1 | Tier 2 | 2018-02-15 | 2014-06-27 | Equipment | 515 | 513 | CONNECTOR | P216017 | P216017 | P216018 | 2018 | 2014
130422E15853 | 0908-G | Before | 0.99178 | 22.0192 | 1 | Tier 2 | 2023-01-03 | 2013-04-22 | Equipment | 513 | 214 | OH CONDUCTOR | P115832 | P115832 | P716003 | 2023 | 2013
191120E191010 | 0908-G | Before | 0.99178 | 22.0192 | 1 | Tier 2 | 2023-01-03 | 2019-11-20 | Equipment | 513 |  | OH CONDUCTOR | P115835 | P115835 | P163664 | 2023 | 2019
090906E7801 | 0971-C | Before | 6.2384 | 16.7726 | 1 | Tier 3 | 2017-10-06 | 2009-09-06 | Equipment | 513 |  | OH CONDUCTOR | P116556 | P116556 | P116557 | 2017 | 2009
030626E5065 | 1030-D | Before | 4.2849 | 18.726 | 1 | Tier 3 | 2019-09-19 | 2003-06-26 | Equipment | 513 |  | OH CONDUCTOR | P113860 | P113860 | P113859 | 2019 | 2003
130506E16791 | 1030-N | Before | 6.3836 | 16.6274 | 1 | Tier 3 | 2017-08-14 | 2013-05-06 | Equipment | 515 | 513 | CONNECTOR | P117524 | P117524 | P117525 | 2017 | 2013
070930E7702 | 1030-U | Before | 6.1233 | 16.8877 | 1 | Tier 2 | 2017-11-17 | 2007-09-30 | Equipment | 513 |  | OH CONDUCTOR | P211295 | P211295 | P211296 | 2017 | 2007
020812E7202 | 1458-B | Before | 6.6219 | 16.389 | 1 | Tier 2 | 2017-05-19 | 2002-08-12 | Equipment | 513 |  | OH CONDUCTOR | P573907 | P573907 | P174839 | 2017 | 2002
020812E7203 | 1458-B | Before | 6.6219 | 16.389 | 1 | Tier 2 | 2017-05-19 | 2002-08-12 | Equipment | 513 |  | OH CONDUCTOR | P573907 | P573907 | P174839 | 2017 | 2002
191010E187219 | 448NNN | Before | 2.4055 | 20.6055 | 1 | Tier 3 | 2021-08-05 | 2019-10-10 | Equipment | 513 |  | CONNECTOR | P43500 | P43500 | P43501 | 2021 | 2019
190314E171590 | C221:ERI 2012 REBUILD IM R9 | After | 10.1945 | 12.8164 | 1 | Tier 3 | 2013-10-23 | 2019-03-14 | Equipment | 528 |  | MISC EQUIPMENT | P18540 | P18540 | P18541 | 2013 | 2019
131008E27441 | C222 FIRE RISK MITIG PRJPH | Before | 8.8877 | 14.1233 | 1 | Tier 3 | 2015-02-12 | 2013-10-08 | Equipment | 515 | 513 | CONNECTOR | P17727 | P17727 | P17726 | 2015 | 2013
131008E27441 | C222 FIRE RISK MITIG PROJP | Before | 8.8877 | 14.1233 | 1 | Tier 3 | 2015-02-12 | 2013-10-08 | Equipment | 515 | 513 | CONNECTOR | P17727 | P17727 | P17726 | 2015 | 2013
131008E27441 | C222 PH 1 H RECONDUC R1 | Before | 8.1479 | 14.863 | 1 | Tier 3 | 2015-11-09 | 2013-10-08 | Equipment | 515 | 513 | CONNECTOR | P17727 | P17727 | P17726 | 2015 | 2013
070528E7702 | C222 PH4 SEC2 CPOLE CHGOU | Before | 8.6767 | 14.3342 | 1 | Tier 3 | 2015-04-30 | 2007-05-28 | Equipment | 513 | 214 | OH CONDUCTOR | P111081 | P111081 | P111077 | 2015 | 2007
081004E7801 | C237 PH 2 D RECONDUCT R1 | Before | 8.4329 | 14.5781 | 1 | Tier 3 | 2015-07-28 | 2008-10-04 | Equipment | 510 |  | OH CONDUCTOR | P17619 | P17619 | P17620 | 2015 | 2008
121231E8025 | C239:2013 RIRAT RELIABILITY | Before | 8.4356 | 14.5753 | 1 | Tier 3 | 2015-07-27 | 2012-12-31 | Equipment | 515 | 513 | CONNECTOR | P218931 | P218931 | P519397 | 2015 | 2012
150211E62272 | C442 PH 4 HPOLE CHGOUT/RE | Before | 8.3973 | 14.6137 | 1 | Tier 3 | 2015-08-10 | 2015-02-11 | Equipment | 513 |  | OH CONDUCTOR | P273284 | P273284 | P273285 | 2015 | 2015
030112E7107 | C444 BRANCHLN CFSP P4 R1 | Before | 8.0493 | 14.9616 | 1 | Tier 2 | 2015-12-15 | 2003-01-12 | Equipment | 513 |  | OH CONDUCTOR | P41976 | P41976 | P41977 | 2015 | 2003
091227E7601 | C444 BRANCHLN CFSP P4 R1 | Before | 8.0493 | 14.9616 | 1 | Tier 2 | 2015-12-15 | 2009-12-27 | Equipment | 513 |  | OH CONDUCTOR | P41967 | P41967 | P41968 | 2015 | 2009
100320E7601 | C444 BRANCHLN CFSP P4 R1 | Before | 8.0493 | 14.9616 | 1 | Tier 2 | 2015-12-15 | 2010-03-20 | Equipment | 513 |  | OH CONDUCTOR | P41967 | P41967 | P41968 | 2015 | 2010
130913E25788 | C444 BRANCHLN CFSP P4 R1 | Before | 8.0493 | 14.9616 | 1 | Tier 2 | 2015-12-15 | 2013-09-13 | Equipment | 528 | 513 | MISC EQUIPMENT | P41967 | P41967 | P41968 | 2015 | 2013
091227E7601 | C444 BRANCHLN PH2 P4196 R1 | Before | 8.7836 | 14.2274 | 1 | Tier 2 | 2015-03-22 | 2009-12-27 | Equipment | 513 |  | OH CONDUCTOR | P41967 | P41967 | P41968 | 2015 | 2009
100320E7601 | C444 BRANCHLN PH2 P4196 R1 | Before | 8.7836 | 14.2274 | 1 | Tier 2 | 2015-03-22 | 2010-03-20 | Equipment | 513 |  | OH CONDUCTOR | P41967 | P41967 | P41968 | 2015 | 2010
130913E25788 | C444 BRANCHLN PH2 P4196 R1 | Before | 8.7836 | 14.2274 | 1 | Tier 2 | 2015-03-22 | 2013-09-13 | Equipment | 528 | 513 | MISC EQUIPMENT | P41967 | P41967 | P41968 | 2015 | 2013
090110E7601 | C79 FIRE RISK MITIGATION R2 | Before | 8.4658 | 14.5452 | 1 | Tier 3 | 2015-07-16 | 2009-01-10 | Equipment | 530 | 510 | OH CONDUCTOR | P275363 | P275363 | P275364 | 2015 | 2009
140326E39201 | C79 FIRE RISK MITIGATION R2 | Before | 8.4658 | 14.5452 | 1 | Tier 3 | 2015-07-16 | 2014-03-26 | Equipment | 513 | 214 | OH CONDUCTOR | P275376 | P275376 | P275377 | 2015 | 2014
230228E279685 | 0221-A | After | 5.7425 | 17.2685 | 1 | Tier 3 | 2018-04-05 | 2023-03-02 | Equipment | 515 | 214 | JUMPER | P412622 | P412622 | P412623 | 2018 | 2023
100227E5065 | 0157-H | Before | 3.3014 | 19.7096 | 1 | Tier 3 | 2020-09-12 | 2010-02-27 | Foreign Object | 308 | 513 | OH CONDUCTOR | P175942 | P175942 | P175943 | 2020 | 2010
040805E5007 | 0176-D | Before | 4.9753 | 18.0356 | 1 | Tier 3 | 2019-01-10 | 2004-08-05 | Foreign Object | 308 | 510 | OH CONDUCTOR | P115206 | P115206 | P716206 | 2019 | 2004
190314E171666 | 0176-F | After | 5.3562 | 17.6548 | 1 | Tier 3 | 2018-08-24 | 2019-03-14 | Foreign Object | 315 | 510 | OH CONDUCTOR | P215732 | P215732 | P215733 | 2018 | 2019
120202E7801 | 0212-A | Before | 4.0137 | 18.9973 | 1 | Tier 2 | 2019-12-27 | 2012-02-02 | Foreign Object | 315 | 513 | OH CONDUCTOR | P19557 | P19557 | P19556 | 2019 | 2012
121218E7497 | 0212-A | Before | 4.0137 | 18.9973 | 1 | Tier 2 | 2019-12-27 | 2012-12-18 | Foreign Object | 308 | 513 | OH CONDUCTOR | P19568 | P19568 | P19570 | 2019 | 2012
011024E5003 | 0212-B | Before | 4.0137 | 18.9973 | 1 | Tier 3 | 2019-12-27 | 2001-10-24 | Foreign Object | 308 |  |  | P19521 | P19521 | P19522 | 2019 | 2001
021209E5004 | 0212-B | Before | 4.0137 | 18.9973 | 1 | Tier 3 | 2019-12-27 | 2002-12-09 | Foreign Object | 308 | 513 | OH CONDUCTOR | P19529 | P19529 | P19530 | 2019 | 2002
070415E5004 | 0212-B | Before | 4.0137 | 18.9973 | 1 | Tier 3 | 2019-12-27 | 2007-04-15 | Foreign Object | 308 | 510 | OH CONDUCTOR | P19533 | P19533 | P19529 | 2019 | 2007
161220E111926 | 0212-B | Before | 4.0137 | 18.9973 | 1 | Tier 3 | 2019-12-27 | 2016-12-20 | Foreign Object | 308 | 513 | OH CONDUCTOR | P19530 | P19530 | P19529 | 2019 | 2016
181126E164103 | 0212-B | Before | 4.0137 | 18.9973 | 1 | Tier 3 | 2019-12-27 | 2018-11-26 | Foreign Object | 304 | 510 | OH CONDUCTOR | P19522 | P19522 | P19523 | 2019 | 2018
110208E7501 | 0212-C-PH-02 | Before | 3.0904 | 19.9205 | 1 | Tier 3 | 2020-11-28 | 2011-02-08 | Foreign Object | 308 | 513 | OH CONDUCTOR | P112474 | P112474 | P112475 | 2020 | 2011
050220E5005 | 0212-C-PH-03 | Before | 3.0904 | 19.9205 | 1 | Tier 3 | 2020-11-28 | 2005-02-20 | Foreign Object | 308 | 513 | OH CONDUCTOR | P112500 | P112500 | P112499 | 2020 | 2005
050220E5005 | 0212-D | Before | 3.0904 | 19.9205 | 1 | Tier 3 | 2020-11-28 | 2005-02-20 | Foreign Object | 308 | 513 | OH CONDUCTOR | P112500 | P112500 | P112499 | 2020 | 2005
060103E5007 | 0212-D | Before | 3.2822 | 19.7288 | 1 | Tier 3 | 2020-09-19 | 2006-01-03 | Foreign Object | 308 | 510 | OH CONDUCTOR | P112502 | P112502 | P112503 | 2020 | 2006
200723E210343 | 0212-D | Before | 3.2822 | 19.7288 | 1 | Tier 3 | 2020-09-19 | 2020-07-23 | Foreign Object | 314 | 510 | OH CONDUCTOR | P112510 | P112510 | P112511 | 2020 | 2020
210705E237157 | 0212-E | After | 3.474 | 19.537 | 1 | Tier 2 | 2020-07-11 | 2021-07-05 | Foreign Object | 315 | 510 | OH CONDUCTOR | P216460 | P216460 | P216461 | 2020 | 2021
170406E119723 | 0212-E | Before | 3.474 | 19.537 | 1 | Tier 2 | 2020-07-11 | 2017-04-06 | Foreign Object | 315 | 513 | OH CONDUCTOR | P216503 | P216503 | P216504 | 2020 | 2017
180522E150424 | 0217-C | After | 5.8384 | 17.1726 | 1 | Tier 3 | 2018-03-01 | 2018-05-22 | Foreign Object | 315 | 510 | OH CONDUCTOR | P214790 | P214790 | P214791 | 2018 | 2018
090525E5001 | 0220-C | Before | 7.7342 | 15.2767 | 1 | Tier 3 | 2016-04-08 | 2009-05-25 | Foreign Object | 308 | 513 | OH CONDUCTOR | P19500 | P19500 | P19501 | 2016 | 2009
051011E5027 | 0222-JJ | Before | 3.2247 | 19.7863 | 1 | Tier 3 | 2020-10-10 | 2005-10-11 | Foreign Object | 308 | 513 | OH CONDUCTOR | P117680 | P117680 | P117681 | 2020 | 2005
190602E177510 | 0222-U | After | 7.4384 | 15.5726 | 1 | Tier 3 | 2016-07-25 | 2019-06-02 | Foreign Object | 308 | 510 | OH CONDUCTOR | P311742 | P311742 | P311743 | 2016 | 2019
081018E7801 | 0222-U | Before | 7.4384 | 15.5726 | 1 | Tier 3 | 2016-07-25 | 2008-10-18 | Foreign Object | 308 | 510 | OH CONDUCTOR | P311744 | P311744 | P311743 | 2016 | 2008
131111E29755 | 0222-U | Before | 7.4384 | 15.5726 | 1 | Tier 3 | 2016-07-25 | 2013-11-11 | Foreign Object | 308 | 510 | OH CONDUCTOR | P311742 | P311742 | P311743 | 2016 | 2013
130913E25750 | 0350-D | Before | 4.0356 | 18.9753 | 1 | Tier 2 | 2019-12-19 | 2013-09-13 | Foreign Object | 310 | 513 | OH CONDUCTOR | P410320 | P410320 | P410321 | 2019 | 2013
230126E277182 | 0442-I | After | 1.3973 | 21.6137 | 1 | Tier 3 | 2022-08-08 | 2023-01-26 | Foreign Object | 322 | 513 | Conductor, OH | P173166 | P173166 | P173165 | 2022 | 2023
160401E92271 | 0520-C | Before | 6.3753 | 16.6356 | 1 | Tier 2 | 2017-08-17 | 2016-04-01 | Foreign Object | 308 | 513 | OH CONDUCTOR | P216105 | P216105 | P216106 | 2017 | 2016
061225E5013 | 0520-F | Before | 5.4384 | 17.5726 | 1 | Tier 2 | 2018-07-25 | 2006-12-25 | Foreign Object | 310 | 513 | OH CONDUCTOR | P512485 | P512485 | P512484 | 2018 | 2006
160711E100064 | 0520-H | Before | 5.8767 | 17.1342 | 1 | Tier 2 | 2018-02-15 | 2016-07-11 | Foreign Object | 314 | 510 | OH CONDUCTOR | P228931 | P228931 | P228932 | 2018 | 2016
170819E129301 | 0908-G | Before | 0.99178 | 22.0192 | 1 | Tier 2 | 2023-01-03 | 2017-08-19 | Foreign Object | 315 | 510 | OH CONDUCTOR | P817115 | P817115 | P213271 | 2023 | 2017
100807E7701 | 0971-J | Before | 6.6027 | 16.4082 | 1 | Tier 3 | 2017-05-26 | 2010-08-07 | Foreign Object | 310 | 513 | OH CONDUCTOR | P112744 | P112744 | P112743 | 2017 | 2010
161212E111279 | 0972-A | Before | 6.5096 | 16.5014 | 1 | Tier 3 | 2017-06-29 | 2016-12-12 | Foreign Object | 308 | 513 | OH CONDUCTOR | P13256 | P13256 | P13262 | 2017 | 2016
161212E111279 | 0972-B | Before | 6.6521 | 16.3589 | 1 | Tier 3 | 2017-05-08 | 2016-12-12 | Foreign Object | 308 | 513 | OH CONDUCTOR | P13256 | P13256 | P13262 | 2017 | 2016
220610E261533 | 0972-D | After | 6.6137 | 16.3973 | 1 | Tier 2 | 2017-05-22 | 2022-06-10 | Foreign Object | 308 | 510 | OH CONDUCTOR | P215662 | P215662 | P116940 | 2017 | 2022
220610E261533 | 0972-E | After | 6.6137 | 16.3973 | 1 | Tier 2 | 2017-05-22 | 2022-06-10 | Foreign Object | 308 | 510 | OH CONDUCTOR | P215662 | P215662 | P116940 | 2017 | 2022
230126E277182 | 442U | After | 1.3973 | 21.6137 | 1 | Tier 3 | 2022-08-08 | 2023-01-26 | Foreign Object | 322 | 513 | Conductor, OH | P173166 | P173166 | P173165 | 2022 | 2023
131124E30662 | C1215 MAINLINE CFSP W/S R1 | Before | 8.6712 | 14.3397 | 1 | Tier 3 | 2015-05-02 | 2013-11-24 | Foreign Object | 308 | 513 | OH CONDUCTOR | P40839 | P40839 | P40840 | 2015 | 2013
080921E7603 | C157:2013 CFSP CNF RIDGEPI | Before | 9.4137 | 13.5973 | 1 | Tier 3 | 2014-08-04 | 2008-09-21 | Foreign Object | 308 | 513 | OH CONDUCTOR | P278724 | P278724 | P278725 | 2014 | 2008
050927E7601 | C220 PH 2 O RECONDUCTOR | Before | 8.1288 | 14.8822 | 1 | Tier 3 | 2015-11-16 | 2005-09-27 | Foreign Object | 310 | 214 | OH CONDUCTOR | P310516 | P310516 | P219466 | 2015 | 2005
121116E5723 | C230: 2013 FIRE HARDNG 4 R2 | Before | 8.6986 | 14.3123 | 1 | Tier 2 | 2015-04-22 | 2012-11-16 | Foreign Object | 308 | 510 | OH CONDUCTOR | P610498 | P610498 | P610499 | 2015 | 2012
070915E5016 | 0221-W | Before | 5.3562 | 17.6548 | 1 | Tier 3 | 2018-08-24 | 2007-09-15 | Miscellaneous | 206 | 532 | POLE | P410198 | P410198 | P410199 | 2018 | 2007
031027E5090 | 0222-SS (ASD) | Before | 0.34247 | 22.6685 | 1 | Tier 3 | 2023-08-28 | 2003-10-27 | Miscellaneous | 206 |  | OH CONDUCTOR | P196115 | P196115 | P17794 | 2023 | 2003
031027E5090 | 0222-X | Before | 7.1671 | 15.8438 | 1 | Tier 3 | 2016-11-01 | 2003-10-27 | Miscellaneous | 206 |  | OH CONDUCTOR | P196115 | P196115 | P17794 | 2016 | 2003
071023E5097 | 0230-C | Before | 4.9753 | 18.0356 | 1 | Tier 2 | 2019-01-10 | 2007-10-23 | Miscellaneous | 206 | 513 | OH CONDUCTOR | P216899 | P216899 | P316594 | 2019 | 2007
071022E5018 | PE1 PH 4 A POLE CHGO R11 | Before | 8.5096 | 14.5014 | 1 | Tier 3 | 2015-06-30 | 2007-10-22 | Miscellaneous | 206 | 513 | OH CONDUCTOR | P116838 | P116838 | P116840 | 2015 | 2007
201120E221064 | 0212-C-PH-02 | Before | 3.0904 | 19.9205 | 1 | Tier 3 | 2020-11-28 | 2020-11-20 | SDGE/Contractor Contact | 632 | 218 | OH CONDUCTOR | P166149 | P166149 | P112488 | 2020 | 2020
201120E221064 | 0212-C-PH-02 | Before | 3.0904 | 19.9205 | 1 | Tier 3 | 2020-11-28 | 2020-11-20 | SDGE/Contractor Contact | 632 | 513 | OH CONDUCTOR | P166149 | P166149 | P112488 | 2020 | 2020
170905E130653 | 0157-H | Before | 3.3014 | 19.7096 | 1 | Tier 3 | 2020-09-12 | 2017-09-05 | Tree Contact | 322 | 513 | OH CONDUCTOR | P175945 | P175945 | P175946 | 2020 | 2017
181123E164074 | 0157-H | Before | 3.3014 | 19.7096 | 1 | Tier 3 | 2020-09-12 | 2018-11-23 | Tree Contact | 318 | 513 | OH CONDUCTOR | P175945 | P175945 | P175946 | 2020 | 2018
021029E5067 | 0175-A | Before | 6.9507 | 16.0603 | 1 | Tier 3 | 2017-01-19 | 2002-10-29 | Tree Contact | 322 | 510 | OH CONDUCTOR | P311257 | P311257 | P311258 | 2017 | 2002
071026E5026 | 0221-J | Before | 7.0055 | 16.0055 | 1 | Tier 3 | 2016-12-30 | 2007-10-26 | Tree Contact | 322 | 513 | OH CONDUCTOR | P115679 | P115679 | P115680 | 2016 | 2007
030317E5008 | 0222-NN | Before | 2.6329 | 20.3781 | 1 | Tier 3 | 2021-05-14 | 2003-03-17 | Tree Contact | 318 | 513 | OH CONDUCTOR | P312952 | P312952 | P316731 | 2021 | 2003
070902E5150 | 0222-R | Before | 7.7315 | 15.2795 | 1 | Tier 3 | 2016-04-09 | 2007-09-02 | Tree Contact | 322 | 513 | OH CONDUCTOR | P416781 | P416781 | P416782 | 2016 | 2007
030729E7601 | 0222-S | Before | 7.8356 | 15.1753 | 1 | Tier 3 | 2016-03-02 | 2003-07-29 | Tree Contact | 322 | 214 | OH CONDUCTOR | P116912 | P116912 | P116913 | 2016 | 2003
030309E5009 | 0230-B | Before | 4.9753 | 18.0356 | 1 | Tier 2 | 2019-01-10 | 2003-03-09 | Tree Contact | 322 | 513 | OH CONDUCTOR | P316588 | P316588 | P517425 | 2019 | 2003
030309E5009 | 0230-C | Before | 4.9753 | 18.0356 | 1 | Tier 2 | 2019-01-10 | 2003-03-09 | Tree Contact | 322 | 513 | OH CONDUCTOR | P316588 | P316588 | P517425 | 2019 | 2003
160731E101667 | 0230-D | Before | 4.9342 | 18.0767 | 1 | Tier 2 | 2019-01-25 | 2016-07-31 | Tree Contact | 322 | 513 | OH CONDUCTOR | P418313 | P418313 | P418314 | 2019 | 2016
080920E7601 | 0237-C | Before | 7.4658 | 15.5452 | 1 | Tier 3 | 2016-07-15 | 2008-09-19 | Tree Contact | 322 | 513 | OH CONDUCTOR | P17636 | P17636 | P19785 | 2016 | 2008
040319E7701 | 0237-N | Before | 7.3616 | 15.6493 | 1 | Tier 3 | 2016-08-22 | 2004-03-19 | Tree Contact | 322 | 513 | OH CONDUCTOR | P317736 | P317736 | P317737 | 2016 | 2004
150212E62367 | 0237-Q | Before | 7.5836 | 15.4274 | 1 | Tier 2 | 2016-06-02 | 2015-02-12 | Tree Contact | 322 | 513 | OH CONDUCTOR | P14699 | P14699 | P14700J | 2016 | 2015
120212E7601 | 0240-G | Before | 5.2493 | 17.7616 | 1 | Tier 3 | 2018-10-02 | 2012-02-12 | Tree Contact | 322 | 510 | OH CONDUCTOR | P74062 | P74062 | P877134 | 2018 | 2012
110530E7801 | 0350-G | Before | 5.2658 | 17.7452 | 1 | Tier 2 | 2018-09-26 | 2011-05-30 | Tree Contact | 318 | 513 | OH CONDUCTOR | P514661 | P514661 | P514662 | 2018 | 2011
130730E22576 | 0445-O | Before | 3.3397 | 19.6712 | 1 | Tier 2 | 2020-08-29 | 2013-07-30 | Tree Contact | 322 | 510 | OH CONDUCTOR | P41266 | P41266 | P45601 | 2020 | 2013
140331E39501 | 0520-I | Before | 5.8767 | 17.1342 | 1 | Tier 2 | 2018-02-15 | 2014-03-31 | Tree Contact | 322 | 513 | OH CONDUCTOR | P216031 | P216031 | P216032 | 2018 | 2014
191217E192658 | 0908-G | Before | 0.99178 | 22.0192 | 1 | Tier 2 | 2023-01-03 | 2019-12-17 | Tree Contact | 322 | 510 | OH CONDUCTOR | P219432 | P219432 | P219431 | 2023 | 2019
060629E5050 | 0971-D | Before | 6.2384 | 16.7726 | 1 | Tier 3 | 2017-10-06 | 2006-06-29 | Tree Contact | 322 | 510 | OH CONDUCTOR | P611658 | P611658 | P611659 | 2017 | 2006
050921E7604 | C222 PH 1 P RECONDUC R7 | Before | 8.589 | 14.4219 | 1 | Tier 3 | 2015-06-01 | 2005-09-21 | Tree Contact | 322 | 513 | OH CONDUCTOR | P214099 | P214099 | P318180 | 2015 | 2005
080920E7601 | C237 PH 2 H RECONDUCT R8 | Before | 8.3863 | 14.6247 | 1 | Tier 3 | 2015-08-14 | 2008-09-19 | Tree Contact | 322 | 513 | OH CONDUCTOR | P17636 | P17636 | P19785 | 2015 | 2008
100407E7601 | C441 PH 4 POLE REPLACE R2 | Before | 9.189 | 13.8219 | 1 | Tier 3 | 2014-10-25 | 2010-04-07 | Tree Contact | 322 | 510 | OH CONDUCTOR | P40498 | P40498 | P40499 | 2014 | 2010
130730E22576 | C445,BU:LG SPAN/DESIMI R16 | Before | 3.3397 | 19.6712 | 1 | Tier 2 | 2020-08-29 | 2013-07-30 | Tree Contact | 322 | 510 | OH CONDUCTOR | P41266 | P41266 | P45601 | 2020 | 2013
021110E5001 | C73 PH 4 CPOLE CHGOUT R11 | Before | 8.0055 | 15.0055 | 1 | Tier 3 | 2015-12-31 | 2002-11-10 | Tree Contact | 322 |  | OH CONDUCTOR | P173323 | P173323 | P173324 | 2015 | 2002
030106E5054 | 0078-D | Before | 6.3397 | 16.6712 | 1 | Tier 3 | 2017-08-30 | 2003-01-06 | Weather | 404 | 554 | CROSSARM | P172683 | P172683 | P172683 | 2017 | 2003
041229E5262 | 0157-J | Before | 2.6822 | 20.3288 | 1 | Tier 3 | 2021-04-26 | 2004-12-29 | Weather | 426 | 513 | OH CONDUCTOR | P177532 | P177532 | P177531 | 2021 | 2004
041229E5262 | 0157-J | Before | 2.6822 | 20.3288 | 1 | Tier 3 | 2021-04-26 | 2004-12-29 | Weather | 426 | 513 | OH CONDUCTOR | P177532 | P177532 | P177531 | 2021 | 2004
150302E63481 | 0175-A | Before | 6.9507 | 16.0603 | 1 | Tier 3 | 2017-01-19 | 2015-03-02 | Weather | 410 | 515 | JUMPER | P311259 | P311259 | P114914 | 2017 | 2015
050104E5082 | 0175-D | Before | 6.8932 | 16.1178 | 1 | Tier 3 | 2017-02-09 | 2005-01-04 | Weather | 412 | 530 | OH CONDUCTOR | P612465 | P612465 | P613832 | 2017 | 2005
170122E113967 | 0176-C | Before | 6.8932 | 16.1178 | 1 | Tier 3 | 2017-02-09 | 2017-01-22 | Weather | 412 | 510 | OH CONDUCTOR | P212520 | P212520 | P212527 | 2017 | 2017
041020E5098 | 0176-D | Before | 4.9753 | 18.0356 | 1 | Tier 3 | 2019-01-10 | 2004-10-20 | Weather | 412 | 513 | OH CONDUCTOR | P716206 | P716206 | P115207 | 2019 | 2004
100119E7501 | 0176-E | Before | 6.6986 | 16.3123 | 1 | Tier 2 | 2017-04-21 | 2010-01-19 | Weather | 412 | 513 | OH CONDUCTOR | P114000 | P114000 | P115198 | 2017 | 2010
020910E5031 | 0212-A | Before | 4.0137 | 18.9973 | 1 | Tier 2 | 2019-12-27 | 2002-09-10 | Weather | 412 | 513 | OH CONDUCTOR | P19565 | P19565 | P19567 | 2019 | 2002
030824E5037 | 0212-C-PH-02 | Before | 3.0904 | 19.9205 | 1 | Tier 3 | 2020-11-28 | 2003-08-24 | Weather | 412 | 513 | OH CONDUCTOR | P112471 | P112471 | P112472 | 2020 | 2003
120227E9901 | 0212-C-PH-03 | Before | 3.0904 | 19.9205 | 1 | Tier 3 | 2020-11-28 | 2012-02-27 | Weather | 412 | 513 | OH CONDUCTOR | P112496 | P112496 | P112497 | 2020 | 2012
041121E5111 | 0212-E | Before | 3.474 | 19.537 | 1 | Tier 2 | 2020-07-11 | 2004-11-21 | Weather | 412 |  | OH CONDUCTOR | P216486 | P216486 | P216487 | 2020 | 2004
091207E5580 | 0212-E | Before | 3.474 | 19.537 | 1 | Tier 2 | 2020-07-11 | 2009-12-07 | Weather | 412 | 513 | OH CONDUCTOR | P216471 | P216471 | P216472 | 2020 | 2009
120809E8104 | 0212-T | Before | 2.5534 | 20.4575 | 1 | Tier 2 | 2021-06-12 | 2012-08-09 | Weather | 410 | 510 | OH CONDUCTOR | P217948 | P217948 | P217986 | 2021 | 2012
120809E8104 | 0212-T | Before | 2.611 | 20.4 | 1 | Tier 2 | 2021-05-22 | 2012-08-09 | Weather | 410 | 510 | OH CONDUCTOR | P217948 | P217948 | P217986 | 2021 | 2012
120809E8104 | 0212-U | Before | 2.5534 | 20.4575 | 1 | Tier 2 | 2021-06-12 | 2012-08-09 | Weather | 410 | 510 | OH CONDUCTOR | P217948 | P217948 | P217986 | 2021 | 2012
151226E85131 | 0212-V | Before | 3.6849 | 19.326 | 1 | Tier 2 | 2020-04-25 | 2015-12-26 | Weather | 412 |  | OH CONDUCTOR | P218022 | P218022 | P317438 | 2020 | 2015
150126E60773 | 0212-X | Before | 2.5151 | 20.4959 | 1 | Tier 2 | 2021-06-26 | 2015-01-26 | Weather | 412 | 513 | OH CONDUCTOR | P310550 | P310550 | P310551 | 2021 | 2015
041229E7504 | 0215-A | Before | 5.5178 | 17.4932 | 1 | Tier 2 | 2018-06-26 | 2004-12-29 | Weather | 426 | 513 | OH CONDUCTOR | P211160 | P211160 | P115840 | 2018 | 2004
040813E5042 | 0217-H | Before | 4.7425 | 18.2685 | 1 | Tier 2 | 2019-04-05 | 2004-08-13 | Weather | 410 | 550 | TRANSFORMER | P311538 | P311538 | P218395 | 2019 | 2004
140430E41817 | 0217-N | Before | 4.9068 | 18.1041 | 1 | Tier 2 | 2019-02-04 | 2014-04-30 | Weather | 426 | 526 | GUY WIRE | P214141 | P214141 | P214142 | 2019 | 2014
030329E5027 | 0220-N | Before | 7.1836 | 15.8274 | 1 | Tier 3 | 2016-10-26 | 2003-03-29 | Weather | 412 |  | OH CONDUCTOR | P17991 | P17991 | P17993 | 2016 | 2003
061130E7704 | 0220-N | Before | 7.1836 | 15.8274 | 1 | Tier 3 | 2016-10-26 | 2006-11-30 | Weather | 412 |  | OH CONDUCTOR | P17990 | P17990 | P17991 | 2016 | 2006
101222E7704 | 0220-N | Before | 7.1836 | 15.8274 | 1 | Tier 3 | 2016-10-26 | 2010-12-22 | Weather | 412 | 513 | OH CONDUCTOR | P18004 | P18004 | P18005 | 2016 | 2010
091208E7802 | 0221-A | Before | 5.7425 | 17.2685 | 1 | Tier 3 | 2018-04-05 | 2009-12-08 | Weather | 412 | 513 | OH CONDUCTOR | P412625 | P412625 | P412626 | 2018 | 2009
091207E7810 | 0221-H | Before | 7.2055 | 15.8055 | 1 | Tier 3 | 2016-10-18 | 2009-12-07 | Weather | 412 | 513 | OH CONDUCTOR | P112093 | P112093 | P112094 | 2016 | 2009
041216E5089 | 0221-J | Before | 7.0055 | 16.0055 | 1 | Tier 3 | 2016-12-30 | 2004-12-16 | Weather | 412 |  | OH CONDUCTOR | P115685 | P115685 | P115687 | 2016 | 2004
060312E7102 | 0221-N | Before | 7.0438 | 15.9671 | 1 | Tier 3 | 2016-12-16 | 2006-03-12 | Weather | 412 |  | OH CONDUCTOR | P211421 | P211421 | P211422 | 2016 | 2006
081218E5106 | 0221-N | Before | 7.0438 | 15.9671 | 1 | Tier 3 | 2016-12-16 | 2008-12-18 | Weather | 412 | 510 | OH CONDUCTOR | P413439 | P413439 | P413443 | 2016 | 2008
081217E7701 | 0222-AA | Before | 6.4164 | 16.5945 | 1 | Tier 3 | 2017-08-02 | 2008-12-17 | Weather | 426 | 513 | OH CONDUCTOR | P17862 | P17862 | P116633 | 2017 | 2008
081217E7701 | 0222-AA | Before | 6.4164 | 16.5945 | 1 | Tier 3 | 2017-08-02 | 2008-12-17 | Weather | 426 | 513 | OH CONDUCTOR | P17862 | P17862 | P116633 | 2017 | 2008
041121E5093 | 0222-EE | Before | 3.1863 | 19.8247 | 1 | Tier 3 | 2020-10-24 | 2004-11-21 | Weather | 420 | 510 | OH CONDUCTOR | P510223 | P510223 | P510224 | 2020 | 2004
060310E5015 | 0222-FF | Before | 1.7452 | 21.2658 | 1 | Tier 3 | 2022-04-03 | 2006-03-10 | Weather | 408 | 513 | OH CONDUCTOR | P412776 | P412776 | P412777 | 2022 | 2006
100121E7805 | 0222-MM | Before | 3.2822 | 19.7288 | 1 | Tier 3 | 2020-09-19 | 2010-01-21 | Weather | 404 | 513 | OH CONDUCTOR | P312304 | P312304 | P312306 | 2020 | 2010
130220E11376 | 0222-MM | Before | 3.2822 | 19.7288 | 1 | Tier 3 | 2020-09-19 | 2013-02-20 | Weather | 408 | 513 | OH CONDUCTOR | P312309 | P312309 | P312310 | 2020 | 2013
090205E7701 | 0222-X | Before | 7.1671 | 15.8438 | 1 | Tier 3 | 2016-11-01 | 2009-02-05 | Weather | 412 | 513 | OH CONDUCTOR | P17803 | P17803 | P17805 | 2016 | 2009
021129E5148 | 0230-B | Before | 4.9753 | 18.0356 | 1 | Tier 2 | 2019-01-10 | 2002-11-29 | Weather | 412 | 513 | OH CONDUCTOR | P316588 | P316588 | P316589 | 2019 | 2002
030111E5009 | 0230-B | Before | 4.9753 | 18.0356 | 1 | Tier 2 | 2019-01-10 | 2003-01-11 | Weather | 426 | 513 | OH CONDUCTOR | P116149 | P116149 | P714753 | 2019 | 2003
021129E5148 | 0230-C | Before | 4.9753 | 18.0356 | 1 | Tier 2 | 2019-01-10 | 2002-11-29 | Weather | 412 | 513 | OH CONDUCTOR | P316588 | P316588 | P316589 | 2019 | 2002
050219E5026 | 0230-C | Before | 4.9753 | 18.0356 | 1 | Tier 2 | 2019-01-10 | 2005-02-19 | Weather | 412 | 513 | OH CONDUCTOR | P316596 | P316596 | P316595 | 2019 | 2005
080310E5055 | 0236-B | Before | 7.2027 | 15.8082 | 1 | Tier 3 | 2016-10-19 | 2008-03-10 | Weather | 412 | 513 | OH CONDUCTOR | P211587 | P211587 | P211586 | 2016 | 2008
011209E5030 | 0237-I | Before | 4.0247 | 18.9863 | 1 | Tier 3 | 2019-12-23 | 2001-12-09 | Weather | 426 |  |  | P113843 | P113843 | P113842 | 2019 | 2001
021126E5001 | 0350-L | Before | 4.2685 | 18.7425 | 1 | Tier 2 | 2019-09-25 | 2002-11-26 | Weather | 426 |  | POLE | P215146 | P215146 | P215145 | 2019 | 2002
100118E5065 | 0350-N-FT | Before | 4.0767 | 18.9342 | 1 | Tier 2 | 2019-12-04 | 2010-01-18 | Weather | 420 | 510 | OH CONDUCTOR | P215153 | P215153 | P817002 | 2019 | 2010
100119E7803 | 0350-N-FT | Before | 4.0767 | 18.9342 | 1 | Tier 2 | 2019-12-04 | 2010-01-19 | Weather | 420 | 510 | OH CONDUCTOR | P215153 | P215153 | P817002 | 2019 | 2010
060311E5102 | 0441-CFSP | Before | 7.2055 | 15.8055 | 1 | Tier 3 | 2016-10-18 | 2006-03-11 | Weather | 412 |  | OH CONDUCTOR | P40811 | P40811 | P40812 | 2016 | 2006
090110E5050 | 0442-D | Before | 8.1151 | 14.8959 | 1 | Tier 3 | 2015-11-21 | 2009-01-10 | Weather | 412 | 513 | OH CONDUCTOR | P173171 | P173171 | P173172 | 2015 | 2009
140430E41755 | 0442-D | Before | 8.1151 | 14.8959 | 1 | Tier 3 | 2015-11-21 | 2014-04-30 | Weather | 426 | 532 |  | P173170 | P173170 | P173172 | 2015 | 2014
120227E5119 | 0444-A | Before | 2.5589 | 20.4521 | 1 | Tier 2 | 2021-06-10 | 2012-02-27 | Weather | 412 | 513 | OH CONDUCTOR | P42046 | P42046 | P42045 | 2021 | 2012
120227E5119 | 0444-B | Before | 2.5534 | 20.4575 | 1 | Tier 2 | 2021-06-12 | 2012-02-27 | Weather | 412 | 513 | OH CONDUCTOR | P42046 | P42046 | P42045 | 2021 | 2012
110220E7602 | 0445-N | Before | 4.6274 | 18.3836 | 1 | Tier 2 | 2019-05-17 | 2011-02-20 | Weather | 412 | 513 | OH CONDUCTOR | P41237 | P41237 | P41238 | 2019 | 2011
140301E37038 | 0445-Q | Before | 2.0356 | 20.9753 | 1 | Tier 2 | 2021-12-18 | 2014-03-01 | Weather | 412 | 513 | OH CONDUCTOR | P41365 | P41365 | P41366 | 2021 | 2014
140301E37038 | 0445-Q | Before | 2.0356 | 20.9753 | 1 | Tier 2 | 2021-12-18 | 2014-03-01 | Weather | 412 | 513 | OH CONDUCTOR | P41365 | P41365 | P41366 | 2021 | 2014
060115E5023 | 0520-B | Before | 6.3534 | 16.6575 | 1 | Tier 2 | 2017-08-25 | 2006-01-15 | Weather | 426 | 513 | OH CONDUCTOR | P311973 | P311973 | P311972 | 2017 | 2006
060115E5023 | 0520-C | Before | 6.3753 | 16.6356 | 1 | Tier 2 | 2017-08-17 | 2006-01-15 | Weather | 426 | 513 | OH CONDUCTOR | P311973 | P311973 | P311972 | 2017 | 2006
111102E5010 | 0908-F | Before | 3.3589 | 19.6521 | 1 | Tier 2 | 2020-08-22 | 2011-11-02 | Weather | 426 | 513 | OH CONDUCTOR | P117357 | P117357 | P117358 | 2020 | 2011
050723E5051 | 0908-G | Before | 0.99178 | 22.0192 | 1 | Tier 2 | 2023-01-03 | 2005-07-23 | Weather | 412 |  | OH CONDUCTOR | P518205 | P518205 | P115827 | 2023 | 2005
120910E8106 | 0908-G | Before | 0.99178 | 22.0192 | 1 | Tier 2 | 2023-01-03 | 2012-09-09 | Weather | 410 | 513 | OH CONDUCTOR | P163664 | P163664 | P115836 | 2023 | 2012
030106E7115 | 0971-J | Before | 6.6027 | 16.4082 | 1 | Tier 3 | 2017-05-26 | 2003-01-06 | Weather | 412 | 513 | OH CONDUCTOR | P112741 | P112741 | P311523 | 2017 | 2003
160105E85494 | 0971-J | Before | 6.6027 | 16.4082 | 1 | Tier 3 | 2017-05-26 | 2016-01-05 | Weather | 412 | 513 | OH CONDUCTOR | P111581 | P111581 | P111580 | 2017 | 2016
041216E7701 | 0971-M | Before | 5.8384 | 17.1726 | 1 | Tier 3 | 2018-03-01 | 2004-12-16 | Weather | 412 | 513 | OH CONDUCTOR | P213599 | P213599 | P213600 | 2018 | 2004
160131E87294 | 0971-M | Before | 5.8384 | 17.1726 | 1 | Tier 3 | 2018-03-01 | 2016-01-31 | Weather | 426 | 510 | OH CONDUCTOR | P113153 | P113153 | P113160 | 2018 | 2016
030106E5019 | 0972-A | Before | 6.5096 | 16.5014 | 1 | Tier 3 | 2017-06-29 | 2003-01-06 | Weather | 412 | 513 | OH CONDUCTOR | P13233 | P13233 | P13234 | 2017 | 2003
070322E5059 | 1030-D | Before | 4.2849 | 18.726 | 1 | Tier 3 | 2019-09-19 | 2007-03-22 | Weather | 410 | 513 | OH CONDUCTOR | P113858 | P113858 | P113859 | 2019 | 2007
080522E5035 | 1030-D | Before | 4.2849 | 18.726 | 1 | Tier 3 | 2019-09-19 | 2008-05-22 | Weather | 410 | 513 | OH CONDUCTOR | P411943 | P411943 | P612230 | 2019 | 2008
071022E5108 | 1030-K | Before | 6.4356 | 16.5753 | 1 | Tier 3 | 2017-07-26 | 2007-10-22 | Weather | 412 | 513 | OH CONDUCTOR | P112251 | P112251 | P112255 | 2017 | 2007
170120E113778 | 1030-O | Before | 6.6521 | 16.3589 | 1 | Tier 3 | 2017-05-08 | 2017-01-20 | Weather | 412 | 513 | OH CONDUCTOR | P117175 | P117175 | P117176 | 2017 | 2017
091207E7801 | 1030-R | Before | 6.3836 | 16.6274 | 1 | Tier 3 | 2017-08-14 | 2009-12-07 | Weather | 430 | 513 | OH CONDUCTOR | P115513 | P115513 | P319261 | 2017 | 2009
071022E5213 | 448NNN | Before | 2.4055 | 20.6055 | 1 | Tier 3 | 2021-08-05 | 2007-10-22 | Weather | 412 | 513 | OH CONDUCTOR | P43506 | P43506 | P43508 | 2021 | 2007
110227E5004 | 79F | Before | 3.3808 | 19.6301 | 1 | Tier 3 | 2020-08-14 | 2011-02-27 | Weather | 426 | 513 | OH CONDUCTOR | P475945 | P475945 | P475946 | 2020 | 2011
110202E5017 | C222 FIRE RISK MITIG PRO R2 | Before | 7.3616 | 15.6493 | 1 | Tier 3 | 2016-08-22 | 2011-02-02 | Weather | 412 | 510 | OH CONDUCTOR | P111818 | P111818 | P111819 | 2016 | 2011
110202E5017 | C222 FIRE RISK MITIG PRO R2 | Before | 9.8274 | 13.1836 | 1 | Tier 3 | 2014-03-06 | 2011-02-02 | Weather | 412 | 510 | OH CONDUCTOR | P111818 | P111818 | P111819 | 2014 | 2011
031216E7501 | C222 FIRE RISK MITIG PROJP | Before | 9.4548 | 13.5562 | 1 | Tier 3 | 2014-07-20 | 2003-12-16 | Weather | 412 | 530 | INSULATOR | P311305 | P311305 | P311306 | 2014 | 2003
020210E7105 | C222 PH 1 I RECONDUC R7 | Before | 8.389 | 14.6219 | 1 | Tier 3 | 2015-08-13 | 2002-02-10 | Weather | 412 | 532 | POLE | P711508 | P711508 | P619513 | 2015 | 2002
160131E87248 | C237 PH 2 D RECONDUCT R1 | After | 8.4329 | 14.5781 | 1 | Tier 3 | 2015-07-28 | 2016-01-31 | Weather | 412 | 513 | OH CONDUCTOR | P17618 | P17618 | P17617 | 2015 | 2016
071231E7701 | C237 PH 2 D RECONDUCT R1 | Before | 8.4329 | 14.5781 | 1 | Tier 3 | 2015-07-28 | 2007-12-31 | Weather | 412 |  | OH CONDUCTOR | P17607 | P17607 | P17608 | 2015 | 2007
020210E7205 | C357:2011 CFSP WS,TW ON R12 | Before | 8.7945 | 14.2164 | 1 | Tier 2 | 2015-03-18 | 2002-02-10 | Weather | 412 | 513 |  | P277707 | P277707 | P372529 | 2015 | 2002
110308E7606 | C444 BRANCHLN CFSP P4 R1 | Before | 8.0493 | 14.9616 | 1 | Tier 2 | 2015-12-15 | 2011-03-08 | Weather | 412 | 513 | OH CONDUCTOR | P41967 | P41967 | P41968 | 2015 | 2011
130208E10784 | C444 BRANCHLN CFSP P4 R1 | Before | 8.0493 | 14.9616 | 1 | Tier 2 | 2015-12-15 | 2013-02-08 | Weather | 408 | 513 | OH CONDUCTOR | P41976 | P41976 | P41977 | 2015 | 2013
110308E7606 | C444 BRANCHLN PH2 P4196 R1 | Before | 8.7836 | 14.2274 | 1 | Tier 2 | 2015-03-22 | 2011-03-08 | Weather | 412 | 513 | OH CONDUCTOR | P41967 | P41967 | P41968 | 2015 | 2011
050409E5002 | C444,BU:2011 CFSP RCNDCT R8 | Before | 10.2767 | 12.7342 | 1 | Tier 2 | 2013-09-23 | 2005-04-09 | Weather | 412 | 513 | OH CONDUCTOR | P42128 | P42128 | P42129 | 2013 | 2005
060311E7119 | C445 2012 CFSP WS BRANCH R1 | Before | 8.0329 | 14.9781 | 1 | Tier 2 | 2015-12-21 | 2006-03-11 | Weather | 410 | 412 | OH CONDUCTOR | P41587 | P41587 | P41585 | 2015 | 2006
080316E5004 | C445 2012 CFSP WS BRANCH R1 | Before | 8.0329 | 14.9781 | 1 | Tier 2 | 2015-12-21 | 2008-03-16 | Weather | 408 | 513 | OH CONDUCTOR | P41596 | P41596 | P41597 | 2015 | 2008
120214E9901 | C445 2012 CFSP WS BRANCH R1 | Before | 8.0329 | 14.9781 | 1 | Tier 2 | 2015-12-21 | 2012-02-14 | Weather | 412 | 513 | OH CONDUCTOR | P41586 | P41586 | P41585 | 2015 | 2012
130220E11367 | C445,BU:LG SPAN/DESIMI R16 | Before | 5.4438 | 17.5671 | 1 | Tier 2 | 2018-07-23 | 2013-02-20 | Weather | 404 | 412 | OH CONDUCTOR | P41267 | P41267 | P41269 | 2018 | 2013
130220E11367 | C445,BU:LG SPAN/DESIMI R16 | Before | 8.9041 | 14.1068 | 1 | Tier 2 | 2015-02-06 | 2013-02-20 | Weather | 404 | 412 | OH CONDUCTOR | P41267 | P41267 | P41269 | 2015 | 2013
020210E5092 | C79 PH4 SEC 2 #G POLE R6 | Before | 8.4438 | 14.5671 | 1 | Tier 3 | 2015-07-24 | 2002-02-10 | Weather | 426 | 513 |  | P172823 | P172823 | P172824 | 2015 | 2002
041217E5049 | CPE1-D | Before | 7.9342 | 15.0767 | 1 | Tier 3 | 2016-01-26 | 2004-12-17 | Weather | 412 | 513 | OH CONDUCTOR | P115172 | P115172 | P115173 | 2016 | 2004
020210E5107 | PE1 PH 4 A POLE CHGO R11 | Before | 8.5096 | 14.5014 | 1 | Tier 3 | 2015-06-30 | 2002-02-10 | Weather | 420 | 513 |  | P18906 | P18906 | P19717 | 2015 | 2002
041217E5049 | PE1 PH 4 A POLE CHGO R11 | Before | 8.5096 | 14.5014 | 1 | Tier 3 | 2015-06-30 | 2004-12-17 | Weather | 412 | 513 | OH CONDUCTOR | P115172 | P115172 | P115173 | 2015 | 2004
200226E197756 | 448CC CC | Before | 1.5945 | 21.4164 | 1 | Tier 3 | 2022-05-28 | 2020-02-26 | Weather | 412 | 513 | POLE | P43890 | P43890 | P43891 | 2022 | 2020
221124E273544 | C442 PH 4 FPOLE CHGOUT R1 | After | 7.6575 | 15.3534 | 1 | Tier 3 | 2016-05-06 | 2022-11-24 | Weather | 420 | 510 | Conductor, OH | P873423 | P873423 | P873424 | 2016 | 2022
220909E268067 | C78 PH4 CPOLE CHGOUT/RECO | After | 8.7781 | 14.2329 | 1 | Tier 3 | 2015-03-24 | 2022-09-09 | Weather | 412 | 510 | Wire Slap | P274658 | P274658 | P172729 | 2015 | 2022

## Summary Effectiveness
Project ID | Unhardened Faults | Unhardened Years | Unhardened faults per operating year average | Hardened Faults | Hardened Years | Hardened faults per operating year average | Poles
448NNN | 2 | 20.6055 | 0.097062 | 0 | 2.4055 | 0 | 9
448QQQ | 1 | 20.6466 | 0.048434 | 0 | 2.3644 | 0 | 8
448RRR | 4 | 20.5726 | 0.19443 | 0 | 2.4384 | 0 | 12
448S | 1 | 20.9425 | 0.04775 | 0 | 2.0685 | 0 | 13
448T | 1 | 22.3151 | 0.044813 | 0 | 0.69589 | 0 | 10
448U | 1 | 20.5288 | 0.048712 | 0 | 2.4822 | 0 | 11
448W | 2 | 20.5123 | 0.097502 | 0 | 2.4986 | 0 | 5
448X | 2 | 20.5068 | 0.097528 | 0 | 2.5041 | 0 | 8
448YY | 3 | 20.811 | 0.14415 | 0 | 2.2 | 0 | 8
79F | 2 | 19.6301 | 0.10188 | 0 | 3.3808 | 0 | 3
79M | 1 | 22.4849 | 0.044474 | 0 | 0.52603 | 0 | 10
79N | 1 | 21.4493 | 0.046622 | 0 | 1.5616 | 0 | 4
C1023/C354_NEW_12KV_RECON | 5 | 20.9315 | 0.23887 | 0 | 2.0795 | 0 | 80
C1023/C354_RFS_FREEWAY_X | 1 | 20.3808 | 0.049066 | 0 | 2.6301 | 0 | 9
C1215 CWLONG SPAN/DESI R12 | 0 | 13.7068 | 0 | 2 | 9.3041 | 0.21496 | 5
C1215 MAINLINE CFSP W/S R1 | 2 | 14.3397 | 0.13947 | 2 | 8.6712 | 0.23065 | 17
C157:2013 CFSP CNF RIDGEPI | 1 | 13.5973 | 0.073544 | 0 | 9.4137 | 0 | 3
C220 PH 2 I RECONDUCT R8 | 3 | 14.6712 | 0.20448 | 1 | 8.3397 | 0.11991 | 50
C220 PH 2 L RECONDUCT R1 | 1 | 14.5589 | 0.068686 | 0 | 8.4521 | 0 | 29
C220 PH 2 O RECONDUCTOR | 2 | 14.8822 | 0.13439 | 1 | 8.1288 | 0.12302 | 15
C220 PH 4 B POLE CHGO R3 | 0 | 14.4082 | 0 | 1 | 8.6027 | 0.11624 | 30
C220 PH 4 D POLE CHGOUT | 0 | 13.9616 | 0 | 1 | 9.0493 | 0.11051 | 14
C220 PH 4 G POLE CHGO R2 | 0 | 14.8274 | 0 | 2 | 8.1836 | 0.24439 | 8
C221 PH4 #B POLE REPLA R1 | 0 | 14.4164 | 0 | 1 | 8.5945 | 0.11635 | 19
C221 PH4 D POLE REPLA R2 | 2 | 15.3973 | 0.12989 | 3 | 7.6137 | 0.39403 | 4
C221:ERI 2012 REBUILD | 3 | 14.6658 | 0.20456 | 0 | 8.3452 | 0 | 4
C221:ERI 2012 REBUILD IM R9 | 0 | 12.8164 | 0 | 2 | 10.1945 | 0.19618 | 11
C222 FIRE RISK MITIG PRJPH | 3 | 14.1233 | 0.21242 | 0 | 8.8877 | 0 | 74
C222 FIRE RISK MITIG PRO R1 | 1 | 14.1096 | 0.070874 | 1 | 8.9014 | 0.11234 | 15
C222 FIRE RISK MITIG PRO R2 | 1 | 13.1836 | 0.075852 | 0 | 9.8274 | 0 | 26
C222 FIRE RISK MITIG PROJP | 4 | 12.9699 | 0.30841 | 1 | 10.0411 | 0.099591 | 51
C222 PH 1 #Q RECONDUC R3 | 0 | 14.6767 | 0 | 1 | 8.3342 | 0.11999 | 15
C222 PH 1 F RECONDUCTOR | 1 | 15.2 | 0.065789 | 1 | 7.811 | 0.12803 | 24
C222 PH 1 H RECONDUC R1 | 1 | 14.863 | 0.067281 | 0 | 8.1479 | 0 | 10
C222 PH 1 I RECONDUC R7 | 3 | 14.6219 | 0.20517 | 1 | 8.389 | 0.1192 | 25
C222 PH 1 J RECONDUC R6 | 0 | 14.7562 | 0 | 1 | 8.2548 | 0.12114 | 19
C222 PH 1 P RECONDUC R7 | 4 | 14.4219 | 0.27736 | 0 | 8.589 | 0 | 25
C222 PH 2 #T RECONDU R11 | 2 | 14.8548 | 0.13464 | 0 | 8.1562 | 0 | 23
C222 PH4 SEC2 CPOLE CHGOU | 5 | 14.3342 | 0.34881 | 0 | 8.6767 | 0 | 29
C222 PH4 SEC2 DPOLE CH R1 | 2 | 14.0055 | 0.1428 | 0 | 9.0055 | 0 | 22
C230: 2013 FIRE HARDNG 4 R2 | 1 | 14.3123 | 0.06987 | 0 | 8.6986 | 0 | 2
C233 LONG SPAN EVAL P61 R18 | 1 | 13.9808 | 0.071527 | 1 | 9.0301 | 0.11074 | 3
C236 PH 2 C RECONDUCTOR | 2 | 15.3507 | 0.13029 | 0 | 7.6603 | 0 | 20
C236 PH 2 D RECONDUCTOR | 3 | 15.4822 | 0.19377 | 1 | 7.5288 | 0.13282 | 35
C237 PH 2 A RECONDUCTOR | 1 | 14.6438 | 0.068288 | 0 | 8.3671 | 0 | 27
C237 PH 2 D RECONDUCT R1 | 3 | 14.5781 | 0.20579 | 2 | 8.4329 | 0.23717 | 38
C237 PH 2 E RECONDUCTOR | 1 | 14.4795 | 0.069063 | 0 | 8.5315 | 0 | 22
C237 PH 2 H RECONDUCT R8 | 1 | 14.6247 | 0.068378 | 1 | 8.3863 | 0.11924 | 22
C237 PH 2 J RECONDUCTOR | 2 | 14.5781 | 0.13719 | 2 | 8.4329 | 0.23717 | 24
C237 PH 2 M RECONDUCTOR | 2 | 14.663 | 0.1364 | 0 | 8.3479 | 0 | 41
C239:2013 RIRAT RELIABILITY | 2 | 14.5753 | 0.13722 | 0 | 8.4356 | 0 | 12
C240 PH 2 E RECONDUCT R1 | 1 | 14.9425 | 0.066923 | 2 | 8.0685 | 0.24788 | 28
C357:2011 CFSP WS,TW ON R12 | 1 | 14.2164 | 0.070341 | 0 | 8.7945 | 0 | 6
C358 PH 2 A RECONDUCTOR | 0 | 14.7918 | 0 | 2 | 8.2192 | 0.24333 | 9
C358 PH 2 B RECONDUCTOR | 0 | 14.6192 | 0 | 1 | 8.3918 | 0.11916 | 14
C441 BRLINE CFSP W/S(P1 R1 | 1 | 14.926 | 0.066997 | 0 | 8.0849 | 0 | 28
C441 PH 4 POLE REPLACE R2 | 1 | 13.8219 | 0.072349 | 3 | 9.189 | 0.32648 | 16
C442 PH 2 J RECONDUCT R8 | 1 | 14.9671 | 0.066813 | 0 | 8.0438 | 0 | 10
C442 PH 4 BPOLE CHGOUT R1 | 2 | 14.2767 | 0.14009 | 1 | 8.7342 | 0.11449 | 25
C442 PH 4 EPOLE CHGOUT R7 | 1 | 13.8027 | 0.072449 | 0 | 9.2082 | 0 | 4
C442 PH 4 FPOLE CHGOUT R1 | 2 | 15.3534 | 0.13026 | 1 | 7.6575 | 0.13059 | 40
C442 PH 4 GPOLE CHGOUT R1 | 2 | 14.9397 | 0.13387 | 2 | 8.0712 | 0.24779 | 9
C442 PH 4 HPOLE CHGOUT/RE | 1 | 14.6137 | 0.068429 | 0 | 8.3973 | 0 | 21
C444 BRANCHLN CFSP P4 R1 | 11 | 14.9616 | 0.73521 | 0 | 8.0493 | 0 | 16
C444 BRANCHLN CFSP W/S R1 | 1 | 14.4055 | 0.069418 | 0 | 8.6055 | 0 | 5
C444 BRANCHLN PH1 P41936 | 1 | 14.389 | 0.069497 | 0 | 8.6219 | 0 | 13
C444 BRANCHLN PH2 P4196 R1 | 5 | 14.2274 | 0.35143 | 0 | 8.7836 | 0 | 23
C444,BU:2011 CFSP RCNDCT R8 | 2 | 12.7342 | 0.15706 | 0 | 10.2767 | 0 | 14
C445 2012 CFSP WS BRANCH R1 | 6 | 14.9781 | 0.40059 | 2 | 8.0329 | 0.24898 | 34
C445,BU:LG SPAN/DESIMI R16 | 3 | 14.1068 | 0.21266 | 0 | 8.9041 | 0 | 5
C67,BAR:LG SPAN/DESIMIL R3 | 1 | 13.6411 | 0.073308 | 0 | 9.3699 | 0 | 13
C73 PH 4 APOLE CHGOUT/ R9 | 1 | 14.2192 | 0.070328 | 1 | 8.7918 | 0.11374 | 17
C73 PH 4 BPOLE CHGOUT/ R5 | 1 | 13.9836 | 0.071513 | 0 | 9.0274 | 0 | 28
C73 PH 4 CPOLE CHGOUT R11 | 2 | 15.0055 | 0.13328 | 0 | 8.0055 | 0 | 40
C73 PH 4 EPOLE CHGOUT R11 | 2 | 14.3068 | 0.13979 | 1 | 8.7041 | 0.11489 | 29
C78 PH4 BPOLE CHGOUT/R R8 | 1 | 14.2329 | 0.07026 | 0 | 8.7781 | 0 | 9
C78 PH4 CPOLE CHGOUT/RECO | 2 | 14.2329 | 0.14052 | 2 | 8.7781 | 0.22784 | 20
C79 FIRE RISK MITIGATION R2 | 5 | 14.5452 | 0.34376 | 0 | 8.4658 | 0 | 72
C79 PH 1 #O RECONDUCTOR | 0 | 14.8521 | 0 | 1 | 8.1589 | 0.12257 | 14
C79 PH 2 R RECONDUCTOR | 1 | 14.8082 | 0.06753 | 1 | 8.2027 | 0.12191 | 22
C79 PH4 SEC 2 #G POLE R6 | 2 | 14.5671 | 0.1373 | 0 | 8.4438 | 0 | 15
C79 PH4 SEC 2 E POLE R1 | 2 | 14.4219 | 0.13868 | 0 | 8.589 | 0 | 18
C79 PH4 SEC 2 K POLE R7 | 1 | 14.463 | 0.069142 | 0 | 8.5479 | 0 | 42
C973 PH 2 #A RECOND | 2 | 14.5233 | 0.13771 | 0 | 8.4877 | 0 | 17
CNF-C79B | 1 | 20.7699 | 0.048147 | 1 | 2.2411 | 0.44621 | 177
CNF-TL629A | 9 | 19.726 | 0.45625 | 2 | 3.2849 | 0.60884 | 134
CPE1-D | 1 | 15.0767 | 0.066327 | 0 | 7.9342 | 0 | 28
CPE1-PH-04-B | 1 | 14.3753 | 0.069564 | 0 | 8.6356 | 0 | 18
CRA1 PH 2 A RECONDUCTOR | 2 | 14.7507 | 0.13559 | 0 | 8.2603 | 0 | 23
CRB1 | 5 | 19.9781 | 0.25027 | 0 | 3.0329 | 0 | 21
PE1 PH 4 A POLE CHGO R11 | 6 | 14.5014 | 0.41375 | 0 | 8.5096 | 0 | 51
PE1 PH 4#C POLE CHGOUT/RE | 1 | 14.2795 | 0.070031 | 0 | 8.7315 | 0 | 11
Track 2 530000154309 | 2 | 20.0877 | 0.099564 | 0 | 2.9233 | 0 | 16
0078-D | 6 | 16.6712 | 0.3599 | 1 | 6.3397 | 0.15774 | 26
0078-E | 3 | 15.2329 | 0.19694 | 0 | 7.7781 | 0 | 8
0078-G | 2 | 16.674 | 0.11995 | 0 | 6.337 | 0 | 26
0079-A | 2 | 15.2219 | 0.13139 | 4 | 7.789 | 0.51354 | 29
0079-M | 2 | 15.2356 | 0.13127 | 2 | 7.7753 | 0.25722 | 18
0079-P | 1 | 14.9315 | 0.066972 | 1 | 8.0795 | 0.12377 | 45
0157-B | 2 | 20.7644 | 0.096319 | 0 | 2.2466 | 0 | 48
0157-D | 5 | 20.7644 | 0.2408 | 0 | 2.2466 | 0 | 39
0157-G | 4 | 20.4384 | 0.19571 | 0 | 2.5726 | 0 | 40
0157-H | 5 | 19.7096 | 0.25368 | 0 | 3.3014 | 0 | 36
0157-J | 1 | 20.3288 | 0.049191 | 0 | 2.6822 | 0 | 29
0157-T | 3 | 18.9562 | 0.15826 | 0 | 4.0548 | 0 | 8
0157-V | 2 | 20.2082 | 0.09897 | 0 | 2.8027 | 0 | 48
0157-W | 9 | 19.1726 | 0.46942 | 0 | 3.8384 | 0 | 35
0157-X | 2 | 21.3123 | 0.093842 | 0 | 1.6986 | 0 | 32
0175-A | 2 | 16.0603 | 0.12453 | 0 | 6.9507 | 0 | 40
0175-B | 5 | 16.3068 | 0.30662 | 0 | 6.7041 | 0 | 32
0175-C | 3 | 16.2521 | 0.18459 | 0 | 6.7589 | 0 | 38
0175-D | 1 | 16.1178 | 0.062043 | 2 | 6.8932 | 0.29014 | 17
0175-E | 1 | 15.8274 | 0.063182 | 0 | 7.1836 | 0 | 9
0176-A | 2 | 16.2712 | 0.12292 | 2 | 6.7397 | 0.29675 | 32
0176-C | 4 | 16.1178 | 0.24817 | 0 | 6.8932 | 0 | 24
0176-D | 4 | 18.0356 | 0.22178 | 0 | 4.9753 | 0 | 24
0176-E | 1 | 16.3123 | 0.061303 | 1 | 6.6986 | 0.14928 | 28
0176-F | 0 | 17.6548 | 0 | 1 | 5.3562 | 0.1867 | 31
0176-H | 2 | 18.0356 | 0.11089 | 0 | 4.9753 | 0 | 17
0176-I-FT-02 | 1 | 20.7041 | 0.0483 | 0 | 2.3068 | 0 | 2
0176-J | 2 | 16.3836 | 0.12207 | 0 | 6.6274 | 0 | 23
0176-L | 2 | 20.4959 | 0.097581 | 0 | 2.5151 | 0 | 14
0182-COUNTRY_CLUB | 1 | 20.5863 | 0.048576 | 0 | 2.4247 | 0 | 8
0185-CAMINITO_A_CASA | 1 | 21.8137 | 0.045843 | 0 | 1.1973 | 0 | 4
0212-A | 12 | 18.9973 | 0.63167 | 1 | 4.0137 | 0.24915 | 71
0212-B | 20 | 18.9973 | 1.0528 | 0 | 4.0137 | 0 | 47
0212-C-PH-02 | 8 | 19.9205 | 0.4016 | 0 | 3.0904 | 0 | 45
0212-C-PH-03 | 3 | 19.9205 | 0.1506 | 0 | 3.0904 | 0 | 12
0212-D | 6 | 19.7288 | 0.30412 | 0 | 3.2822 | 0 | 35
0212-E | 5 | 19.537 | 0.25592 | 1 | 3.474 | 0.28785 | 70
0212-F | 1 | 19.5562 | 0.051135 | 0 | 3.4548 | 0 | 41
0212-GG | 1 | 20.6247 | 0.048486 | 1 | 2.3863 | 0.41906 | 32
0212-I | 1 | 19.4027 | 0.051539 | 0 | 3.6082 | 0 | 8
0212-J | 2 | 20.8795 | 0.095788 | 1 | 2.1315 | 0.46915 | 53
0212-P | 1 | 19.9014 | 0.050248 | 0 | 3.1096 | 0 | 61
0212-Q | 0 | 21.2247 | 0 | 1 | 1.7863 | 0.55982 | 78
0212-T | 1 | 20.4 | 0.04902 | 0 | 2.611 | 0 | 18
0212-U | 5 | 20.4575 | 0.24441 | 0 | 2.5534 | 0 | 75
0212-V | 2 | 19.326 | 0.10349 | 0 | 3.6849 | 0 | 56
0212-W | 3 | 19.326 | 0.15523 | 0 | 3.6849 | 0 | 40
0212-W-FT-02 | 1 | 19.3233 | 0.051751 | 0 | 3.6877 | 0 | 10
0212-X | 2 | 20.4959 | 0.097581 | 0 | 2.5151 | 0 | 30
0215-A | 6 | 17.4932 | 0.34299 | 1 | 5.5178 | 0.18123 | 27
0215-B | 5 | 17.4438 | 0.28663 | 0 | 5.5671 | 0 | 29
0215-C | 2 | 18.6877 | 0.10702 | 0 | 4.3233 | 0 | 32
0217-AD | 1 | 19.326 | 0.051744 | 0 | 3.6849 | 0 | 5
0217-B | 2 | 17.6466 | 0.11334 | 0 | 5.3644 | 0 | 23
0217-C | 2 | 17.1726 | 0.11646 | 1 | 5.8384 | 0.17128 | 37
0217-D | 5 | 18.9753 | 0.2635 | 0 | 4.0356 | 0 | 33
0217-E | 3 | 18.9753 | 0.1581 | 0 | 4.0356 | 0 | 37
0217-F | 1 | 17.3781 | 0.057544 | 0 | 5.6329 | 0 | 28
0217-G | 1 | 17.674 | 0.05658 | 0 | 5.337 | 0 | 18
0217-H | 3 | 18.2685 | 0.16422 | 0 | 4.7425 | 0 | 26
0217-J | 6 | 18.4603 | 0.32502 | 0 | 4.5507 | 0 | 26
0217-K | 1 | 18.2685 | 0.054739 | 0 | 4.7425 | 0 | 34
0217-M | 4 | 18.1808 | 0.22001 | 0 | 4.8301 | 0 | 31
0217-N | 2 | 18.1041 | 0.11047 | 0 | 4.9068 | 0 | 29
0217-P | 1 | 18.2685 | 0.054739 | 0 | 4.7425 | 0 | 27
0217-Q | 1 | 18.4603 | 0.05417 | 0 | 4.5507 | 0 | 30
0217-R | 6 | 18.7096 | 0.32069 | 0 | 4.3014 | 0 | 26
0217-V | 1 | 18.9781 | 0.052692 | 0 | 4.0329 | 0 | 5
0217-X (ASD) | 1 | 18.937 | 0.052807 | 0 | 4.074 | 0 | 5
0220-C | 2 | 15.2767 | 0.13092 | 1 | 7.7342 | 0.1293 | 18
0220-K | 2 | 15.789 | 0.12667 | 0 | 7.2219 | 0 | 28
0220-N | 6 | 15.8274 | 0.37909 | 0 | 7.1836 | 0 | 28
0220-Q | 3 | 16.3425 | 0.18357 | 0 | 6.6685 | 0 | 11
0221-A | 9 | 17.2685 | 0.52118 | 6 | 5.7425 | 1.0448 | 32
0221-D-VOLCAN MTN | 0 | 19.6904 | 0 | 1 | 3.3205 | 0.30116 | 20
0221-F | 3 | 17.4164 | 0.17225 | 2 | 5.5945 | 0.35749 | 36
0221-G | 2 | 17.0904 | 0.11702 | 0 | 5.9205 | 0 | 22
0221-H | 1 | 15.8055 | 0.063269 | 0 | 7.2055 | 0 | 22
0221-I | 1 | 16.3863 | 0.061027 | 0 | 6.6247 | 0 | 32
0221-J | 3 | 16.0055 | 0.18744 | 0 | 7.0055 | 0 | 36
0221-K | 2 | 15.6137 | 0.12809 | 1 | 7.3973 | 0.13519 | 42
0221-L | 0 | 15.9671 | 0 | 1 | 7.0438 | 0.14197 | 29
0221-M | 0 | 15.7726 | 0 | 1 | 7.2384 | 0.13815 | 24
0221-N | 2 | 15.9671 | 0.12526 | 0 | 7.0438 | 0 | 38
0221-O | 1 | 17.3644 | 0.057589 | 0 | 5.6466 | 0 | 14
0221-P | 0 | 17.1342 | 0 | 1 | 5.8767 | 0.17016 | 25
0221-R | 0 | 17.5918 | 0 | 2 | 5.4192 | 0.36906 | 22
0221-S | 2 | 17.6767 | 0.11314 | 0 | 5.3342 | 0 | 30
0221-V | 2 | 15.9233 | 0.1256 | 1 | 7.0877 | 0.14109 | 27
0221-W | 1 | 17.6548 | 0.056642 | 0 | 5.3562 | 0 | 13
0221-Y-PH1-SLAUGHTER | 1 | 17.5726 | 0.056907 | 1 | 5.4384 | 0.18388 | 2
0222-AA | 3 | 16.5945 | 0.18078 | 1 | 6.4164 | 0.15585 | 29
0222-BB | 0 | 15.2438 | 0 | 2 | 7.7671 | 0.2575 | 10
0222-CC | 1 | 19.6055 | 0.051006 | 0 | 3.4055 | 0 | 9
0222-EE | 3 | 19.8247 | 0.15133 | 0 | 3.1863 | 0 | 27
0222-FF | 7 | 21.2658 | 0.32917 | 0 | 1.7452 | 0 | 35
0222-FF-PH-02 | 5 | 21.2247 | 0.23558 | 0 | 1.7863 | 0 | 15
0222-HH | 1 | 19.3644 | 0.051641 | 0 | 3.6466 | 0 | 5
0222-II | 2 | 19.7671 | 0.10118 | 0 | 3.2438 | 0 | 38
0222-JJ | 1 | 19.7863 | 0.05054 | 0 | 3.2247 | 0 | 23
0222-K | 3 | 15.5452 | 0.19299 | 2 | 7.4658 | 0.26789 | 32
0222-MM | 2 | 19.7288 | 0.10137 | 0 | 3.2822 | 0 | 43
0222-N | 1 | 15.6493 | 0.063901 | 0 | 7.3616 | 0 | 31
0222-NN | 1 | 20.3781 | 0.049072 | 0 | 2.6329 | 0 | 56
0222-PP | 3 | 20.8986 | 0.14355 | 1 | 2.1123 | 0.47341 | 45
0222-R | 3 | 15.2795 | 0.19634 | 0 | 7.7315 | 0 | 45
0222-S | 1 | 15.1753 | 0.065896 | 0 | 7.8356 | 0 | 18
0222-SS (ASD) | 1 | 22.6685 | 0.044114 | 0 | 0.34247 | 0 | 7
0222-U | 2 | 15.5726 | 0.12843 | 1 | 7.4384 | 0.13444 | 36
0222-UU | 1 | 20.8027 | 0.048071 | 0 | 2.2082 | 0 | 8
0222-W | 1 | 15.4877 | 0.064567 | 0 | 7.5233 | 0 | 40
0222-X | 3 | 15.8438 | 0.18935 | 0 | 7.1671 | 0 | 32
0222-Y | 2 | 15.8932 | 0.12584 | 0 | 7.1178 | 0 | 24
0222-Z | 3 | 16.3671 | 0.18329 | 2 | 6.6438 | 0.30103 | 26
0230-A | 1 | 17.2493 | 0.057973 | 0 | 5.7616 | 0 | 16
0230-B | 8 | 18.0356 | 0.44357 | 0 | 4.9753 | 0 | 48
0230-C | 8 | 18.0356 | 0.44357 | 0 | 4.9753 | 0 | 39
0230-D | 6 | 18.0767 | 0.33192 | 0 | 4.9342 | 0 | 43
0230-E | 2 | 17.4411 | 0.11467 | 0 | 5.5699 | 0 | 22
0230-F | 1 | 17.589 | 0.056854 | 0 | 5.4219 | 0 | 31
0230-I | 1 | 20.4 | 0.04902 | 0 | 2.611 | 0 | 10
0230-J | 1 | 22.1178 | 0.045212 | 0 | 0.89315 | 0 | 10
0236-B | 2 | 15.8082 | 0.12652 | 2 | 7.2027 | 0.27767 | 36
0237-C | 6 | 15.5452 | 0.38597 | 0 | 7.4658 | 0 | 27
0237-F | 0 | 15.074 | 0 | 3 | 7.937 | 0.37798 | 26
0237-G | 1 | 17.1726 | 0.058232 | 1 | 5.8384 | 0.17128 | 26
0237-I | 2 | 18.9863 | 0.10534 | 1 | 4.0247 | 0.24847 | 28
0237-N | 2 | 15.6493 | 0.1278 | 0 | 7.3616 | 0 | 25
0237-O | 2 | 15.4274 | 0.12964 | 1 | 7.5836 | 0.13186 | 40
0237-P | 1 | 15.3671 | 0.065074 | 0 | 7.6438 | 0 | 45
0237-Q | 3 | 15.4274 | 0.19446 | 0 | 7.5836 | 0 | 28
0237-S | 0 | 15.6795 | 0 | 1 | 7.3315 | 0.1364 | 32
0239.1-A-FT | 1 | 20.1233 | 0.049694 | 0 | 2.8877 | 0 | 4
0240-C | 1 | 15.1562 | 0.06598 | 0 | 7.8548 | 0 | 24
0240-D | 2 | 15.5589 | 0.12854 | 0 | 7.4521 | 0 | 23
0240-G | 2 | 17.7616 | 0.1126 | 1 | 5.2493 | 0.1905 | 33
0350-A | 1 | 17.3781 | 0.057544 | 0 | 5.6329 | 0 | 30
0350-D | 2 | 18.9753 | 0.1054 | 0 | 4.0356 | 0 | 34
0350-E | 1 | 18.5918 | 0.053787 | 0 | 4.4192 | 0 | 32
0350-F | 2 | 18.7781 | 0.10651 | 2 | 4.2329 | 0.47249 | 41
0350-G | 3 | 17.7452 | 0.16906 | 0 | 5.2658 | 0 | 26
0350-H | 1 | 17.7808 | 0.05624 | 0 | 5.2301 | 0 | 40
0350-I | 1 | 17.6932 | 0.056519 | 0 | 5.3178 | 0 | 24
0350-J | 1 | 18.5699 | 0.053851 | 0 | 4.4411 | 0 | 24
0350-K | 1 | 18.0712 | 0.055337 | 0 | 4.9397 | 0 | 32
0350-L | 2 | 18.7425 | 0.10671 | 0 | 4.2685 | 0 | 11
0350-M | 1 | 18.7425 | 0.053355 | 0 | 4.2685 | 0 | 3
0350-N-FT | 2 | 18.9342 | 0.10563 | 0 | 4.0767 | 0 | 8
0358-C | 1 | 15.4027 | 0.064924 | 2 | 7.6082 | 0.26287 | 30
0358-D | 1 | 14.8575 | 0.067306 | 1 | 8.1534 | 0.12265 | 27
0441-CFSP | 1 | 15.8055 | 0.063269 | 0 | 7.2055 | 0 | 25
0442-D | 3 | 14.8959 | 0.2014 | 1 | 8.1151 | 0.12323 | 14
0442-I | 0 | 21.6137 | 0 | 1 | 1.3973 | 0.71569 | 13
0442-L | 1 | 18.9562 | 0.052753 | 0 | 4.0548 | 0 | 29
0442-M | 0 | 15.3178 | 0 | 1 | 7.6932 | 0.12999 | 12
0444-A | 3 | 20.4521 | 0.14668 | 0 | 2.5589 | 0 | 38
0444-A-PH-02 | 2 | 20.4575 | 0.097763 | 0 | 2.5534 | 0 | 30
0444-B | 2 | 20.4575 | 0.097763 | 0 | 2.5534 | 0 | 20
0445-C | 1 | 17.5671 | 0.056925 | 1 | 5.4438 | 0.18369 | 42
0445-D | 1 | 17.7507 | 0.056336 | 0 | 5.2603 | 0 | 31
0445-E | 2 | 19.3644 | 0.10328 | 3 | 3.6466 | 0.82269 | 45
0445-F | 1 | 17.4164 | 0.057417 | 0 | 5.5945 | 0 | 14
0445-G | 1 | 17.4301 | 0.057372 | 0 | 5.5808 | 0 | 3
0445-J | 3 | 19.4027 | 0.15462 | 0 | 3.6082 | 0 | 29
0445-K | 1 | 18.3178 | 0.054592 | 0 | 4.6932 | 0 | 41
0445-M | 1 | 19.3068 | 0.051795 | 2 | 3.7041 | 0.53994 | 14
0445-N | 6 | 18.3836 | 0.32638 | 0 | 4.6274 | 0 | 36
0445-O | 6 | 19.6712 | 0.30501 | 0 | 3.3397 | 0 | 27
0445-Q | 5 | 20.9753 | 0.23838 | 0 | 2.0356 | 0 | 49
0445-R | 3 | 20.9945 | 0.14289 | 0 | 2.0164 | 0 | 38
0445-U | 1 | 18.7068 | 0.053456 | 0 | 4.3041 | 0 | 20
0448-A | 1 | 20.7644 | 0.048159 | 0 | 2.2466 | 0 | 13
0520-B | 2 | 16.6575 | 0.12007 | 0 | 6.3534 | 0 | 49
0520-C | 3 | 16.6356 | 0.18034 | 0 | 6.3753 | 0 | 28
0520-D | 1 | 16.4795 | 0.060682 | 0 | 6.5315 | 0 | 31
0520-F | 5 | 17.5726 | 0.28453 | 0 | 5.4384 | 0 | 60
0520-G | 1 | 16.5753 | 0.060331 | 1 | 6.4356 | 0.15539 | 19
0520-H | 2 | 17.1342 | 0.11673 | 0 | 5.8767 | 0 | 33
0520-I | 2 | 17.1342 | 0.11673 | 0 | 5.8767 | 0 | 54
0520-L | 5 | 17.4438 | 0.28663 | 0 | 5.5671 | 0 | 51
0908-A | 2 | 17.9808 | 0.11123 | 0 | 5.0301 | 0 | 39
0908-C | 1 | 18.1151 | 0.055203 | 0 | 4.8959 | 0 | 39
0908-D | 5 | 18.8356 | 0.26545 | 0 | 4.1753 | 0 | 38
0908-E | 3 | 18.7068 | 0.16037 | 0 | 4.3041 | 0 | 33
0908-F | 4 | 19.6521 | 0.20354 | 0 | 3.3589 | 0 | 37
0908-G | 10 | 22.0192 | 0.45415 | 0 | 0.99178 | 0 | 38
0908-H | 2 | 19.2877 | 0.10369 | 0 | 3.7233 | 0 | 6
0908-I | 2 | 19.4219 | 0.10298 | 0 | 3.589 | 0 | 19
0971-A | 5 | 16.4082 | 0.30473 | 0 | 6.6027 | 0 | 37
0971-C | 1 | 16.7726 | 0.059621 | 0 | 6.2384 | 0 | 33
0971-D | 2 | 16.7726 | 0.11924 | 0 | 6.2384 | 0 | 44
0971-E | 3 | 16.1945 | 0.18525 | 0 | 6.8164 | 0 | 21
0971-F | 2 | 17.1726 | 0.11646 | 0 | 5.8384 | 0 | 34
0971-G | 3 | 16.3014 | 0.18403 | 0 | 6.7096 | 0 | 34
0971-I | 1 | 16.5041 | 0.060591 | 0 | 6.5068 | 0 | 27
0971-J | 6 | 16.4082 | 0.36567 | 2 | 6.6027 | 0.3029 | 33
0971-K | 0 | 16.5041 | 0 | 1 | 6.5068 | 0.15368 | 21
0971-M | 4 | 17.1726 | 0.23293 | 0 | 5.8384 | 0 | 32
0971-Q | 3 | 20.937 | 0.14329 | 0 | 2.074 | 0 | 53
0972-A | 2 | 16.5014 | 0.1212 | 0 | 6.5096 | 0 | 32
0972-B | 2 | 16.3589 | 0.12226 | 0 | 6.6521 | 0 | 26
0972-C | 2 | 16.2055 | 0.12342 | 1 | 6.8055 | 0.14694 | 26
0972-D | 1 | 16.2274 | 0.061624 | 2 | 6.7836 | 0.29483 | 24
0972-E | 0 | 16.3973 | 0 | 1 | 6.6137 | 0.1512 | 31
0973-B | 0 | 15.7945 | 0 | 1 | 7.2164 | 0.13857 | 29
0974-B | 6 | 16.9342 | 0.35431 | 2 | 6.0767 | 0.32913 | 29
0974-C | 7 | 16.7836 | 0.41707 | 0 | 6.2274 | 0 | 27
0974-D | 2 | 16.8274 | 0.11885 | 0 | 6.1836 | 0 | 38
1030-B | 1 | 15.5589 | 0.064272 | 1 | 7.4521 | 0.13419 | 17
1030-C | 5 | 16.3589 | 0.30564 | 1 | 6.6521 | 0.15033 | 42
1030-D | 3 | 18.726 | 0.1602 | 0 | 4.2849 | 0 | 41
1030-E | 1 | 16.8877 | 0.059215 | 0 | 6.1233 | 0 | 35
1030-F | 4 | 16.6384 | 0.24041 | 1 | 6.3726 | 0.15692 | 44
1030-I | 1 | 15.6356 | 0.063957 | 0 | 7.3753 | 0 | 29
1030-J | 5 | 16.8986 | 0.29588 | 1 | 6.1123 | 0.1636 | 42
1030-K | 3 | 16.5753 | 0.18099 | 0 | 6.4356 | 0 | 26
1030-L | 2 | 16.2329 | 0.12321 | 0 | 6.7781 | 0 | 24
1030-M | 1 | 16.0356 | 0.062361 | 1 | 6.9753 | 0.14336 | 31
1030-N | 2 | 16.6274 | 0.12028 | 1 | 6.3836 | 0.15665 | 44
1030-O | 6 | 16.3589 | 0.36677 | 0 | 6.6521 | 0 | 58
1030-Q | 2 | 16.4603 | 0.1215 | 0 | 6.5507 | 0 | 31
1030-R | 3 | 16.6274 | 0.18043 | 0 | 6.3836 | 0 | 36
1030-T | 0 | 15.6411 | 0 | 1 | 7.3699 | 0.13569 | 7
1030-U | 5 | 16.8877 | 0.29607 | 0 | 6.1233 | 0 | 38
1458-B | 2 | 16.389 | 0.12203 | 0 | 6.6219 | 0 | 33
442U | 0 | 21.6137 | 0 | 1 | 1.3973 | 0.71569 | 3
448CC CC | 1 | 21.4164 | 0.046693 | 0 | 1.5945 | 0 | 26
448CCC CC | 1 | 21.5644 | 0.046373 | 0 | 1.4466 | 0 | 12
448HHH | 0 | 20.4575 | 0 | 0 | 2.5534 | 0 | 8
448II | 0 | 20.4137 | 0 | 0 | 2.5973 | 0 | 9
448JJJ | 0 | 20.9178 | 0 | 0 | 2.0932 | 0 | 4
448K | 0 | 21.2767 | 0 | 0 | 1.7342 | 0 | 3
448OOO | 0 | 20.8493 | 0 | 0 | 2.1616 | 0 | 11
448SSS | 0 | 20.7945 | 0 | 0 | 2.2164 | 0 | 9
448V-TU | 0 | 22.7288 | 0 | 0 | 0.28219 | 0 | 3
448WW | 0 | 20.3781 | 0 | 0 | 2.6329 | 0 | 5
448ZZ | 0 | 20.3233 | 0 | 0 | 2.6877 | 0 | 10
449HH | 0 | 18.2493 | 0 | 0 | 4.7616 | 0 | 4
79HH | 0 | 21.8192 | 0 | 0 | 1.1918 | 0 | 2
79J | 0 | 20.2329 | 0 | 0 | 2.7781 | 0 | 4
79TT | 0 | 19.4301 | 0 | 0 | 3.5808 | 0 | 3
79W | 0 | 20.4301 | 0 | 0 | 2.5808 | 0 | 3
C1001-SF_ADDL_WRK | 0 | 20.9288 | 0 | 0 | 2.0822 | 0 | 2
C1215 PH 4 POLE REPLACE/R | 0 | 14.3397 | 0 | 0 | 8.6712 | 0 | 10
C1233,PA LONGSPAN/DESIM R3 | 0 | 13.8466 | 0 | 0 | 9.1644 | 0 | 6
C1250 AERIAL MARKING R1 | 0 | 12.7151 | 0 | 0 | 10.2959 | 0 | 2
C1458 PH 2 #A RECONDUC R5 | 0 | 14.4411 | 0 | 0 | 8.5699 | 0 | 2
C217,RIN:LG SPAN/DESIMI R3 | 0 | 13.6301 | 0 | 0 | 9.3808 | 0 | 3
C220 PH 2 H RECONDUCT R1 | 0 | 14.4521 | 0 | 0 | 8.5589 | 0 | 34
C220 PH 2 J RECONDUCT R6 | 0 | 14.5781 | 0 | 0 | 8.4329 | 0 | 25
C220 PH 4 E POLE CHGOUT | 0 | 13.8795 | 0 | 0 | 9.1315 | 0 | 3
C221 PH4 #E POLE REPLA R1 | 0 | 14.8082 | 0 | 0 | 8.2027 | 0 | 7
C221 PH4 C POLE REPLA R1 | 0 | 14.7781 | 0 | 0 | 8.2329 | 0 | 17
C222 PH 1 #L RECONDUC R1 | 0 | 14.6 | 0 | 0 | 8.411 | 0 | 5
C222 PH 1 #O RECONDUC R1 | 0 | 14.4548 | 0 | 0 | 8.5562 | 0 | 39
C222 PH 1 M RECONDUC R6 | 0 | 14.7534 | 0 | 0 | 8.2575 | 0 | 19
C222 PH 2 V RECONDUCTOR | 0 | 14.8548 | 0 | 0 | 8.1562 | 0 | 35
C222 PH4 SEC2 APOLE CH R1 | 0 | 14.0603 | 0 | 0 | 8.9507 | 0 | 4
C222 PH4 SEC2 BPOLE CH R1 | 0 | 14.3479 | 0 | 0 | 8.663 | 0 | 12
C233, MN: RECONDUCTOR R4 | 0 | 13.0795 | 0 | 0 | 9.9315 | 0 | 38
C236 PH 2 A RECONDUCTOR | 0 | 14.4795 | 0 | 0 | 8.5315 | 0 | 19
C237 PH 2 L RECONDUCTOR | 0 | 14.7589 | 0 | 0 | 8.2521 | 0 | 30
C239: RELOCATION TO MITI R5 | 0 | 13.4356 | 0 | 0 | 9.5753 | 0 | 3
C240 PH 2 A RECONDUCT R1 | 0 | 14.8274 | 0 | 0 | 8.1836 | 0 | 32
C240 PH 2 H RECONDUCT R1 | 0 | 14.8877 | 0 | 0 | 8.1233 | 0 | 8
C350,LI:LG SPA/DESIMILAR W | 0 | 13.8329 | 0 | 0 | 9.1781 | 0 | 7
C357:2011 CFSP WS,TW ON R4 | 0 | 13.5616 | 0 | 0 | 9.4493 | 0 | 7
C441 PHASE 4RECONDCTR P R6 | 0 | 13.2822 | 0 | 0 | 9.7288 | 0 | 7
C441: REBUILD P40714 TO R13 | 0 | 13.3973 | 0 | 0 | 9.6137 | 0 | 10
C442 PH 2 K RECONDUCT R7 | 0 | 15.1562 | 0 | 0 | 7.8548 | 0 | 32
C442 PH 4 APOLE CHGOUT R1 | 0 | 14.1589 | 0 | 0 | 8.8521 | 0 | 5
C442 PH 4 CPOLE CHGOUT R1 | 0 | 14.5534 | 0 | 0 | 8.4575 | 0 | 9
C521,AV:LG SPAN/DESIMILAR | 0 | 14.1178 | 0 | 0 | 8.8932 | 0 | 4
C73 PH 2 I RECONDUCTO R1 | 0 | 14.8959 | 0 | 0 | 8.1151 | 0 | 8
C73 PH 2 JPOLE CHGOUT/ R1 | 0 | 15.2575 | 0 | 0 | 7.7534 | 0 | 6
C73 PH 4 FPOLE CHGOUT/ R8 | 0 | 14.1973 | 0 | 0 | 8.8137 | 0 | 7
C78 PH2 F RECONDUCTOR | 0 | 15.4082 | 0 | 0 | 7.6027 | 0 | 12
C78 PH4 APOLE CHGOUT/R R1 | 0 | 14.0027 | 0 | 0 | 9.0082 | 0 | 8
C79 PH 1 N RECONDUCTO R2 | 0 | 14.4822 | 0 | 0 | 8.5288 | 0 | 6
C79 PH4 SEC 2 F POLE R1 | 0 | 14.6192 | 0 | 0 | 8.3918 | 0 | 14
C79 PH4 SEC 2 H POLE R1 | 0 | 14.526 | 0 | 0 | 8.4849 | 0 | 22
C79 PH4 SEC 2 L POLE R1 | 0 | 14.3753 | 0 | 0 | 8.6356 | 0 | 15
C908:LONG SPAN RFS REL R2 | 0 | 12.8904 | 0 | 0 | 10.1205 | 0 | 7
C974 E RECONDUCTOR R1 | 0 | 15.2 | 0 | 0 | 7.811 | 0 | 24
CNF-C79A | 0 | 19.726 | 0 | 0 | 3.2849 | 0 | 2
ESH C0442 A TH | 0 | 20.9753 | 0 | 0 | 2.0356 | 0 | 2
Track 2 530000153622 | 0 | 18.6384 | 0 | 0 | 4.3726 | 0 | 13
Track 2 530000153928 | 0 | 19.5644 | 0 | 0 | 3.4466 | 0 | 6
0073-H | 0 | 16.2521 | 0 | 0 | 6.7589 | 0 | 23
0075-A | 0 | 17.1014 | 0 | 0 | 5.9096 | 0 | 21
0079-I | 0 | 14.3288 | 0 | 0 | 8.6822 | 0 | 24
0157-AA (ASD) | 0 | 22.2411 | 0 | 0 | 0.76986 | 0 | 6
0157-CC | 0 | 19.9397 | 0 | 0 | 3.0712 | 0 | 8
0157-FF | 0 | 20.7452 | 0 | 0 | 2.2658 | 0 | 10
0157-I | 0 | 19.5562 | 0 | 0 | 3.4548 | 0 | 22
0157-K | 0 | 19.5753 | 0 | 0 | 3.4356 | 0 | 44
0157-L | 0 | 20.1205 | 0 | 0 | 2.8904 | 0 | 37
0157-M | 0 | 19.0384 | 0 | 0 | 3.9726 | 0 | 37
0157-N | 0 | 20.5726 | 0 | 0 | 2.4384 | 0 | 36
0157-Q | 0 | 19.1151 | 0 | 0 | 3.8959 | 0 | 21
0157-U | 0 | 19.3068 | 0 | 0 | 3.7041 | 0 | 28
0176-B | 0 | 16.3507 | 0 | 0 | 6.6603 | 0 | 23
0176-G | 0 | 16.0411 | 0 | 0 | 6.9699 | 0 | 18
0176-M | 0 | 20.6877 | 0 | 0 | 2.3233 | 0 | 10
0211-FTZAP-FT | 0 | 19.7041 | 0 | 0 | 3.3068 | 0 | 5
0212-AA | 0 | 20.9836 | 0 | 0 | 2.0274 | 0 | 9
0212-DD (ASD) | 0 | 20.8301 | 0 | 0 | 2.1808 | 0 | 5
0212-FF | 0 | 20.1589 | 0 | 0 | 2.8521 | 0 | 17
0212-G | 0 | 19.5562 | 0 | 0 | 3.4548 | 0 | 36
0212-H | 0 | 19.6137 | 0 | 0 | 3.3973 | 0 | 18
0212-K | 0 | 20.8219 | 0 | 0 | 2.189 | 0 | 48
0212-K-PH-02 | 0 | 20.9753 | 0 | 0 | 2.0356 | 0 | 8
0212-L | 0 | 21.1863 | 0 | 0 | 1.8247 | 0 | 38
0212-M | 0 | 20.3151 | 0 | 0 | 2.6959 | 0 | 8
0212-S | 0 | 21.0411 | 0 | 0 | 1.9699 | 0 | 35
0212-W-PH-02 | 0 | 20.2904 | 0 | 0 | 2.7205 | 0 | 6
0212-Y | 0 | 20.937 | 0 | 0 | 2.074 | 0 | 18
0212-Z | 0 | 21.1945 | 0 | 0 | 1.8164 | 0 | 6
0217-I | 0 | 17.6466 | 0 | 0 | 5.3644 | 0 | 10
0217-L | 0 | 18.2685 | 0 | 0 | 4.7425 | 0 | 22
0217-O | 0 | 17.674 | 0 | 0 | 5.337 | 0 | 17
0217-S | 0 | 18.0767 | 0 | 0 | 4.9342 | 0 | 18
0220-P | 0 | 15.8274 | 0 | 0 | 7.1836 | 0 | 14
0221-Q | 0 | 17.1342 | 0 | 0 | 5.8767 | 0 | 29
0221-U | 0 | 17.5288 | 0 | 0 | 5.4822 | 0 | 18
0222-DD | 0 | 20.0356 | 0 | 0 | 2.9753 | 0 | 5
0222-G | 0 | 18.9068 | 0 | 0 | 4.1041 | 0 | 10
0222-GG | 0 | 19.326 | 0 | 0 | 3.6849 | 0 | 20
0222-TT | 0 | 20.3425 | 0 | 0 | 2.6685 | 0 | 11
0237-B | 0 | 16.3589 | 0 | 0 | 6.6521 | 0 | 21
0240-Z-FT | 0 | 19.5753 | 0 | 0 | 3.4356 | 0 | 2
0350-B | 0 | 17.3781 | 0 | 0 | 5.6329 | 0 | 30
0350-C | 0 | 17.2658 | 0 | 0 | 5.7452 | 0 | 9
0350-O (ASD) | 0 | 18.9534 | 0 | 0 | 4.0575 | 0 | 5
0441-A-TH | 0 | 21.8 | 0 | 0 | 1.211 | 0 | 5
0444-B-FT-02 | 0 | 20.411 | 0 | 0 | 2.6 | 0 | 2
0445-X | 0 | 20.3123 | 0 | 0 | 2.6986 | 0 | 15
0448-C-FT | 0 | 19.0082 | 0 | 0 | 4.0027 | 0 | 2
0520-A | 0 | 16.6356 | 0 | 0 | 6.3753 | 0 | 24
0520-E | 0 | 17.4411 | 0 | 0 | 5.5699 | 0 | 33
0520-J | 0 | 17.1342 | 0 | 0 | 5.8767 | 0 | 17
0520-K | 0 | 17.4822 | 0 | 0 | 5.5288 | 0 | 47
0520-M | 0 | 17.2301 | 0 | 0 | 5.7808 | 0 | 29
0520-N | 0 | 17.5726 | 0 | 0 | 5.4384 | 0 | 44
0520-O (ASD) | 0 | 20.6466 | 0 | 0 | 2.3644 | 0 | 12
0520-P (ASD) | 0 | 20.8712 | 0 | 0 | 2.1397 | 0 | 12
0859-SUNHILL_RANCH | 0 | 20.6274 | 0 | 0 | 2.3836 | 0 | 3
0908-B | 0 | 18.8356 | 0 | 0 | 4.1753 | 0 | 25
0908-I-FT | 0 | 19.7068 | 0 | 0 | 3.3041 | 0 | 9
0908-J | 0 | 19.2493 | 0 | 0 | 3.7616 | 0 | 11
0908-K | 0 | 18.7068 | 0 | 0 | 4.3041 | 0 | 10
0908-M | 0 | 20.5726 | 0 | 0 | 2.4384 | 0 | 8
0908-M-PH-02 | 0 | 21.7452 | 0 | 0 | 1.2658 | 0 | 6
0971-L | 0 | 17.1726 | 0 | 0 | 5.8384 | 0 | 33
0971-N | 0 | 20.9753 | 0 | 0 | 2.0356 | 0 | 28
0971-O | 0 | 16.6356 | 0 | 0 | 6.3753 | 0 | 37
0971-P | 0 | 16.7918 | 0 | 0 | 6.2192 | 0 | 23
0973-WILDCAT CYN-R1-FTZ-1 | 0 | 13.6822 | 0 | 0 | 9.3288 | 0 | 3
0974-A | 0 | 16.9534 | 0 | 0 | 6.0575 | 0 | 5
0974-F | 0 | 16.8685 | 0 | 0 | 6.1425 | 0 | 3
1030-A | 0 | 14.2384 | 0 | 0 | 8.7726 | 0 | 17
1030-G | 0 | 16.5753 | 0 | 0 | 6.4356 | 0 | 25
1030-H | 0 | 15.789 | 0 | 0 | 7.2219 | 0 | 26
1030-P | 0 | 16.5753 | 0 | 0 | 6.4356 | 0 | 33
1030-P-TU | 0 | 22.5452 | 0 | 0 | 0.46575 | 0 | 2
1030-S | 0 | 15.6137 | 0 | 0 | 7.3973 | 0 | 13
1030-U-TU | 0 | 20.7699 | 0 | 0 | 2.2411 | 0 | 2
1233B | 0 | 20.4712 | 0 | 0 | 2.5397 | 0 | 13
240A | 0 | 20.3425 | 0 | 0 | 2.6685 | 0 | 4
355C-TU | 0 | 21.2986 | 0 | 0 | 1.7123 | 0 | 4
442G | 0 | 20.1699 | 0 | 0 | 2.8411 | 0 | 3
442S | 0 | 20.4767 | 0 | 0 | 2.5342 | 0 | 3
442W | 0 | 22.0356 | 0 | 0 | 0.97534 | 0 | 2
442X | 0 | 22.5836 | 0 | 0 | 0.4274 | 0 | 2
448AA CC | 0 | 21.9726 | 0 | 0 | 1.0384 | 0 | 8
448BB | 0 | 20.726 | 0 | 0 | 2.2849 | 0 | 7
448CCC2 CC | 0 | 21.5699 | 0 | 0 | 1.4411 | 0 | 2
448DD | 0 | 20.5452 | 0 | 0 | 2.4658 | 0 | 7
448FF | 0 | 20.7178 | 0 | 0 | 2.2932 | 0 | 11
448G | 0 | 20.6685 | 0 | 0 | 2.3425 | 0 | 10
448GG | 0 | 20.5973 | 0 | 0 | 2.4137 | 0 | 6
448GGG | 0 | 20.4438 | 0 | 0 | 2.5671 | 0 | 2
448HH | 0 | 20.5863 | 0 | 0 | 2.4247 | 0 | 6
Average | 1.5756 | 17.5016 | 0.090028 | 0.30042 | 5.5094 | 0.054529 | 23.1387
Avg no of poles per 100 miles | 2316
Unhardened faults per year per 100 miles | 9.0111
Hardened faults per year per 100 miles | 5.4579
Risk Reduction | 39.43%

## Effectiveness_by_Driver
| Unhardened_Fault | Hardened_Fault | Avg_Unhardend_Fault | Avg_Hardened_Fault
Crew Contact | 13 | 1 | 0.027311 | 0.0021008 |  | Total Hardening Projects | 476
Customer Contact | 98 | 7 | 0.20588 | 0.014706
Equipment | 270 | 52 | 0.56723 | 0.10924 |  | Avg no of poles per 100 miles | 2316
Foreign Object | 134 | 37 | 0.28151 | 0.077731
Miscellaneous | 13 | 1 | 0.027311 | 0.0021008
SDGE/Contractor Contact | 5 | 2 | 0.010504 | 0.0042017
Third Party Contact | 1 | 11 | 0.0021008 | 0.023109
Tree Contact | 32 | 0 | 0.067227 | 0
Undetermined | 14 | 7 | 0.029412 | 0.014706
Weather | 170 | 25 | 0.35714 | 0.052521
| 750 | 143
Risk Driver | Avg_Unhardened Faults | Avg_Unhardened Years | Unhardened faults per operating year average | Avg_Hardened Faults | Avg_Hardened Years | Hardened faults per operating year average | Avg_Poles | Avg_Hardened rate | Avg_Unhardened rate | Risk_Reduction
Crew Contact | 0.027311 | 17.5016 | 0.0015605 | 0.0021008 | 5.5094 | 0.00038132 | 23.1387 | 0.038167 | 0.15619 | 75.56%
Customer Contact | 0.20588 | 17.5016 | 0.011764 | 0.014706 | 5.5094 | 0.0026692 | 23.1387 | 0.26717 | 1.1775 | 77.31%
Equipment Failure | 0.56723 | 17.5016 | 0.03241 | 0.10924 | 5.5094 | 0.019829 | 23.1387 | 1.9847 | 3.244 | 38.82%
Foreign Object | 0.28151 | 17.5016 | 0.016085 | 0.077731 | 5.5094 | 0.014109 | 23.1387 | 1.4122 | 1.61 | 12.29%
Miscellaneous | 0.027311 | 17.5016 | 0.0015605 | 0.0021008 | 5.5094 | 0.00038132 | 23.1387 | 0.038167 | 0.15619 | 75.56%
SDGE/Contractor Contact | 0.010504 | 17.5016 | 0.00060019 | 0.0042017 | 5.5094 | 0.00076264 | 23.1387 | 0.076334 | 0.060074 | -27.07%
Third Party Contact | 0.0021008 | 17.5016 | 0.00012004 | 0.023109 | 5.5094 | 0.0041945 | 23.1387 | 0.41984 | 0.012015 | -3394% | This cause category was introduced in 2020, which explains the limited number of unhardened fault records available. As a result, the model reflects a disproportionately high number of negative risk reduction values, driven by insufficient baseline data for comparison.
Tree Contact | 0.067227 | 17.5016 | 0.0038412 | 0 | 5.5094 | 0 | 23.1387 | 0 | 0.38447 | 100%
Undetermined | 0.029412 | 17.5016 | 0.0016805 | 0.014706 | 5.5094 | 0.0026692 | 23.1387 | 0.26717 | 0.16821 | -58.83%
Weather | 0.35714 | 17.5016 | 0.020406 | 0.052521 | 5.5094 | 0.009533 | 23.1387 | 0.95418 | 2.0425 | 53.28%
[6 empty] | Avg fault rate per year per 100 miles |  | 5.4579 | 9.0111 | 39.43%

## SummaryHFTD_2023_archive (hidden)
Project ID | Unhardened Faults | Unhardened Years | Unhardened faults per operating year average | Hardened Faults | Hardened Years | Hardened faults per operating year average | Poles
0078-D | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0078-E | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0078-G | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0079-A | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0079-M | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0079-P | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0157-B | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0157-D | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0157-G | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0157-H | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0157-J | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0157-T | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0157-V | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0157-W | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0157-X | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0175-A | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0175-B | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0175-C | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0175-D | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0175-E | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0176-A | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0176-C | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0176-D | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0176-E | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0176-F | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0176-H | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0176-I-FT-02 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0176-J | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0176-L | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0182-COUNTRY_CLUB | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0185-CAMINITO_A_CASA | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0212-A | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0212-B | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0212-C-PH-02 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0212-C-PH-03 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0212-D | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0212-E | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0212-F | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0212-GG | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0212-I | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0212-J | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0212-P | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0212-T | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0212-U | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0212-V | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0212-W | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0212-W-FT-02 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0212-X | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0215-A | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0215-B | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0215-C | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0217-AD | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0217-B | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0217-C | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0217-D | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0217-E | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0217-F | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0217-G | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0217-H | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0217-J | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0217-K | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0217-M | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0217-N | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0217-P | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0217-Q | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0217-R | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0217-V | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0217-X (ASD) | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0220-C | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0220-K | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0220-N | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0220-Q | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0221-A | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0221-D-VOLCAN MTN | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0221-F | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0221-G | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0221-H | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0221-I | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0221-J | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0221-K | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0221-L | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0221-N | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0221-O | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0221-R | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0221-S | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0221-V | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0221-W | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0221-Y-PH1-SLAUGHTER | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0222-AA | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0222-BB | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0222-CC | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0222-EE | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0222-FF | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0222-FF-PH-02 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0222-HH | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0222-II | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0222-JJ | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0222-K | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0222-MM | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0222-N | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0222-NN | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0222-PP | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0222-R | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0222-S | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0222-SS (ASD) | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0222-U | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0222-X | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0222-Y | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0222-Z | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0230-A | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0230-B | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0230-C | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0230-D | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0230-E | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0230-F | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0230-J | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0236-B | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0237-C | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0237-F | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0237-G | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0237-I | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0237-N | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0237-O | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0237-P | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0237-Q | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0237-S | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0239.1-A-FT | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0240-C | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0240-D | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0240-G | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0350-A | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0350-D | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0350-E | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0350-F | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0350-G | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0350-H | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0350-I | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0350-J | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0350-K | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0350-L | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0350-M | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0350-N-FT | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0358-C | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0358-D | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0441-CFSP | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0442-D | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0442-I | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0442-L | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0442-M | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0444-A | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0444-A-PH-02 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0444-B | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0445-C | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0445-D | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0445-E | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0445-F | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0445-G | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0445-J | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0445-K | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0445-M | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0445-N | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0445-O | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0445-Q | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0445-R | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0445-U | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0448-A | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0520-B | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0520-C | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0520-D | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0520-F | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0520-G | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0520-H | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0520-I | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0520-L | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0908-A | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0908-C | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0908-D | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0908-E | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0908-F | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0908-G | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0908-I | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0971-A | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0971-C | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0971-D | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0971-E | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0971-F | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0971-G | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0971-J | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0971-K | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0971-M | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0971-Q | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0972-A | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0972-B | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0972-C | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0972-D | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0972-E | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0973-B | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0974-B | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0974-C | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0974-D | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
1030-B | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
1030-C | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
1030-D | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
1030-E | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
1030-F | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
1030-J | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
1030-K | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
1030-L | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
1030-M | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
1030-N | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
1030-O | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
1030-Q | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
1030-R | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
1030-T | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
1030-U | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
1458-B | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
442U | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
448CC CC | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
448CCC CC | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
448NNN | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
448QQQ | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
448RRR | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
448S | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
448T | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
448U | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
448YY | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
79F | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
79M | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
79N | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C1023/C354_NEW_12KV_RECON | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C1023/C354_RFS_FREEWAY_X | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C1215 CWLONG SPAN/DESI R12 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C1215 MAINLINE CFSP W/S R1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C157:2013 CFSP CNF RIDGEPI | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C220 PH 2 I RECONDUCT R8 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C220 PH 2 L RECONDUCT R1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C220 PH 2 M RECONDUCTOR | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C220 PH 2 O RECONDUCTOR | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C220 PH 4 B POLE CHGO R3 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C220 PH 4 D POLE CHGOUT | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C220 PH 4 F POLE CHGO R2 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C220 PH 4 G POLE CHGO R2 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C221 PH4 #B POLE REPLA R1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C221 PH4 D POLE REPLA R2 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C221:ERI 2012 REBUILD | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C221:ERI 2012 REBUILD IM R9 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C222 FIRE RISK MITIG PRJPH | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C222 FIRE RISK MITIG PRO R1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C222 FIRE RISK MITIG PRO R2 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C222 FIRE RISK MITIG PROJP | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C222 PH 1 #Q RECONDUC R3 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C222 PH 1 F RECONDUCTOR | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C222 PH 1 H RECONDUC R1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C222 PH 1 I RECONDUC R7 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C222 PH 1 J RECONDUC R6 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C222 PH 1 P RECONDUC R7 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C222 PH 2 #T RECONDU R11 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C222 PH4 SEC2 CPOLE CHGOU | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C222 PH4 SEC2 DPOLE CH R1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C230: 2013 FIRE HARDNG 4 R2 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C233 LONG SPAN EVAL P61 R18 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C236 PH 2 C RECONDUCTOR | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C236 PH 2 D RECONDUCTOR | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C237 PH 2 A RECONDUCTOR | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C237 PH 2 D RECONDUCT R1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C237 PH 2 E RECONDUCTOR | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C237 PH 2 H RECONDUCT R8 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C237 PH 2 J RECONDUCTOR | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C237 PH 2 M RECONDUCTOR | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C239:2013 RIRAT RELIABILITY | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C240 PH 2 E RECONDUCT R1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C357:2011 CFSP WS,TW ON R12 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C358 PH 2 A RECONDUCTOR | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C358 PH 2 B RECONDUCTOR | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C441 BRLINE CFSP W/S(P1 R1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C441 PH 4 POLE REPLACE R2 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C442 PH 2 J RECONDUCT R8 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C442 PH 4 BPOLE CHGOUT R1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C442 PH 4 FPOLE CHGOUT R1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C442 PH 4 GPOLE CHGOUT R1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C444 BRANCHLN CFSP P4 R1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C444 BRANCHLN CFSP W/S R1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C444 BRANCHLN PH1 P41936 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C444 BRANCHLN PH2 P4196 R1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C444,BU:2011 CFSP RCNDCT R8 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C445 2012 CFSP WS BRANCH R1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C445,BU:LG SPAN/DESIMI R16 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C67,BAR:LG SPAN/DESIMIL R3 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C73 PH 4 APOLE CHGOUT/ R9 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C73 PH 4 CPOLE CHGOUT R11 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C73 PH 4 EPOLE CHGOUT R11 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C78 PH4 BPOLE CHGOUT/R R8 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C78 PH4 CPOLE CHGOUT/RECO | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C79 FIRE RISK MITIGATION R2 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C79 PH 1 #O RECONDUCTOR | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C79 PH 2 R RECONDUCTOR | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C79 PH4 SEC 2 #G POLE R6 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C79 PH4 SEC 2 E POLE R1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C79 PH4 SEC 2 K POLE R7 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
C973 PH 2 #A RECOND | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
CNF-C79B | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
CNF-TL629A | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
CPE1-D | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
CPE1-PH-04-B | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
CRA1 PH 2 A RECONDUCTOR | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
CRB1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
PE1 PH 4 A POLE CHGO R11 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
PE1 PH 4#C POLE CHGOUT/RE | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Track 2 530000154309 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0073-H | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0075-A | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0079-I | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0157-AA (ASD) | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0157-CC | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0157-FF | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0157-I | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0157-K | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0157-L | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0157-M | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0157-N | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0157-Q | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0157-U | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0176-B | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0176-G | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0176-M | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0211-FTZAP-FT | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0212-AA | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0212-DD (ASD) | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0212-FF | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0212-G | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0212-H | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0212-K | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0212-K-PH-02 | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0212-L | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0212-M | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0212-Q | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0212-S | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0212-W-PH-02 | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0212-Y | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0212-Z | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0217-I | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0217-L | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0217-O | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0217-S | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0220-P | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0221-M | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0221-P | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0221-Q | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0221-U | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0222-DD | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0222-G | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0222-GG | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0222-TT | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0222-UU | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0222-W | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0230-I | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0237-B | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0240-Z-FT | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0350-B | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0350-C | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0350-O (ASD) | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0441-A-TH | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0444-B-FT-02 | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0445-X | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0448-C-FT | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0520-A | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0520-E | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0520-J | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0520-K | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0520-M | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0520-N | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0520-O (ASD) | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0520-P (ASD) | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0859-SUNHILL_RANCH | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0908-B | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0908-H | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0908-I-FT | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0908-J | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0908-K | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0908-M | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0908-M-PH-02 | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0971-I | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0971-L | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0971-N | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0971-O | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0971-P | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0973-WILDCAT CYN-R1-FTZ-1 | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0974-A | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
0974-F | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
1030-A | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
1030-G | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
1030-H | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
1030-I | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
1030-P | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
1030-P-TU | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
1030-S | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
1030-U-TU | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
1233B | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
240A | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
355C-TU | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
442G | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
442S | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
442W | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
442X | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
448AA CC | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
448BB | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
448CCC2 CC | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
448DD | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
448FF | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
448G | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
448GG | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
448GGG | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
448HH | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
448HHH | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
448II | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
448JJJ | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
448K | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
448OOO | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
448SSS | 0 | #REF! | #REF! | 0 | #REF! | #REF! | #REF!
Average | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Unhardened faults per year per 100 miles | #REF!
Hardened faults per year per 100 miles | #REF!
Reduction | #REF!

## SummaryHFTD_2019_archive (hidden)
Project ID | Unhardened Faults | Unhardened Years | Unhardened faults per operating year average | Hardened Faults | Hardened Years | Hardened faults per operating year average | Poles
0078-D | 6 | 16.6712 | 0.3599 | 0 | 2.337 | 0 | 26
0078-E | 3 | 15.2329 | 0.19694 | 0 | 3.7753 | 0 | 8
0078-G | 1 | 16.674 | 0.059974 | 0 | 2.3342 | 0 | 26
0079-A | 2 | 15.2219 | 0.13139 | 3 | 3.7863 | 0.79233 | 29
0079-M | 2 | 15.2356 | 0.13127 | 1 | 3.7726 | 0.26507 | 18
0079-P | 1 | 14.9315 | 0.066972 | 1 | 4.0767 | 0.2453 | 45
0157-T | 3 | 18.9562 | 0.15826 | 0 | 0.052055 | 0 | 8
0175-A | 2 | 16.0603 | 0.12453 | 0 | 2.9479 | 0 | 40
0175-B | 5 | 16.3068 | 0.30662 | 0 | 2.7014 | 0 | 32
0175-C | 2 | 16.2521 | 0.12306 | 0 | 2.7562 | 0 | 38
0175-D | 1 | 16.1178 | 0.062043 | 2 | 2.8904 | 0.69194 | 17
0175-E | 1 | 15.8274 | 0.063182 | 0 | 3.1808 | 0 | 9
0176-A | 2 | 16.2712 | 0.12292 | 2 | 2.737 | 0.73073 | 32
0176-C | 3 | 16.1178 | 0.18613 | 0 | 2.8904 | 0 | 24
0176-D | 4 | 18.0356 | 0.22178 | 0 | 0.9726 | 0 | 24
0176-E | 1 | 16.3123 | 0.061303 | 0 | 2.6959 | 0 | 28
0176-F | 0 | 17.6548 | 0 | 1 | 1.3534 | 0.73887 | 31
0176-H | 2 | 18.0356 | 0.11089 | 0 | 0.9726 | 0 | 17
0176-J | 2 | 16.3836 | 0.12207 | 0 | 2.6247 | 0 | 23
0212-A | 10 | 18.9973 | 0.52639 | 0 | 0.010959 | 0 | 71
0212-B | 19 | 18.9973 | 1.0001 | 0 | 0.010959 | 0 | 47
0215-A | 5 | 17.4932 | 0.28583 | 0 | 1.5151 | 0 | 27
0215-B | 5 | 17.4438 | 0.28663 | 0 | 1.5644 | 0 | 29
0215-C | 2 | 18.6877 | 0.10702 | 0 | 0.32055 | 0 | 32
0217-B | 2 | 17.6466 | 0.11334 | 0 | 1.3616 | 0 | 23
0217-C | 2 | 17.1726 | 0.11646 | 0 | 1.8356 | 0 | 37
0217-D | 4 | 18.9753 | 0.2108 | 0 | 0.032877 | 0 | 33
0217-E | 3 | 18.9753 | 0.1581 | 0 | 0.032877 | 0 | 37
0217-F | 1 | 17.3781 | 0.057544 | 0 | 1.6301 | 0 | 28
0217-G | 1 | 17.674 | 0.05658 | 0 | 1.3342 | 0 | 18
0217-H | 3 | 18.2685 | 0.16422 | 0 | 0.73973 | 0 | 26
0217-J | 5 | 18.4603 | 0.27085 | 0 | 0.54795 | 0 | 26
0217-K | 1 | 18.2685 | 0.054739 | 0 | 0.73973 | 0 | 34
0217-M | 4 | 18.1808 | 0.22001 | 0 | 0.8274 | 0 | 31
0217-N | 2 | 18.1041 | 0.11047 | 0 | 0.90411 | 0 | 29
0217-P | 1 | 18.2685 | 0.054739 | 0 | 0.73973 | 0 | 27
0217-Q | 1 | 18.4603 | 0.05417 | 0 | 0.54795 | 0 | 30
0217-R | 6 | 18.7096 | 0.32069 | 0 | 0.29863 | 0 | 26
0217-V | 1 | 18.9781 | 0.052692 | 0 | 0.030137 | 0 | 5
0217-X (ASD) | 1 | 18.937 | 0.052807 | 0 | 0.071233 | 0 | 5
0220-C | 2 | 15.2767 | 0.13092 | 0 | 3.7315 | 0 | 18
0220-K | 2 | 15.789 | 0.12667 | 0 | 3.2192 | 0 | 28
0220-N | 6 | 15.8274 | 0.37909 | 0 | 3.1808 | 0 | 28
0220-Q | 3 | 16.3425 | 0.18357 | 0 | 2.6658 | 0 | 11
0221-A | 9 | 17.2685 | 0.52118 | 1 | 1.7397 | 0.5748 | 32
0221-F | 3 | 17.4164 | 0.17225 | 0 | 1.5918 | 0 | 36
0221-G | 2 | 17.0904 | 0.11702 | 0 | 1.9178 | 0 | 22
0221-H | 1 | 15.8055 | 0.063269 | 0 | 3.2027 | 0 | 22
0221-I | 1 | 16.3863 | 0.061027 | 0 | 2.6219 | 0 | 32
0221-J | 3 | 16.0055 | 0.18744 | 0 | 3.0027 | 0 | 36
0221-K | 2 | 15.6137 | 0.12809 | 0 | 3.3945 | 0 | 42
0221-L | 0 | 15.9671 | 0 | 1 | 3.0411 | 0.32883 | 29
0221-N | 2 | 15.9671 | 0.12526 | 0 | 3.0411 | 0 | 38
0221-O | 1 | 17.3644 | 0.057589 | 0 | 1.6438 | 0 | 14
0221-S | 2 | 17.6767 | 0.11314 | 0 | 1.3315 | 0 | 30
0221-V | 1 | 15.9233 | 0.062801 | 1 | 3.0849 | 0.32416 | 27
0221-W | 1 | 17.6548 | 0.056642 | 0 | 1.3534 | 0 | 13
0221-Y-PH1-SLAUGHTER | 1 | 17.5726 | 0.056907 | 0 | 1.4356 | 0 | 2
0222-AA | 3 | 16.5945 | 0.18078 | 1 | 2.4137 | 0.4143 | 29
0222-K | 3 | 15.5452 | 0.19299 | 1 | 3.463 | 0.28877 | 32
0222-N | 1 | 15.6493 | 0.063901 | 0 | 3.3589 | 0 | 31
0222-R | 3 | 15.2795 | 0.19634 | 0 | 3.7288 | 0 | 45
0222-S | 1 | 15.1753 | 0.065896 | 0 | 3.8329 | 0 | 18
0222-U | 2 | 15.5726 | 0.12843 | 1 | 3.4356 | 0.29107 | 36
0222-X | 3 | 15.8438 | 0.18935 | 0 | 3.1644 | 0 | 32
0222-Y | 1 | 15.8932 | 0.06292 | 0 | 3.1151 | 0 | 24
0222-Z | 3 | 16.3671 | 0.18329 | 0 | 2.6411 | 0 | 26
0230-A | 1 | 17.2493 | 0.057973 | 0 | 1.7589 | 0 | 16
0230-B | 8 | 18.0356 | 0.44357 | 0 | 0.9726 | 0 | 48
0230-C | 8 | 18.0356 | 0.44357 | 0 | 0.9726 | 0 | 39
0230-D | 6 | 18.0767 | 0.33192 | 0 | 0.93151 | 0 | 43
0230-E | 2 | 17.4411 | 0.11467 | 0 | 1.5671 | 0 | 22
0230-F | 1 | 17.589 | 0.056854 | 0 | 1.4192 | 0 | 31
0236-B | 2 | 15.8082 | 0.12652 | 1 | 3.2 | 0.3125 | 36
0237-C | 6 | 15.5452 | 0.38597 | 0 | 3.463 | 0 | 27
0237-F | 0 | 15.074 | 0 | 1 | 3.9342 | 0.25418 | 26
0237-G | 1 | 17.1726 | 0.058232 | 0 | 1.8356 | 0 | 26
0237-I | 2 | 18.9863 | 0.10534 | 0 | 0.021918 | 0 | 28
0237-N | 1 | 15.6493 | 0.063901 | 0 | 3.3589 | 0 | 25
0237-O | 2 | 15.4274 | 0.12964 | 0 | 3.5808 | 0 | 40
0237-P | 1 | 15.3671 | 0.065074 | 0 | 3.6411 | 0 | 45
0237-Q | 3 | 15.4274 | 0.19446 | 0 | 3.5808 | 0 | 28
0240-C | 1 | 15.1562 | 0.06598 | 0 | 3.8521 | 0 | 24
0240-D | 2 | 15.5589 | 0.12854 | 0 | 3.4493 | 0 | 23
0240-G | 2 | 17.7616 | 0.1126 | 1 | 1.2466 | 0.8022 | 33
0350-A | 1 | 17.3781 | 0.057544 | 0 | 1.6301 | 0 | 30
0350-D | 2 | 18.9753 | 0.1054 | 0 | 0.032877 | 0 | 34
0350-E | 1 | 18.5918 | 0.053787 | 0 | 0.41644 | 0 | 32
0350-F | 2 | 18.7781 | 0.10651 | 0 | 0.23014 | 0 | 41
0350-G | 3 | 17.7452 | 0.16906 | 0 | 1.263 | 0 | 26
0350-H | 1 | 17.7808 | 0.05624 | 0 | 1.2274 | 0 | 40
0350-I | 1 | 17.6932 | 0.056519 | 0 | 1.3151 | 0 | 24
0350-J | 1 | 18.5699 | 0.053851 | 0 | 0.43836 | 0 | 24
0350-K | 1 | 18.0712 | 0.055337 | 0 | 0.93699 | 0 | 32
0350-L | 2 | 18.7425 | 0.10671 | 0 | 0.26575 | 0 | 11
0350-M | 1 | 18.7425 | 0.053355 | 0 | 0.26575 | 0 | 3
0350-N-FT | 2 | 18.9342 | 0.10563 | 0 | 0.073973 | 0 | 8
0358-C | 1 | 15.4027 | 0.064924 | 2 | 3.6055 | 0.55471 | 30
0358-D | 1 | 14.8575 | 0.067306 | 0 | 4.1507 | 0 | 27
0441-CFSP | 1 | 15.8055 | 0.063269 | 0 | 3.2027 | 0 | 25
0442-D | 3 | 14.8959 | 0.2014 | 0 | 4.1123 | 0 | 14
0442-L | 1 | 18.9562 | 0.052753 | 0 | 0.052055 | 0 | 29
0442-M | 0 | 15.3178 | 0 | 1 | 3.6904 | 0.27097 | 12
0445-C | 1 | 17.5671 | 0.056925 | 1 | 1.4411 | 0.69392 | 42
0445-D | 1 | 17.7507 | 0.056336 | 0 | 1.2575 | 0 | 31
0445-F | 1 | 17.4164 | 0.057417 | 0 | 1.5918 | 0 | 14
0445-G | 1 | 17.4301 | 0.057372 | 0 | 1.5781 | 0 | 3
0445-K | 1 | 18.3178 | 0.054592 | 0 | 0.69041 | 0 | 41
0445-N | 6 | 18.3836 | 0.32638 | 0 | 0.62466 | 0 | 36
0445-U | 1 | 18.7068 | 0.053456 | 0 | 0.30137 | 0 | 20
0520-B | 1 | 16.6575 | 0.060033 | 0 | 2.3507 | 0 | 49
0520-C | 3 | 16.6356 | 0.18034 | 0 | 2.3726 | 0 | 28
0520-D | 1 | 16.4795 | 0.060682 | 0 | 2.5288 | 0 | 31
0520-F | 5 | 17.5726 | 0.28453 | 0 | 1.4356 | 0 | 60
0520-G | 1 | 16.5753 | 0.060331 | 0 | 2.4329 | 0 | 19
0520-H | 2 | 17.1342 | 0.11673 | 0 | 1.874 | 0 | 33
0520-I | 2 | 17.1342 | 0.11673 | 0 | 1.874 | 0 | 54
0520-L | 5 | 17.4438 | 0.28663 | 0 | 1.5644 | 0 | 51
0908-A | 1 | 17.9808 | 0.055615 | 0 | 1.0274 | 0 | 39
0908-C | 1 | 18.1151 | 0.055203 | 0 | 0.89315 | 0 | 39
0908-D | 5 | 18.8356 | 0.26545 | 0 | 0.1726 | 0 | 38
0908-E | 2 | 18.7068 | 0.10691 | 0 | 0.30137 | 0 | 33
0971-A | 5 | 16.4082 | 0.30473 | 0 | 2.6 | 0 | 37
0971-C | 1 | 16.7726 | 0.059621 | 0 | 2.2356 | 0 | 33
0971-D | 2 | 16.7726 | 0.11924 | 0 | 2.2356 | 0 | 44
0971-E | 3 | 16.1945 | 0.18525 | 0 | 2.8137 | 0 | 21
0971-F | 2 | 17.1726 | 0.11646 | 0 | 1.8356 | 0 | 34
0971-G | 3 | 16.3014 | 0.18403 | 0 | 2.7068 | 0 | 34
0971-J | 6 | 16.4082 | 0.36567 | 1 | 2.6 | 0.38462 | 33
0971-M | 4 | 17.1726 | 0.23293 | 0 | 1.8356 | 0 | 32
0972-A | 2 | 16.5014 | 0.1212 | 0 | 2.5068 | 0 | 32
0972-B | 2 | 16.3589 | 0.12226 | 0 | 2.6493 | 0 | 26
0972-C | 2 | 16.2055 | 0.12342 | 1 | 2.8027 | 0.35679 | 26
0972-D | 1 | 16.2274 | 0.061624 | 0 | 2.7808 | 0 | 24
0974-B | 4 | 16.9342 | 0.23621 | 0 | 2.074 | 0 | 29
0974-C | 7 | 16.7836 | 0.41707 | 0 | 2.2247 | 0 | 27
0974-D | 2 | 16.8274 | 0.11885 | 0 | 2.1808 | 0 | 38
1030-B | 1 | 15.5589 | 0.064272 | 0 | 3.4493 | 0 | 17
1030-C | 5 | 16.3589 | 0.30564 | 1 | 2.6493 | 0.37746 | 42
1030-D | 3 | 18.726 | 0.1602 | 0 | 0.28219 | 0 | 41
1030-E | 1 | 16.8877 | 0.059215 | 0 | 2.1205 | 0 | 35
1030-F | 4 | 16.6384 | 0.24041 | 1 | 2.3699 | 0.42197 | 44
1030-J | 5 | 16.8986 | 0.29588 | 0 | 2.1096 | 0 | 42
1030-K | 3 | 16.5753 | 0.18099 | 0 | 2.4329 | 0 | 26
1030-L | 2 | 16.2329 | 0.12321 | 0 | 2.7753 | 0 | 24
1030-M | 1 | 16.0356 | 0.062361 | 0 | 2.9726 | 0 | 31
1030-N | 2 | 16.6274 | 0.12028 | 0 | 2.3808 | 0 | 44
1030-O | 5 | 16.3589 | 0.30564 | 0 | 2.6493 | 0 | 58
1030-Q | 2 | 16.4603 | 0.1215 | 0 | 2.5479 | 0 | 31
1030-R | 3 | 16.6274 | 0.18043 | 0 | 2.3808 | 0 | 36
1030-T | 0 | 15.6411 | 0 | 1 | 3.3671 | 0.29699 | 7
1030-U | 5 | 16.8877 | 0.29607 | 0 | 2.1205 | 0 | 38
1458-B | 2 | 16.389 | 0.12203 | 0 | 2.6192 | 0 | 33
C1215 MAINLINE CFSP W/S R1 | 2 | 14.3397 | 0.13947 | 2 | 4.6685 | 0.4284 | 17
C157:2013 CFSP CNF RIDGEPI | 1 | 13.5973 | 0.073544 | 0 | 5.411 | 0 | 3
C220 PH 2 I RECONDUCT R8 | 3 | 14.6712 | 0.20448 | 0 | 4.337 | 0 | 50
C220 PH 2 L RECONDUCT R1 | 1 | 14.5589 | 0.068686 | 0 | 4.4493 | 0 | 29
C220 PH 2 O RECONDUCTOR | 2 | 14.8822 | 0.13439 | 0 | 4.126 | 0 | 15
C220 PH 4 G POLE CHGO R2 | 0 | 14.8274 | 0 | 2 | 4.1808 | 0.47837 | 8
C221 PH4 D POLE REPLA R2 | 2 | 15.3973 | 0.12989 | 1 | 3.611 | 0.27693 | 4
C221:ERI 2012 REBUILD | 3 | 14.6658 | 0.20456 | 0 | 4.3425 | 0 | 4
C221:ERI 2012 REBUILD IM R9 | 0 | 12.8164 | 0 | 2 | 6.1918 | 0.32301 | 11
C222 FIRE RISK MITIG PRJPH | 3 | 14.1233 | 0.21242 | 0 | 4.8849 | 0 | 74
C222 FIRE RISK MITIG PRO R1 | 1 | 14.1096 | 0.070874 | 1 | 4.8986 | 0.20414 | 15
C222 FIRE RISK MITIG PRO R2 | 1 | 13.1836 | 0.075852 | 0 | 5.8247 | 0 | 26
C222 FIRE RISK MITIG PROJP | 4 | 12.9699 | 0.30841 | 0 | 6.0384 | 0 | 51
C222 PH 1 F RECONDUCTOR | 1 | 15.2 | 0.065789 | 0 | 3.8082 | 0 | 24
C222 PH 1 H RECONDUC R1 | 1 | 14.863 | 0.067281 | 0 | 4.1452 | 0 | 10
C222 PH 1 I RECONDUC R7 | 3 | 14.6219 | 0.20517 | 0 | 4.3863 | 0 | 25
C222 PH 1 P RECONDUC R7 | 4 | 14.4219 | 0.27736 | 0 | 4.5863 | 0 | 25
C222 PH 2 #T RECONDU R11 | 2 | 14.8548 | 0.13464 | 0 | 4.1534 | 0 | 23
C222 PH4 SEC2 CPOLE CHGOU | 4 | 14.3342 | 0.27905 | 0 | 4.674 | 0 | 29
C222 PH4 SEC2 DPOLE CH R1 | 1 | 14.0055 | 0.071401 | 0 | 5.0027 | 0 | 22
C230: 2013 FIRE HARDNG 4 R2 | 1 | 14.3123 | 0.06987 | 0 | 4.6959 | 0 | 2
C233 LONG SPAN EVAL P61 R18 | 1 | 13.9808 | 0.071527 | 0 | 5.0274 | 0 | 3
C236 PH 2 C RECONDUCTOR | 2 | 15.3507 | 0.13029 | 0 | 3.6575 | 0 | 20
C236 PH 2 D RECONDUCTOR | 2 | 15.4822 | 0.12918 | 0 | 3.526 | 0 | 35
C237 PH 2 A RECONDUCTOR | 1 | 14.6438 | 0.068288 | 0 | 4.3644 | 0 | 27
C237 PH 2 D RECONDUCT R1 | 3 | 14.5781 | 0.20579 | 1 | 4.4301 | 0.22573 | 38
C237 PH 2 E RECONDUCTOR | 1 | 14.4795 | 0.069063 | 0 | 4.5288 | 0 | 22
C237 PH 2 H RECONDUCT R8 | 1 | 14.6247 | 0.068378 | 0 | 4.3836 | 0 | 22
C237 PH 2 J RECONDUCTOR | 2 | 14.5781 | 0.13719 | 0 | 4.4301 | 0 | 24
C237 PH 2 M RECONDUCTOR | 2 | 14.663 | 0.1364 | 0 | 4.3452 | 0 | 41
C239:2013 RIRAT RELIABILITY | 2 | 14.5753 | 0.13722 | 0 | 4.4329 | 0 | 12
C240 PH 2 E RECONDUCT R1 | 1 | 14.9425 | 0.066923 | 0 | 4.0658 | 0 | 28
C357:2011 CFSP WS,TW ON R12 | 1 | 14.2164 | 0.070341 | 0 | 4.7918 | 0 | 6
C358 PH 2 A RECONDUCTOR | 0 | 14.7918 | 0 | 1 | 4.2164 | 0.23717 | 9
C441 BRLINE CFSP W/S(P1 R1 | 1 | 14.926 | 0.066997 | 0 | 4.0822 | 0 | 28
C441 PH 4 POLE REPLACE R2 | 1 | 13.8219 | 0.072349 | 0 | 5.1863 | 0 | 16
C442 PH 2 J RECONDUCT R8 | 1 | 14.9671 | 0.066813 | 0 | 4.0411 | 0 | 10
C442 PH 4 BPOLE CHGOUT R1 | 2 | 14.2767 | 0.14009 | 0 | 4.7315 | 0 | 25
C442 PH 4 FPOLE CHGOUT R1 | 1 | 15.3534 | 0.065132 | 0 | 3.6548 | 0 | 40
C442 PH 4 GPOLE CHGOUT R1 | 2 | 14.9397 | 0.13387 | 1 | 4.0685 | 0.24579 | 9
C444 BRANCHLN CFSP P4 R1 | 10 | 14.9616 | 0.66838 | 0 | 4.0466 | 0 | 16
C444 BRANCHLN CFSP W/S R1 | 1 | 14.4055 | 0.069418 | 0 | 4.6027 | 0 | 5
C444 BRANCHLN PH1 P41936 | 1 | 14.389 | 0.069497 | 0 | 4.6192 | 0 | 13
C444 BRANCHLN PH2 P4196 R1 | 5 | 14.2274 | 0.35143 | 0 | 4.7808 | 0 | 23
C444,BU:2011 CFSP RCNDCT R8 | 2 | 12.7342 | 0.15706 | 0 | 6.274 | 0 | 14
C445 2012 CFSP WS BRANCH R1 | 6 | 14.9781 | 0.40059 | 1 | 4.0301 | 0.24813 | 34
C445,BU:LG SPAN/DESIMI R16 | 2 | 14.1068 | 0.14178 | 0 | 4.9014 | 0 | 5
C67,BAR:LG SPAN/DESIMIL R3 | 1 | 13.6411 | 0.073308 | 0 | 5.3671 | 0 | 13
C73 PH 4 APOLE CHGOUT/ R9 | 1 | 14.2192 | 0.070328 | 0 | 4.789 | 0 | 17
C73 PH 4 CPOLE CHGOUT R11 | 2 | 15.0055 | 0.13328 | 0 | 4.0027 | 0 | 40
C73 PH 4 EPOLE CHGOUT R11 | 2 | 14.3068 | 0.13979 | 1 | 4.7014 | 0.2127 | 29
C78 PH4 BPOLE CHGOUT/R R8 | 1 | 14.2329 | 0.07026 | 0 | 4.7753 | 0 | 9
C78 PH4 CPOLE CHGOUT/RECO | 2 | 14.2329 | 0.14052 | 1 | 4.7753 | 0.20941 | 20
C79 FIRE RISK MITIGATION R2 | 5 | 14.5452 | 0.34376 | 0 | 4.463 | 0 | 72
C79 PH 2 R RECONDUCTOR | 1 | 14.8082 | 0.06753 | 0 | 4.2 | 0 | 22
C79 PH4 SEC 2 #G POLE R6 | 2 | 14.5671 | 0.1373 | 0 | 4.4411 | 0 | 15
C79 PH4 SEC 2 E POLE R1 | 2 | 14.4219 | 0.13868 | 0 | 4.5863 | 0 | 18
C79 PH4 SEC 2 K POLE R7 | 1 | 14.463 | 0.069142 | 0 | 4.5452 | 0 | 42
C973 PH 2 #A RECOND | 2 | 14.5233 | 0.13771 | 0 | 4.4849 | 0 | 17
CPE1-D | 1 | 15.0767 | 0.066327 | 0 | 3.9315 | 0 | 28
CPE1-PH-04-B | 1 | 14.3753 | 0.069564 | 0 | 4.6329 | 0 | 18
CRA1 PH 2 A RECONDUCTOR | 1 | 14.7507 | 0.067793 | 0 | 4.2575 | 0 | 23
PE1 PH 4 A POLE CHGO R11 | 6 | 14.5014 | 0.41375 | 0 | 4.5068 | 0 | 51
PE1 PH 4#C POLE CHGOUT/RE | 1 | 14.2795 | 0.070031 | 0 | 4.7288 | 0 | 11
0073-H | 0 | 16.2521 | 0 | 0 | 2.7562 | 0 | 23
0075-A | 0 | 17.1014 | 0 | 0 | 1.9068 | 0 | 21
0079-I | 0 | 14.3288 | 0 | 0 | 4.6795 | 0 | 24
0176-B | 0 | 16.3507 | 0 | 0 | 2.6575 | 0 | 23
0176-G | 0 | 16.0411 | 0 | 0 | 2.9671 | 0 | 18
0217-I | 0 | 17.6466 | 0 | 0 | 1.3616 | 0 | 10
0217-L | 0 | 18.2685 | 0 | 0 | 0.73973 | 0 | 22
0217-O | 0 | 17.674 | 0 | 0 | 1.3342 | 0 | 17
0217-S | 0 | 18.0767 | 0 | 0 | 0.93151 | 0 | 18
0220-P | 0 | 15.8274 | 0 | 0 | 3.1808 | 0 | 14
0221-M | 0 | 15.7726 | 0 | 0 | 3.2356 | 0 | 24
0221-P | 0 | 17.1342 | 0 | 0 | 1.874 | 0 | 25
0221-Q | 0 | 17.1342 | 0 | 0 | 1.874 | 0 | 29
0221-R | 0 | 17.5918 | 0 | 0 | 1.4164 | 0 | 22
0221-U | 0 | 17.5288 | 0 | 0 | 1.4795 | 0 | 18
0222-BB | 0 | 15.2438 | 0 | 0 | 3.7644 | 0 | 10
0222-G | 0 | 18.9068 | 0 | 0 | 0.10137 | 0 | 10
0222-W | 0 | 15.4877 | 0 | 0 | 3.5205 | 0 | 40
0237-B | 0 | 16.3589 | 0 | 0 | 2.6493 | 0 | 21
0237-S | 0 | 15.6795 | 0 | 0 | 3.3288 | 0 | 32
0350-B | 0 | 17.3781 | 0 | 0 | 1.6301 | 0 | 30
0350-C | 0 | 17.2658 | 0 | 0 | 1.7425 | 0 | 9
0350-O (ASD) | 0 | 18.9534 | 0 | 0 | 0.054795 | 0 | 5
0442-I | 0 | 15.1562 | 0 | 0 | 3.8521 | 0 | 13
0448-C-FT | 0 | 19.0082 | 0 | 0 | 0 | #DIV/0! | 2
0520-A | 0 | 16.6356 | 0 | 0 | 2.3726 | 0 | 24
0520-E | 0 | 17.4411 | 0 | 0 | 1.5671 | 0 | 33
0520-J | 0 | 17.1342 | 0 | 0 | 1.874 | 0 | 17
0520-K | 0 | 17.4822 | 0 | 0 | 1.526 | 0 | 47
0520-M | 0 | 17.2301 | 0 | 0 | 1.7781 | 0 | 29
0520-N | 0 | 17.5726 | 0 | 0 | 1.4356 | 0 | 44
0908-B | 0 | 18.8356 | 0 | 0 | 0.1726 | 0 | 25
0908-K | 0 | 18.7068 | 0 | 0 | 0.30137 | 0 | 10
0971-I | 0 | 16.5041 | 0 | 0 | 2.5041 | 0 | 27
0971-K | 0 | 16.5041 | 0 | 0 | 2.5041 | 0 | 21
0971-L | 0 | 17.1726 | 0 | 0 | 1.8356 | 0 | 33
0971-O | 0 | 16.6356 | 0 | 0 | 2.3726 | 0 | 37
0971-P | 0 | 16.7918 | 0 | 0 | 2.2164 | 0 | 23
0972-E | 0 | 16.3973 | 0 | 0 | 2.611 | 0 | 31
0973-B | 0 | 15.7945 | 0 | 0 | 3.2137 | 0 | 29
0973-WILDCAT CYN-R1-FTZ-1 | 0 | 13.6822 | 0 | 0 | 5.326 | 0 | 3
0974-A | 0 | 16.9534 | 0 | 0 | 2.0548 | 0 | 5
0974-F | 0 | 16.8685 | 0 | 0 | 2.1397 | 0 | 3
1030-A | 0 | 14.2384 | 0 | 0 | 4.7699 | 0 | 17
1030-G | 0 | 16.5753 | 0 | 0 | 2.4329 | 0 | 25
1030-H | 0 | 15.789 | 0 | 0 | 3.2192 | 0 | 26
1030-I | 0 | 15.6356 | 0 | 0 | 3.3726 | 0 | 29
1030-P | 0 | 16.5753 | 0 | 0 | 2.4329 | 0 | 33
1030-S | 0 | 15.6137 | 0 | 0 | 3.3945 | 0 | 13
449HH | 0 | 18.2493 | 0 | 0 | 0.7589 | 0 | 4
C1215 CWLONG SPAN/DESI R12 | 0 | 13.7068 | 0 | 0 | 5.3014 | 0 | 5
C1215 PH 4 POLE REPLACE/R | 0 | 14.3397 | 0 | 0 | 4.6685 | 0 | 10
C1233,PA LONGSPAN/DESIM R3 | 0 | 13.8466 | 0 | 0 | 5.1616 | 0 | 6
C1250 AERIAL MARKING R1 | 0 | 12.7151 | 0 | 0 | 6.2932 | 0 | 2
C1458 PH 2 #A RECONDUC R5 | 0 | 14.4411 | 0 | 0 | 4.5671 | 0 | 2
C217,RIN:LG SPAN/DESIMI R3 | 0 | 13.6301 | 0 | 0 | 5.3781 | 0 | 3
C220 PH 2 H RECONDUCT R1 | 0 | 14.4521 | 0 | 0 | 4.5562 | 0 | 34
C220 PH 2 J RECONDUCT R6 | 0 | 14.5781 | 0 | 0 | 4.4301 | 0 | 25
C220 PH 2 M RECONDUCTOR | 0 | 14.8384 | 0 | 0 | 4.1699 | 0 | 56
C220 PH 4 B POLE CHGO R3 | 0 | 14.4082 | 0 | 0 | 4.6 | 0 | 30
C220 PH 4 D POLE CHGOUT | 0 | 13.9616 | 0 | 0 | 5.0466 | 0 | 14
C220 PH 4 E POLE CHGOUT | 0 | 13.8795 | 0 | 0 | 5.1288 | 0 | 3
C220 PH 4 F POLE CHGO R2 | 0 | 13.9616 | 0 | 0 | 5.0466 | 0 | 14
C221 PH4 #B POLE REPLA R1 | 0 | 14.4164 | 0 | 0 | 4.5918 | 0 | 19
C221 PH4 #E POLE REPLA R1 | 0 | 14.8082 | 0 | 0 | 4.2 | 0 | 7
C221 PH4 C POLE REPLA R1 | 0 | 14.7781 | 0 | 0 | 4.2301 | 0 | 17
C222 PH 1 #L RECONDUC R1 | 0 | 14.6 | 0 | 0 | 4.4082 | 0 | 5
C222 PH 1 #O RECONDUC R1 | 0 | 14.4548 | 0 | 0 | 4.5534 | 0 | 39
C222 PH 1 #Q RECONDUC R3 | 0 | 14.6767 | 0 | 0 | 4.3315 | 0 | 15
C222 PH 1 J RECONDUC R6 | 0 | 14.7562 | 0 | 0 | 4.2521 | 0 | 19
C222 PH 1 M RECONDUC R6 | 0 | 14.7534 | 0 | 0 | 4.2548 | 0 | 19
C222 PH 2 V RECONDUCTOR | 0 | 14.8548 | 0 | 0 | 4.1534 | 0 | 35
C222 PH4 SEC2 APOLE CH R1 | 0 | 14.0603 | 0 | 0 | 4.9479 | 0 | 4
C222 PH4 SEC2 BPOLE CH R1 | 0 | 14.3479 | 0 | 0 | 4.6603 | 0 | 12
C233, MN: RECONDUCTOR R4 | 0 | 13.0795 | 0 | 0 | 5.9288 | 0 | 38
C236 PH 2 A RECONDUCTOR | 0 | 14.4795 | 0 | 0 | 4.5288 | 0 | 19
C237 PH 2 L RECONDUCTOR | 0 | 14.7589 | 0 | 0 | 4.2493 | 0 | 30
C239: RELOCATION TO MITI R5 | 0 | 13.4356 | 0 | 0 | 5.5726 | 0 | 3
C240 PH 2 A RECONDUCT R1 | 0 | 14.8274 | 0 | 0 | 4.1808 | 0 | 32
C240 PH 2 H RECONDUCT R1 | 0 | 14.8877 | 0 | 0 | 4.1205 | 0 | 8
C350,LI:LG SPA/DESIMILAR W | 0 | 13.8329 | 0 | 0 | 5.1753 | 0 | 7
C357:2011 CFSP WS,TW ON R4 | 0 | 13.5616 | 0 | 0 | 5.4466 | 0 | 7
C358 PH 2 B RECONDUCTOR | 0 | 14.6192 | 0 | 0 | 4.389 | 0 | 14
C441 PHASE 4RECONDCTR P R6 | 0 | 13.2822 | 0 | 0 | 5.726 | 0 | 7
C441: REBUILD P40714 TO R13 | 0 | 13.3973 | 0 | 0 | 5.611 | 0 | 10
C442 PH 2 K RECONDUCT R7 | 0 | 15.1562 | 0 | 0 | 3.8521 | 0 | 32
C442 PH 4 APOLE CHGOUT R1 | 0 | 14.1589 | 0 | 0 | 4.8493 | 0 | 5
C442 PH 4 CPOLE CHGOUT R1 | 0 | 14.5534 | 0 | 0 | 4.4548 | 0 | 9
C442 PH 4 EPOLE CHGOUT R7 | 0 | 13.8027 | 0 | 0 | 5.2055 | 0 | 4
C442 PH 4 HPOLE CHGOUT/RE | 0 | 14.6137 | 0 | 0 | 4.3945 | 0 | 21
C521,AV:LG SPAN/DESIMILAR | 0 | 14.1178 | 0 | 0 | 4.8904 | 0 | 4
C73 PH 2 I RECONDUCTO R1 | 0 | 14.8959 | 0 | 0 | 4.1123 | 0 | 8
C73 PH 2 JPOLE CHGOUT/ R1 | 0 | 15.2575 | 0 | 0 | 3.7507 | 0 | 6
C73 PH 4 BPOLE CHGOUT/ R5 | 0 | 13.9836 | 0 | 0 | 5.0247 | 0 | 28
C73 PH 4 FPOLE CHGOUT/ R8 | 0 | 14.1973 | 0 | 0 | 4.811 | 0 | 7
C78 PH2 F RECONDUCTOR | 0 | 15.4082 | 0 | 0 | 3.6 | 0 | 12
C78 PH4 APOLE CHGOUT/R R1 | 0 | 14.0027 | 0 | 0 | 5.0055 | 0 | 8
C79 PH 1 #O RECONDUCTOR | 0 | 14.8521 | 0 | 0 | 4.1562 | 0 | 14
C79 PH 1 N RECONDUCTO R2 | 0 | 14.4822 | 0 | 0 | 4.526 | 0 | 6
C79 PH4 SEC 2 F POLE R1 | 0 | 14.6192 | 0 | 0 | 4.389 | 0 | 14
C79 PH4 SEC 2 H POLE R1 | 0 | 14.526 | 0 | 0 | 4.4822 | 0 | 22
C79 PH4 SEC 2 L POLE R1 | 0 | 14.3753 | 0 | 0 | 4.6329 | 0 | 15
C908:LONG SPAN RFS REL R2 | 0 | 12.8904 | 0 | 0 | 6.1178 | 0 | 7
C974 E RECONDUCTOR R1 | 0 | 15.2 | 0 | 0 | 3.8082 | 0 | 24
Track 2 530000153622 | 0 | 18.6384 | 0 | 0 | 0.36986 | 0 | 13
Average | 1.5994 | 16.0083 | 0.099909 | 0.13043 | 2.9999 | 0.04348 | 24.3634
Unhardened faults per year per 100 miles | 9.4975
Hardened faults per year per 100 miles | 4.1332
Reduction | 56.48%