## Evidence of Heat
ID_SO | CD_JOB_DESC | DT_COMPLETED_FIELD | DT_ENROUTE | DT_ON_SITE | ELEC_IN_ORIGIN_FLAG | SELF_SUSTAINING_FLAG | LEFT_ELEC_FACILITY_FLAG | TRAVELED_MORE_THAN_ONE_METER_FLAG | IGNITION_NON_OF_THE_ABOVE_FLAG | EVIDENCE_OF_HEAT_DESC | HEAT_PRIMARY_VOLTAGE | HEAT_SECONDARY_VOLTAGE | CAUSE_OF_HEAT_DESC | CAUSE_OF_HEAT_DETAILS | OUTAGE_CAUSE_DESC | DEVICE_ID | DEVICE_TYPE_DESC | DEVICE_SIZE | DEVICE_FACILITY_ID | CIRCUIT_ID | DAMAGE_ASSESSMENT_DETAILS | REPORTED_BY_NAME | REPORTED_BY_SUPR_TITLE | FIELD_REMARKS | LATITUDE_ID | LONGITUDE_ID | Year | Driver
OMD0000645117-02 | Branch Outage | 2019-07-18 00:51 | 2019-07-17 19:08 | 2019-07-17 19:27 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Device Damaged | F588084 | Fuse | 150A | d3853269961 | 209 | bad fuse cabnet insolator broken flashed over and damaged el | 04148 Fiamengo, Nicholas | NE O&E SUP | need crew to change out single phas | 33.2231 | -117.2328 | 2019 | UG Fuse
OMD0000647548-01 | Dmg/Wlite-Flash or Sparks | 2019-07-26 22:30 | 2019-07-26 19:14 | 2019-07-26 19:33 | N | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility | failing connection | Weather Damaged Service | 377-152 | Transformer | 15 | P830835 | 377 | change out conn on backlotline pole UG service conn failing | 00886 Warren, Christopher | BC O&E SUP | crew to replace conn at pole | 32.6907 | -117.1893 | 2019 | Non Conductor
OMD0000656394-01 | Emer-Specl Req - Fire/Police/Gov | 2019-08-30 03:08 | 2019-08-30 01:49 | 2019-08-30 02:10 | N | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility |  | Conductor Damaged | MK2-11 | Transformer | 100 | P738762 | MK2 | ssc copper pole to pole burned open | 00886 PA-Warren, Christopher | BC O&E SUP | Ssc copper burned down between P738 | 32.7146 | -117.0958 | 2019 | Conductor
OMD0000660456-01 | Emer-Specl Req - Fire/Police/Gov | 2019-09-13 12:58 | 2019-09-13 11:46 | 2019-09-13 11:50 | Y | Y | Y | Y | N | Actual Ignition | 12 kV |  | Electric Facility |  | Connector Damaged | 84-176 | Transformer | 25 | p378837 | 84 |  | 52851 Mackley, Scott | BC O&E SUP | f/u for pole c/o | 32.7861 | -117.0074 | 2019 | Non Conductor
OMD0000645537-01 | Transformer Outage | 2019-07-19 19:27 | 2019-07-19 18:25 | 2019-07-19 18:52 | N | N | N | N | Y | Arching/Charring |  | 240 V | Other/Undetermined | SECONDARY MOLD BURNED UP. | Weather Damaged Conductor | 728-849 | Transformer | 75 | D119042 | 728 | FAILED U.G. SECONDARY FROM STATION TO 3312. AND FAILED MOLDS | 23123 Domnitz, Jared | NC O&E SUP | DAMAGED BACK BONE U.G. SECONDARY WI | 32.9238 | -117.0594 | 2019 | UG UG Cable
OMD0000675677-01 | Non Outage | 2019-11-10 16:32 | 2019-11-10 12:04 | 2019-11-10 12:04 | N | Y | N | Y | N | Actual Ignition | 12 kV |  | Other/Undetermined | fire burned pole ignition source deemed undetermined | Fire Damaged Pole | 4/0 B.STRD ABC 15880.0 | Primary |  | P183604 | 461 | fire burned pole and arms | 00886 PA-Warren, Christopher | BC O&E SUP |  | 32.5527 | -117.0322 | 2019 | Other All
OMD0000678358-01 | Branch Outage | 2019-11-20 03:16 | 2019-11-19 19:36 | 2019-11-19 19:59 | N | N | N | N | Y | Arching/Charring | 12 kV |  | Electric Facility |  | Weather Damaged Pole | F14384 | Fuse | 150A | P160993 | 461 | pole top burned need pole replaced | 00886 PA-Warren, Christopher | BC O&E SUP |  | 32.5438 | -117.0285 | 2019 | Non Conductor
OMD0000646461-01 | Branch Outage | 2019-07-23 22:52 | 2019-07-23 22:50 | 2019-07-23 22:50 | N | N | N | N | Y | Arching/Charring | 12 kV |  | Electric Facility | BAD 65 A CLF | Heat Device/Overload | 59-24R | Recloser |  | D2426569387 | 59 |  | 23123 Domnitz, Jared | NC O&E SUP | BAD FUSE. | 32.8383 | -117.2492 | 2019 | UG Fuse
OMD0000699126-01 | Dmg/Wlite-Other | 2020-02-04 16:24 | 2020-02-04 16:14 | 2020-02-04 16:14 | N | N | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | charring on pole 4' off grd at sta grd wire | Undetermined | 430-176 | Transformer | 37.5 |  | 430 | fix damaged sta grd | 52851 Mackley, Scott | BC O&E SUP | charring on pole 4' off grd at sta | 32.7689 | -117.0636 | 2020 | Undetermined
OMD0000737445-01 | Emer-Specl Req - Fire/Police/Gov | 2020-07-05 10:42 | 2020-07-05 08:06 | 2020-07-05 08:18 | Y | Y | N | N | N | Actual Ignition | 12 kV |  | Electric Facility |  | Damaged Underground Cable | 702-404 | Transformer | 50 | p479087 | 702 | bad cable @ potheads | 52851 Mackley, Scott | BC O&E SUP |  | 32.79 | -117.0895 | 2020 | OH to UG
OMD0000739229-01 | Branch Outage | 2020-07-11 17:55 | 2020-07-11 13:28 | 2020-07-11 14:02 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | connector failed | Connector Damaged | F129504 | Fuse | 150A | h2206575882 | 404 | bad conn and cable | 52851 Mackley, Scott | BC O&E SUP |  | 32.7707 | -117.0329 | 2020 | UG Connector
OMD0000740667-01 | Emer-Specl Req - Fire/Police/Gov | 2020-07-16 03:57 | 2020-07-16 00:43 | 2020-07-16 00:58 | N | N | N | N | Y | Actual Ignition |  | 120 V | Other/Undetermined | Palm tree lit on fire no witnesses burned 2 secondary services fire not started by DSGE | Vandalism | 123-417 | Three Phase Transformer | 500 |  | 123 |  | 00886 PA-Warren, Christopher | BC O&E SUP | Palm tree on fire burned down servi | 32.7034 | -117.1493 | 2020 | Other All
OMD0000753494-01 | Transformer Outage | 2020-08-24 18:16 | 2020-08-24 16:55 | 2020-08-24 17:12 | N | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility | load from sta burnt op conn | Weather Damaged Connector | 946-213 | Transformer | 50 | P576066 | 946 |  | 52851 Mackley, Scott | BC O&E SUP |  | 32.7946 | -117.0113 | 2020 | Non Conductor
OMD0000757106-01 | Emer-Specl Req - Fire/Police/Gov | 2020-09-05 16:54 | 2020-09-05 15:22 | 2020-09-05 15:34 | N | N | N | Y | N | Actual Ignition |  | 240 V | Other/Undetermined | SECONDARY WIRE BURNT OPEN/DOWN P194421 TO P771249. PALM TREE CAUGHT ON FIRE | Undetermined | 76-480 | Transformer | 50 | P194421 | 76 | NEED OH CREW TO REPLACE DAMAGED 3 PHASE RTS P194421 TO P7712 | 00903 PA-Swanstrom, Luke | BC O&E SUP | DAMAGED SECONDARY P194421 TO P77124 | 32.7934 | -116.9662 | 2020 | Conductor
OMD0000773565-01 | Dmg/Wlite-Pole Burning | 2020-10-30 15:23 | 2020-10-30 15:03 | 2020-10-30 15:03 | N | N | N | N | Y | Arching/Charring |  | 208 V | Electric Facility | Bad Secondary wire | Weather Damaged Service | 452-239 | Transformer | 10 | P814915 | 452 | Bad service | 05615 Navarro, Brett | BC O&E SUP |  | 33.1717 | -117.0279 | 2020 | Conductor
OMD0000777001-01 | Dmg/Wlite-Other | 2020-11-11 13:07 | 2020-11-11 12:50 | 2020-11-11 12:50 | Y | Y | Y | Y | N | Actual Ignition | 12 kV |  | Electric Facility |  | Conductor Damaged | 75-824 | Transformer | 75 | p270154 | 75 | 1-wire down 1-span p270154 to p270155 w/ small brush fire | 52851 Mackley, Scott | BC O&E SUP | 1-wire down 1-span p270154 to p2701 | 32.6804 | -116.8575 | 2020 | Conductor
OMD0000788396-01 | Transformer Outage | 2020-12-28 08:47 | 2020-12-28 06:37 | 2020-12-28 06:54 | N | N | N | N | Y | Arching/Charring |  | 240 V | Electric Facility |  | Connector Damaged | 1438-142 | Transformer | 50 | P832393 | 1438 |  | 00886 PA-Warren, Christopher | BC O&E SUP | Replaced all secondary conn on low | 32.7287 | -117.1151 | 2020 | Non Conductor
OMD0000790527-01 | No Lights in Part-Just Started | 2021-01-06 11:14 | 2021-01-06 09:56 | 2021-01-06 10:25 | N | N | N | N | Y | Arching/Charring |  | 120 V | Electric Facility | 2 melted insula link conn | Weather Damaged Connector | 84-344 | Transformer | 15 | @ cus w/h -p378788 | 84 |  | 52851 Mackley, Scott | BC O&E SUP | 2 bad ocnn | 32.7908 | -117.0116 | 2021 | Non Conductor
OMD0000792922-01 | Dmg/Wlite-Xfmr/Grn Box Flash/Spr | 2021-01-16 09:25 | 2021-01-16 07:37 | 2021-01-16 09:01 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Conductor Damaged | 412-900 | Transformer | 25 | p175825 | 412 | damaged cable | 52851 Mackley, Scott | BC O&E SUP | bad cable below pothead term | 32.7852 | -116.9368 | 2021 | OH to UG
OMD0000794852-01 | Emer-Specl Req - Fire/Police/Gov | 2021-01-23 14:39 | 2021-01-23 12:59 | 2021-01-23 13:03 | Y | N | N | N | N | Actual Ignition |  | 240 V | Other/Undetermined | Service burned down and ignighted pool lounge chair | Service Down | IB2-37 | Transformer | 50 |  | IB2 | Replace service midspan to house P185275J | 00886 PA-Warren, Christopher | BC O&E SUP | Sevice burned down burned cust pool | 32.5797 | -117.1013 | 2021 | Conductor
OMD0000795242-01 | Emer-Specl Req - Fire/Police/Gov | 2021-01-25 07:42 | 2021-01-25 06:28 | 2021-01-25 06:54 | N | N | N | N | N | Arching/Charring |  | 240 V | Other/Undetermined | Cust panel bus faulted need electrician to recertiifiy | Customer Problem | 167-332 | Transformer | 75 |  | 167 |  | 00886 PA-Warren, Christopher | BC O&E SUP | Cust panel bus faulted need electri | 32.7345 | -117.0804 | 2021 | Non Conductor
OMD0000795446-01 | Dmg/Wlite-Flash or Sparks | 2021-01-25 11:58 | 2021-01-25 10:53 | 2021-01-25 11:08 | N | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility | grd mid span srvc hitting ps leg | Conductor Damaged | CS1-322 | Transformer | 50 | p177976j | CS1 | mid span srvc off guy wire is touching ps leg in wind about | 52851 Mackley, Scott | BC O&E SUP | mid span srvc off guy wire is touch | 32.7521 | -117.0445 | 2021 | Conductor
OMD0000815442-01 | Emer-Specl Req - Fire/Police/Govt | 2021-04-07 17:32 | 2021-04-07 17:26 | 2021-04-07 17:26 | N | N | N | N | N | Arching/Charring | 12 kV | 480 V | Other/Undetermined | undetermined | Undetermined | UNKNOWN | Switch |  | p771525 |  |  | 52851 Mackley, Scott | BC O&E SUP | did not find cause of fire | 32.812 | -116.9765 | 2021 | Other All
OMD0000818733-01 | Emer-Specl Req - Fire/Police/Govt | 2021-04-22 08:00 | 2021-04-22 05:40 | 2021-04-22 06:12 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | tracking from rain caused arm to burn | Weather Damaged Device | 166-30 | Transformer | 50 | p572113 | 166 | burnt xarm cir 166 damaged c/o | 52851 Mackley, Scott | BC O&E SUP |  | 32.7556 | -117.0256 | 2021 | Non Conductor
OMD0000822938-02 | Branch Outage | 2021-05-11 12:05 | 2021-05-11 10:53 | 2021-05-11 10:54 | Y | N | Y | Y | N | Actual Ignition | 12 kV | 240 V | Contact by Object | MYLAR BALLONS | Equipment Contacted Conductor | F192102 | Fuse | 125A | P376783 | 244 |  | 00903 PA-Swanstrom, Luke | BC O&E SUP | MYLAR BALLONS P376783. SENT PICTURE | 32.8494 | -116.9315 | 2021 | Balloon
OMD0000842979-01 | Branch Outage | 2021-07-28 15:10 | 2021-07-28 15:06 | 2021-07-28 15:06 | N | N | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | Car hit telco wires and slapped primary wires together | Customer Problem | 909-805R | Recloser |  | Z16445 | 909 |  | 05615 Navarro, Brett | BC O&E SUP | car hit telco and slapped wires tog | 33.2282 | -116.9874 | 2021 | Vehicle
OMD0000845525-01 | Emer-Specl Req - Fire/Police/Govt | 2021-08-07 13:51 | 2021-08-07 13:41 | 2021-08-07 13:41 | N | N | N | N | N |  | 12 kV |  | Electric Facility | melted switch started very small fire 2'x2' | Device Damaged | 386-284 | Transformer | 25 | p74004 | 386 | damaged switch 386-4 | 52851 Mackley, Scott | BC O&E SUP | daf for on call w/ traffic | 32.8286 | -116.9084 | 2021 | Non Conductor
OMD0000859506-02 | Branch Outage | 2021-10-05 00:46 | 2021-10-04 23:37 | 2021-10-04 23:48 | N | N | N | N | Y | Arching/Charring | 12 kV |  | Other/Undetermined | lightning, fire dept. called, cant locate any trace of fire in current conditions | Weather Damaged Transformer | F128712 | Fuse | 15A | p678896 | 144 | replace 144-138 25 HE on p678896 | 88586 Dotson, Trevor | BC O&E SUP | replace 144-138 25 HE on p678896 | 32.8057 | -117.159 | 2021 | Other All
OMD0000864643-01 | Branch Outage | 2021-10-26 12:22 | 2021-10-26 10:08 | 2021-10-26 12:10 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | top of LA | Equipment Damaged Transformer | F192054 | Fuse | 20A | p871572 | 1458 | damaged sta 1458-76 | 52851 Mackley, Scott | BC O&E SUP |  |  |  | 2021 | Non Conductor
OMD0000878858-01 | No Lights - Cause Unknown | 2021-12-21 19:30 | 2021-12-21 19:19 | 2021-12-21 19:19 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Device Damaged | 480-522 | Transformer | 50 | p2095569255 | 480 | need to make repairs and or replace scada site 752 on P20955 | 88586 Dotson, Trevor | BC O&E SUP | need to make repairs to scada site | 32.7387 | -117.2515 | 2021 | Non Conductor
OMD0000880100-01 | Dmg/Wlite-Flash or Sparks | 2021-12-28 19:16 | 2021-12-28 18:38 | 2021-12-28 18:50 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Weather Damaged Conductor | 274-161 | Transformer | 37.5 | service at hosue | 274 | 90' of #6 ssc from pole to house | 65802 Littlefield, Skyler | BC O&E SUP | Need service crew to replace servic | 32.8094 | -117.1732 | 2021 | Conductor
OMD0000890268-02 | Branch Outage | 2022-02-14 09:52 | 2022-02-14 06:51 | 2022-02-14 07:04 | Y | N | N | Y | N | Arching/Charring | 12 kV |  | Electric Facility | 12kv fuse did not operate correctly - wire down hot on ground | Foreign Object Contact Conductor | F156860 | Fuse | 150A | p971675 | 86 |  | 52851 Mackley, Scott | BC O&E SUP | cir 86 -eucalyptus tree came down o | 32.769 | -116.9937 | 2022 | Veg
OMD0000892447-01 | Emer-Specl Req - Fire/Police/Govt | 2022-02-23 18:49 | 2022-02-23 17:46 | 2022-02-23 18:08 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Device Damaged | 52-126 | Transformer | 25 | P37108 | 52 | Crew to replace 2-cutouts and doors 15amp QA | 00886 PA-Warren, Christopher | BC O&E SUP | Crew to replace faied cutouts and d | 32.7433 | -117.2506 | 2022 | Non Conductor
OMD0000897667-01 | Emer-Specl Req - Fire/Police/Govt | 2022-03-18 09:05 | 2022-03-18 07:08 | 2022-03-18 07:27 | N | N | N | N | N | Arching/Charring |  | 120 V | Other/Undetermined | services burned and weatherhead burned | Conductor Damaged | 480-452 | Transformer | 50 |  | 480 | two melted services/ cause unknown, masts badly damaged | 88586 Dotson, Trevor | BC O&E SUP | two services badly burned, cause un | 32.7262 | -117.2548 | 2022 | Non Conductor
OMD0000902884-01 | Emer-Specl Req - Fire/Police/Govt | 2022-04-13 00:06 | 2022-04-12 19:40 | 2022-04-12 20:00 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Connector Damaged | 480-291 | Three Phase Transformer | 75 | P104540 | 480 | Burned open cable pole termination | 00886 PA-Warren, Christopher | BC O&E SUP | Burned open cable termination @ P10 | 32.714 | -117.2516 | 2022 | Non Conductor
OMD0000908373-01 | Dmg/Wlite-Wire Down Pole to Pole | 2022-05-07 00:18 | 2022-05-06 19:19 | 2022-05-06 19:19 | N | N | N | N | N | Arching/Charring | 4 kV |  | Electric Facility |  | Conductor Damaged | PB1-71 | Transformer | 50 | p193418 | PB1 | #6 cu secondary ps wire down and reattach PN | 88586 Dotson, Trevor | BC O&E SUP |  | 32.7997 | -117.2523 | 2022 | Conductor
OMD0000910641-01 | Dmg/Wlite-Other | 2022-05-16 05:57 | 2022-05-16 05:46 | 2022-05-16 05:46 | N | N | N | N | Y |  | 12 kV |  | Other/Undetermined | trash can caught fire under meter | Customer Problem | PB1-75 | Transformer | 25 |  | PB1 |  | 88586 Dotson, Trevor | BC O&E SUP | fire burnt meter - replaced | 32.8012 | -117.2503 | 2022 | Other All
OMD0000916019-01 | Dmg/Wlite-Wire Down Pole to Pole | 2022-06-08 01:34 | 2022-06-07 20:36 | 2022-06-07 20:54 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Weather Damaged Pole | 242-711 | Transformer | 75 | p72480 | 242 | 2ndary pole pole fell over | 52851 Mackley, Scott | BC O&E SUP |  | 32.8569 | -116.9294 | 2022 | Non Conductor
OMD0000916323-01 | Emer-Specl Req - Fire/Police/Govt | 2022-06-09 02:48 | 2022-06-08 23:41 | 2022-06-08 23:51 | N | N | N | N | N | Arching/Charring | 4 kV |  | Contact by Object | MYLARS | Foreign Object Contacted Wire | AD1-145 | Transformer | 75 |  | AD1 | mylar balloon contact across all phases on span crossing uta | 88586 Dotson, Trevor | BC O&E SUP | mylar baloon contact | 32.7565 | -117.1321 | 2022 | Balloon
OMD0000926391-01 | Branch Outage | 2022-07-18 13:49 | 2022-07-18 12:27 | 2022-07-18 12:49 | N | N | N | Y | N |  | 12 kV |  | Electric Facility | bird contact | Foreign Object in Transformer | F86391 | Fuse | 150A | p74627 | 524 | bird contact sta 524-290 | 52851 Mackley, Scott | BC O&E SUP |  | 32.73 | -116.8569 | 2022 | Animal
OMD0000927801-01 | Dmg Dim/Nolite-Tree Burn in Wire | 2022-07-24 20:38 | 2022-07-24 20:17 | 2022-07-24 20:17 | N | N | N | N | N | Arching/Charring | 4 kV |  | Electric Facility |  | Weather Damaged Conductor | 95-720 | Transformer | 15 | p173569 | 95 | backlot aleast 2 op jumpers and flashed over deadends & ins | 52851 Mackley, Scott | BC O&E SUP |  | 32.7653 | -116.9655 | 2022 | Non Conductor
OMD0000647533-03 | Branch Outage | 2019-07-27 00:11 | 2019-07-26 19:37 | 2019-07-26 20:59 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | ELBOW FAILED AND FLASHED TO GROUND NO DAMAGE EXCEPT TO SDGE FACILITY | Connector Damaged | F739239 | Fuse | 150A | D5124756267 | 561 |  | 05463 Cittel, Taylor | BC O&E SUP | BRANCH OUTAGE CIR 561. CLOVIS SUBMI | 33.5672 | -117.6866 | 2019 | UG Connector
OMD0000937745-01 | Dmg Dim/Nolite - Flash or Sparks | 2022-09-02 17:54 | 2022-09-02 17:26 | 2022-09-02 17:43 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Weather Damaged Connector | 244-95 | Three Phase Transformer | 75 | P476199 | 244 | bad conn line wire to jumper | 52851 Mackley, Scott | BC O&E SUP | bad conn line wire to jumper | 32.8627 | -116.9217 | 2022 | Non Conductor
OMD0000962441-01 | Substation Outage | 2022-12-05 01:10 | 2022-12-04 20:18 | 2022-12-04 20:37 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Device Damaged | MR-12KV-BK 31 | Substation |  | CIR 761 CB | MIRA |  | 21640 Dawson, Garth | BC O&E SUP | CIR 761 CIR BREAKER HIGH SIDE BUSHI |  |  | 2022 | Undetermined
OMD0000982451-01 | Branch Outage | 2023-02-20 12:59 | 2023-02-20 10:42 | 2023-02-20 10:42 | Y | Y | N | N | N |  | 12 kV | 240 V | Other/Undetermined | failed overhead transformer blew top with oil fire at transformer only | Fire Damaged Transformer | F102656 | Fuse | 150A | P179531 | 60 | XFMR fire at 60-409 / P179531 | 00236 Dunar, Erik | BC O&E SUP | XFMR failed / fire at 60-409 / P179 | 32.7837 | -117.1727 | 2023 | Non Conductor
OMD0000982451-03 | Branch Outage | 2023-02-20 11:22 | 2023-02-20 09:04 | 2023-02-20 09:15 | Y | Y | N | N | N |  | 12 kV |  | Electric Facility |  | Equipment Damaged Transformer | F102656 | Fuse | 150A | P179531 | 60 |  | 52851 Mackley, Scott | BC O&E SUP |  | 32.7837 | -117.1727 | 2023 | Non Conductor
OMD0000984674-01 | Dmg/Wlite-Flash or Sparks | 2023-02-25 08:20 | 2023-02-25 06:43 | 2023-02-25 06:59 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Device Damaged | 136-279 | Transformer | 150 | p729818 | 136 | cracked glass on jumper /under bird cover pole pos | 52851 Mackley, Scott | BC O&E SUP |  | 32.7568 | -117.209 | 2023 | Non Conductor
OMD0001012630-01 | Emer-Specl Req - Fire/Police/Govt | 2023-06-09 09:00 | 2023-06-09 05:33 | 2023-06-09 05:47 | Y | Y | N | N | N |  | 12 kV |  | Electric Facility | pole top fire caused by tracking. Small embers came to ground. Otherwise fire was contained to pole top | Fire Damaged Pole | 571-282 | Transformer | 50 | P191759 | 571 | Pole top fire Cirvcuit 571 at P191759. Fire is out & line de | 00236 Dunar, Erik | BC O&E SUP | Pole top fire circuit 571 at P19175 | 32.831 | -117.278 | 2023 | Other All
OMD0001013158-01 | Emer-Specl Req - Fire/Police/Govt | 2023-06-12 06:59 | 2023-06-12 05:15 | 2023-06-12 05:15 | N | N | N | N | N | Arching/Charring | 4 kV |  | Electric Facility |  | Weather Damaged Conductor | PL6-82 | Transformer | 50 | p2108769972 | PL6 | pl6 wire down 4 spans 4 diff ways | 52851 Mackley, Scott | BC O&E SUP | pl6 wire down 4 spans 4 diff ways - | 32.7422 | -117.2268 | 2023 | Conductor
OMD0001030598-01 | Emer-Specl Req - Fire/Police/Govt | 2023-08-20 12:27 | 2023-08-20 09:06 | 2023-08-20 09:16 | Y | Y | N | N | N |  | 12 kV |  | Electric Facility | pole fire only | Weather Damaged Device | 572-252 | Three Phase Transformer | 300 | p253286 | 572 |  | 52851 Mackley, Scott | BC O&E SUP |  | 32.8429 | -117.274 | 2023 | Non Conductor
OMD0001050007-01 | Dmg/Wlite-Pole Burning | 2023-10-31 11:32 | 2023-10-31 10:14 | 2023-10-31 10:31 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Transformer Problem | 480-516 | Transformer | 50 | p37323 | 480 |  | 52851 Mackley, Scott | BC O&E SUP | turned into dist | 32.7375 | -117.2517 | 2023 | Non Conductor
OMD0001089073-01 | Emer-Specl Req - Fire/Police/Govt | 2024-03-30 08:47 | 2024-03-30 08:05 | 2024-03-30 08:27 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Weather Damaged Conductor | 274-236 | Transformer | 50 | p729850 | 274 | damaged srvc | 52851 Mackley, Scott | BC O&E SUP |  | 32.8176 | -117.1638 | 2024 | Conductor
OMD0001119558-01 | Emer-Specl Req - Fire/Police/Govt | 2024-08-01 20:08 | 2024-08-01 18:40 | 2024-08-01 18:55 | N | N | N | N | N | Arching/Charring | 12 kV | 240 V | Electric Facility |  | Service Deenergized For Safety | 270-451 | Transformer | 50 | P61882 | 270 | Burned open services at 9512 Pool and from P61882 going to | 00886 PA-Warren, Christopher | BC O&E SUP | Wire shorted from P61882 to P61883 | 32.8724 | -117.2445 | 2024 | Conductor
OMD0000648068-01 | Emer-Specl Req - Fire/Police/Gov | 2019-07-29 14:11 | 2019-07-29 13:06 | 2019-07-29 13:38 | N | N | N | N | Y | Actual Ignition | 12 kV |  | Other/Undetermined | OVEN FIRE IN APPARTMENT | Customer Problem | 927-155 | Transformer | 167 | D2887075745 | 927 |  | 02479 Fergerson, Mike | OC O&E SUP |  | 32.9577 | -117.0414 | 2019 | UG transformer
OMD0001159907-01 | Dmg/Wlite-Pole Burning | 2025-01-03 01:49 | 2025-01-03 01:06 | 2025-01-03 01:06 | Y | Y | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | INSULATOR TRACKING CAUSED POLY TO CATCH FIRE MELTING IT | Weather Damaged Conductor | 545-357 | Transformer | 50 | P2268069140 | 545 | INSULATOR TRACKING CAUSED POLY TO CATCH FIRE | 88344 Bryant, Matt | BC O&E SUP | INSULATOR TRACKING CAUSED POLY INSU | 32.7841 | -117.2533 | 2025 | Non Conductor
ADV1000000000823450 | Transformer Outage | 2024-09-09 16:11 | 2024-09-09 15:12 | 2024-09-09 15:30 | N | N | N | N | N | Arching/Charring |  | 240 V | Contact by Object |  | Motor Vehicle Contact with Xfmr | 430-308 | Transformer | 50 |  | 430 |  | 00108 Alvarez, Marco | CM O&E SUP |  | 32.763 | -117.0608 | 2024 | UG Vehicle
OMD0000644321-02 | Branch Outage | 2019-07-15 04:06 | 2019-07-15 00:06 | 2019-07-15 00:31 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Device Damaged | F13774 | Fuse | 100A | P839697 | 158 |  | 04108 Jones, Tyrone | CM O&E SUP | REQ CREW C/O DAMAGED CUT-OUT @ P839 | 32.5832 | -117.1094 | 2019 | Non Conductor
OMD0000644852-03 | Branch Outage | 2019-07-17 00:16 | 2019-07-16 19:18 | 2019-07-16 19:49 | N | N | N | Y | N | Actual Ignition | 12 kV |  | Vegetation Contact | Tree fell on telco wires, which broke telco and SDGE pole. Wire down caused 50' by 60' fire | Tree Damaged Pole | F514527 | Fuse | 150A | P610712 | 1039 | Replace damaged pole P610712 Wire down from p610712 to P112 | 02704 Martinez, Chris | CM O&E SUP |  | 33.182 | -117.1125 | 2019 | Veg
OMD0000645117-01 | Branch Outage | 2019-07-18 00:34 | 2019-07-17 19:55 | 2019-07-17 20:18 | N | N | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | Broken insulator in fuse cab on fuse side & cracked bushing & damaged LBE on cable side... | Device Damaged | F588084 | Fuse | 150A |  | 209 |  | 00832 Arevalo, Greg | CM O&E SUP | Faulted single phase fuse cab. Blow | 33.2231 | -117.2328 | 2019 | Non Conductor
OMD0000645514-01 | No Lights - Cause Unknown | 2019-07-19 18:15 | 2019-07-19 16:03 | 2019-07-19 16:44 | N | N | N | N | N | Arching/Charring |  | 120 V | Other/Undetermined | fire caused due to possible short in customers house, LOAB and booted meter for saftey | Conductor Damaged | HL1-254 | Transformer | 25 |  | HL1 |  | 09424 Garcia, Raul | CM O&E SUP | FIRE CREW ON LOCATION UPON ARRIVAL | 32.7008 | -117.1104 | 2019 | Other All
OMD0000645541-01 | Emer-Specl Req - Fire/Police/Gov | 2019-07-19 18:18 | 2019-07-19 18:16 | 2019-07-19 18:16 | N | N | N | N | N | Arching/Charring |  | 120 V | Other/Undetermined | FIRE CAUSED DUE TO POSSIBLE SHORT ON CUSTOMER HOUSE | Conductor Damaged | HL1-254 | Transformer | 25 |  | HL1 |  | 09424 Garcia, Raul | CM O&E SUP | FIRE CREW ON LOCATION UPON ARRIVAL | 32.7008 | -117.1104 | 2019 | Other All
OMD0000645543-01 | Single No Light | 2019-07-19 19:34 | 2019-07-19 17:35 | 2019-07-19 18:23 | N | N | N | N | N | Arching/Charring | 12 kV |  | Contact by Object | Bird contact on top of lightning arrestor | Foreign Object Contacted Device | 445-558 | Transformer | 15 | P41320 | 445 |  | 02766 Mcghen, Ryan | CM O&E SUP | Bird contact lightning arrestor P41 | 32.6265 | -116.3257 | 2019 | Animal
OMD0000647103-01 | Emer-Specl Req - Fire/Police/Gov | 2019-07-25 17:28 | 2019-07-25 15:33 | 2019-07-25 16:19 | Y | N | N | N | N | Actual Ignition |  | 240 V | Vegetation Contact | Service to house rubbed on tree branch causing a short and small fire. Fire was 3x3ft | Foreign Object Contact Services | 215-1133 | Transformer | 25 | P109151 to house | 215 | C/O Damaged service | 02704 Martinez, Chris | CM O&E SUP |  | 33.2655 | -116.9884 | 2019 | Veg
OMD0000647761-01 | Circuit Outage | 2019-07-28 09:13 | 2019-07-28 04:53 | 2019-07-28 09:10 | Y | Y | Y | Y | N | Actual Ignition | 12 kV |  | Electric Facility | Fire in H123360 when STA A came Hot/Energized. | Conductor Damaged | GR-12KV-410 | Circuit |  | H123360 | 410 |  | 02819 Patrick, Damion | CM O&E SUP | bad run of 1000KCMIL in H123360 to | 32.7852 | -116.9283 | 2019 | UG transformer
OMD0000647762-02 | Branch Outage | 2019-07-28 09:09 | 2019-07-28 04:32 | 2019-07-28 05:18 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | UG cable exploded inside HH | Damaged Underground Cable | 410-50R | Recloser |  | H123360 | 410 | Replace million cable | 02704 Martinez, Chris | CM O&E SUP |  | 32.7785 | -116.9278 | 2019 | UG UG Cable
OMD0000647834-01 | No Lights in Part-Just Started | 2019-07-28 18:10 | 2019-07-28 17:09 | 2019-07-28 17:25 | Y | Y | Y | N | N | Arching/Charring |  | 120 V | Other/Undetermined | Customer outlet melted along w/wires attached...maintenance will fix. | Customer Problem | 169-156 | Transformer | 100 | water heater location | 169 |  | 02819 Patrick, Damion | CM O&E SUP | Customer outlet melted along w/wire | 32.7498 | -117.0674 | 2019 | Other All
OMD0000647837-01 | No Lights - Cause Unknown | 2019-07-28 20:34 | 2019-07-28 19:09 | 2019-07-28 19:23 | Y | Y | N | N | N | Arching/Charring |  | 120 V | Electric Facility | bad breaker | Customer Problem | 1435-505 | Transformer | 25 | Panel | 1435 |  | 02819 Patrick, Damion | CM O&E SUP | Customer has a bad breaker... | 32.7218 | -117.1303 | 2019 | Non Conductor
OMD0000649843-02 | Branch Outage | 2019-08-05 12:17 | 2019-08-05 07:58 | 2019-08-05 08:23 | N | N | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | Faulted 600amp tee damaged & melted all 6 connectors... | Connector Damaged | 854-607F | Switch Position |  |  | 854 | Blown 600amp tees in M3673868463... | 00832 Arevalo, Greg | CM O&E SUP | Blown 600 amp tee connectors in M36 | 33.1691 | -117.2594 | 2019 | UG Connector
OMD0000649869-01 | Flickering Lights-Just Started | 2019-08-05 10:05 | 2019-08-05 09:39 | 2019-08-05 09:47 | Y | N | N | N | N | Arching/Charring |  | 120 V | Other/Undetermined | Bad contact point in panel...cleaned contact R/S. | Customer Restored | 321-542 | Transformer | 50 |  | 321 |  | 02819 Patrick, Damion | CM O&E SUP | 1 of customer breakers had a bad co | 32.6957 | -117.0585 | 2019 | Non Conductor
OMD0000651228-01 | Branch Outage | 2019-08-10 00:35 | 2019-08-09 22:58 | 2019-08-09 23:11 | N | N | N | N | Y | Arching/Charring | 4 kV |  | Other/Undetermined | Loose connection | Connector Damaged | F58442 | Fuse | 150A | P164422 | EO2 |  | 02819 Patrick, Damion | CM O&E SUP | Hotline clamp was loose & caused co | 32.7015 | -117.0735 | 2019 | Non Conductor
OMD0000651408-02 | Branch Outage | 2019-08-11 15:04 | 2019-08-11 12:22 | 2019-08-11 12:42 | N | Y | N | N | N | Arching/Charring | 12 kV |  | Contact by Object | Car hit Terminator D169719 exposing underground cables which caught fire & FD extinguished on site... | Motor Vehicle Contact with Xfmr | 904-255 | Switch |  |  | 904 |  | 00832 Arevalo, Greg | CM O&E SUP | Car hit terminator D169719 & statio | 33.2097 | -117.2788 | 2019 | UG Vehicle
OMD0000652970-01 | Branch Outage | 2019-08-18 11:34 | 2019-08-18 10:19 | 2019-08-18 10:36 | N | N | N | N | N | Arching/Charring | 12 kV |  | Contact by Object | bird contact | Foreign Object Contacted Device | F260 | Fuse | 40A | P176798 | 79 | Bird contact damaged Transformer | 02766 Mcghen, Ryan | CM O&E SUP | Bird contact Damaged sta 79-32 on P | 32.864 | -116.5919 | 2019 | Animal
OMD0000653138-01 | Dmg Dim/Nolite - Explosion | 2019-08-19 00:19 | 2019-08-18 21:21 | 2019-08-18 21:41 | N | N | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | Hot connection caused facility to burn. | Heat Device/Overload | S2-82 | Transformer | 90 | P230708 | S2 | Bad 900a disconnect/switch | 02819 Patrick, Damion | CM O&E SUP | Hot connection caused facility to b | 32.6973 | -117.1393 | 2019 | Non Conductor
OMD0000654801-01 | Flickering Lights-Just Started | 2019-08-24 01:29 | 2019-08-24 01:13 | 2019-08-24 01:13 | N | N | N | N | Y | Arching/Charring |  | 120 V | Electric Facility | ELECTRIC PANEL NEEDS UPGRADE DUE TO SOLAR INSTALL | Connector Damaged | 334-422 | Transformer | 50 | 5372172 | 334 |  | 09424 Garcia, Raul | CM O&E SUP | ELECTRIC PANEL NEEDS UPGRADE DUE TO | 32.5657 | -117.0682 | 2019 | Non Conductor
OMD0000656200-01 | No Lights - Cause Unknown | 2019-08-29 14:16 | 2019-08-29 13:32 | 2019-08-29 13:48 | Y | N | N | N | N | Arching/Charring |  | 208 V | Electric Facility |  | Customer Problem | 42-364 | Transformer | 150 | 3124 E. Plaza Blvd | 42 |  | 02819 Patrick, Damion | CM O&E SUP | Isolated breaker at test blocks on | 32.6816 | -117.0738 | 2019 | Other All
OMD0000656705-01 | No Lights - Cause Unknown | 2019-08-30 22:21 | 2019-08-30 21:40 | 2019-08-30 21:52 | Y | N | N | N | N | Arching/Charring |  | 208 V | Electric Facility | Bad connection inside meter panel caused contact to burn. | Customer Problem | 703-157 | Transformer | 25 | Panel | 703 |  | 02819 Patrick, Damion | CM O&E SUP | Bad connection inside meter panel c | 32.7624 | -117.1407 | 2019 | Non Conductor
OMD0000658167-01 | Dmg Dim/Nolite - Other | 2019-09-05 12:53 | 2019-09-05 11:16 | 2019-09-05 11:41 | N | N | N | N | Y | Actual Ignition | 4 kV |  | Other/Undetermined | Lightning Strike to palm tree next to pole. Damaged Secondary Service | Weather Damaged Connector | 516-72 | Transformer | 150 | P131103 | 516 |  | 02704 Martinez, Chris | CM O&E SUP | Repaired secondary and refused bank | 33.1162 | -117.0873 | 2019 | Veg
OMD0000659330-01 | Emer-Specl Req - Fire/Police/Gov | 2019-09-09 14:09 | 2019-09-09 12:43 | 2019-09-09 12:51 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | In-line switch broke at attachment. | Weather Damaged Device | 718-234 | Three Phase Transformer | 75 | P100044 | 718 | In-line BYPASS switch broke at the primary shoe attachment. | 02819 Patrick, Damion | CM O&E SUP |  | 32.6389 | -117.1111 | 2019 | Non Conductor
OMD0000660293-01 | No Lights in Part-Just Started | 2019-09-12 18:12 | 2019-09-12 17:35 | 2019-09-12 17:46 | Y | N | N | N | N | Arching/Charring |  | 120 V | Other/Undetermined | n/a | Customer Problem | 1434-120 | Transformer | 50 |  | 1434 |  | 02819 Patrick, Damion | CM O&E SUP | Customer has a bad test block...abl | 32.6999 | -117.1246 | 2019 | Other All
OMD0000660988-02 | Branch Outage | 2019-09-16 09:48 | 2019-09-16 08:15 | 2019-09-16 08:41 | N | N | N | N | N | Arching/Charring | 12 kV |  | Contact by Object |  | Device Damaged | 448-23R | Recloser |  | P45345 | 448 |  | 02766 Mcghen, Ryan | CM O&E SUP | Woodpecker contact on station 448-6 | 32.5948 | -116.5323 | 2019 | Animal
OMD0000662041-01 | Dmg/Wlite-Flash or Sparks | 2019-09-20 05:55 | 2019-09-19 23:41 | 2019-09-19 23:41 | N | N | N | N | Y | Arching/Charring | 12 kV |  | Electric Facility | loose bolts on a phz swi 381-444 no fire blts glowing called crew to fix | Conductor Damaged | 384-51 | Transformer | 25 | 381-444 | 384 | ELLIOTT SUB P228456 | 68063 Piraino, Pete | CM O&E SUP | called crewto repl blots on swi 381 | 32.8175 | -117.0897 | 2019 | Other All
OMD0000663765-01 | Dmg/Wlite-Flash or Sparks | 2019-09-26 21:48 | 2019-09-26 19:01 | 2019-09-26 19:28 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Connector Damaged | 322-82 | Transformer | 25 | p193845 | 322 | pothead failure | 12558 Simmons, Anthony | CM O&E SUP |  | 32.7072 | -117.0266 | 2019 | OH to UG
OMD0000675309-01 | Dmg/Wlite-Other | 2019-11-08 12:12 | 2019-11-08 12:03 | 2019-11-08 12:04 | N | N | N | N | Y | Arching/Charring | 12 kV |  | Electric Facility | tracking on pole caused it to catch fire | Customer Restored | 545-372 | Transformer | 50 | p837134 | 545 | pole fire from tracking | 00108 Alvarez, Marco | CM O&E SUP |  | 32.7846 | -117.252 | 2019 | Other All
OMD0000677299-01 | No Lights - Cause Unknown | 2019-11-15 14:01 | 2019-11-15 12:01 | 2019-11-15 12:18 | N | N | N | N | N | Arching/Charring |  | 120 V | Other/Undetermined | load side of cust panel looks overloaded | Conductor Damaged | 703-257 | Transformer | 25 |  | 703 | LOAD SIDE SOCKET AT PANEL IS OVERLOADED, THE THW WAS BRUNT I | 09424 Garcia, Raul | CM O&E SUP |  | 32.759 | -117.1352 | 2019 | Other All
OMD0000682170-01 | No Lights in Part-Just Started | 2019-12-01 22:01 | 2019-12-01 20:36 | 2019-12-01 21:03 | N | N | N | N | Y | Arching/Charring |  | 240 V | Other/Undetermined | corrosion in the sec molds | Weather Damaged Connector | 64-418 | Transformer | 50 | sh2012860 | 64 |  | 00108 Alvarez, Marco | CM O&E SUP |  | 32.8538 | -117.223 | 2019 | Non Conductor
OMD0000688564-01 | Emer-Specl Req - Fire/Police/Gov | 2019-12-22 00:37 | 2019-12-21 22:06 | 2019-12-21 22:29 | N | Y | N | N | N | Actual Ignition | 4 kV |  | Other/Undetermined | Small ignition possibly caused by tracking from salty air. 125 amp Fuse holder was burnt in half. | Heat Device/Overload | 56-306 | Transformer | 150 | P137274 | 56 |  | 05185 Moore, Adrian | CM O&E SUP | Blown 125a fuse on 4kv cir PB1 @ P1 | 32.7974 | -117.2478 | 2019 | Other All
OMD0000690851-01 | Transformer Outage | 2019-12-31 18:37 | 2019-12-31 18:08 | 2019-12-31 18:08 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility | WATER IN SH13282 | Weather Damaged Connector | 159-207 | Transformer | 25 | SH13282 | 159 | BAD SEC. MOLD AT SH13282 | 09424 Garcia, Raul | CM O&E SUP | *BAD SEC. MOLD AT SH13282 *ACROSS T | 32.5798 | -117.1318 | 2019 | Non Conductor
OMD0000695594-01 | Emer-Specl Req - Fire/Police/Gov | 2020-01-21 23:43 | 2020-01-21 21:59 | 2020-01-21 22:23 | N | N | N | N | Y | Actual Ignition |  | 120 V | Other/Undetermined | HOUSE FIRE TO 4369 ALTADENA AVE | Undetermined | 342-229 | Transformer | 150 |  | 342 |  | 09424 Garcia, Raul | CM O&E SUP | 1/21/20 HOUSE FIRE AT 4369 ALTADENA | 32.757 | -117.0848 | 2020 | Other All
OMD0000709274-01 | Emer-Specl Req - Fire/Police/Gov | 2020-03-14 19:11 | 2020-03-14 18:22 | 2020-03-14 18:56 | Y | N | N | N | N | Actual Ignition | 12 kV |  | Electric Facility | cut out caught on fire - dirty | Device Deenergized for Safety | 545-107 | Transformer | 125 | P2218269256 | 545 | cut out caught on fire from being dirty | 00108 Alvarez, Marco | CM O&E SUP | crew to replace 3 cut ots and fuses | 32.7724 | -117.2509 | 2020 | Non Conductor
OMD0000709889-01 | Branch Outage | 2020-03-18 04:26 | 2020-03-18 00:52 | 2020-03-18 00:53 | Y | N | N | N | N | Actual Ignition | 12 kV |  | Vegetation Contact |  | Conductor Damaged | 442-2R | Recloser |  | Z173131 | 442 | wire down | 02766 Mcghen, Ryan | CM O&E SUP | Primary wire down P330216 & Z173131 | 32.8176 | -116.5245 | 2020 | Veg
OMD0000718315-01 | Branch Outage | 2020-04-22 10:02 | 2020-04-22 09:03 | 2020-04-22 09:20 | N | N | N | N | N | Arching/Charring | 12 kV |  | Contact by Object | Woodpeckercontact on station 441-55 | Foreign Object Contacted Device | 441-27R | Recloser |  | P45809 | 441 |  | 02766 Mcghen, Ryan | CM O&E SUP | Woodpecker contact on station 441-5 | 32.7237 | -116.427 | 2020 | Animal
OMD0000723181-01 | Dmg/Wlite-Flash or Sparks | 2020-05-10 16:27 | 2020-05-10 15:10 | 2020-05-10 15:53 | N | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility |  | Connector Damaged | 41-308 | Transformer | 25 | P834857 | 41 |  | 12558 Simmons, Anthony | CM O&E SUP |  | 32.6805 | -117.0939 | 2020 | Non Conductor
OMD0000724870-01 | Dmg/Wlite-Flash or Sparks | 2020-05-16 16:36 | 2020-05-16 14:37 | 2020-05-16 14:50 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Device Damaged | 719-343 | Transformer | 50 | p34171 | 719 | hookstick switch flashed over causing it to be inoperable | 05185 Moore, Adrian | CM O&E SUP | hookstick switiches need to be chan | 32.6168 | -117.083 | 2020 | Non Conductor
OMD0000725063-01 | Emer-Specl Req - Fire/Police/Gov | 2020-05-17 15:46 | 2020-05-17 15:32 | 2020-05-17 15:32 | N | N | N | N | Y | Actual Ignition |  | 120 V | Other/Undetermined | CUST GARAGE FIRE CAUSED SERV TO MELT INSDE CONDUIT | Service Deenergized For Safety | 701-592 | Transformer | 25 |  | 701 |  | 03936 Llano, Brian | CM O&E SUP | FIRE DAMAG MAYERS BOX & CONDUIT. NE | 32.8067 | -117.1376 | 2020 | Other All
OMD0000745800-02 | Branch Outage | 2020-08-01 14:48 | 2020-08-01 11:36 | 2020-08-01 12:42 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | blown up pothead | Damaged Underground Cable | F2198965 | Fuse | 20A | p45248 | 444 |  | 12558 Simmons, Anthony | CM O&E SUP | damaged pot head at p45248. caused | 32.6346 | -116.1664 | 2020 | Non Conductor
OMD0000752041-01 | Emer-Specl Req - Fire/Police/Gov | 2020-08-20 06:35 | 2020-08-20 05:15 | 2020-08-20 05:51 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Conductor Damaged | 165-208 | Transformer | 25 | P776713 | 165 | Bad cable 700' #2 CU 2 wire | 02766 Mcghen, Ryan | CM O&E SUP | Cable faulted 2' outside of conduit | 32.7137 | -117.0842 | 2020 | OH to UG
OMD0000756644-01 | Dmg/Wlite-Other | 2020-09-04 05:01 | 2020-09-04 02:57 | 2020-09-04 02:57 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Device Damaged | 244-163 | Transformer | 50 | p477083 | 244 | Street side cutout is arcing & sparking | 05185 Moore, Adrian | CM O&E SUP | Street side cut-out is arcing & spa | 32.8468 | -116.926 | 2020 | Non Conductor
OMD0000651408-01 | Branch Outage | 2019-08-11 16:04 | 2019-08-11 14:21 | 2019-08-11 14:21 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Contact by Object | Car contact on 3 phase terminator caused elec. fault and the cable to melt | Foreign Object Contacted Device | 904-255 | Switch |  | D169719 | 904 | Car Vs. 3 phase terminator, and single phase xmfr | 03417 Clark, Brian J | EA O&E SUP | Crew repairs neede to replace UG eq | 33.2097 | -117.2788 | 2019 | UG Vehicle
OMD0000654028-01 | No Lights - Cause Unknown | 2019-08-21 13:12 | 2019-08-21 09:04 | 2019-08-21 09:29 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility | sec molds burnt / melted / shorted together. Across street from M2539069399, Prestwick Dr. | Connector Damaged | 65-176S | Transformer | 50 | Unmapped Sec HH | 65 | Bad molds in DEE Manhole. Crew will need to de-energize UG c | 03033 Laws, Jeffery | RA O&E SUP |  | 32.8606 | -117.2473 | 2019 | UG UG Cable
OMD0000762598-01 | Emer-Specl Req - Fire/Police/Gov | 2020-09-21 18:32 | 2020-09-21 01:45 | 2020-09-21 02:06 | N | N | N | Y | N | Actual Ignition |  | 120 V | Other/Undetermined | POLE WAS ON FIRE WHEN UPON ARRIVAL | Undetermined | 341-351 | Three Phase Transformer | 75 |  | 341 | POLE FIRE | 09424 Garcia, Raul | CM O&E SUP | POLE FIRE | 32.6603 | -117.0342 | 2020 | Other All
OMD0000762986-02 | Branch Outage | 2020-09-22 14:33 | 2020-09-22 12:03 | 2020-09-22 12:52 | N | N | N | N | N | Arching/Charring | 12 kV |  | Contact by Object |  | Foreign Object Contact Conductor | F2072268 | Fuse | 150A | P81866 | 718 | Primary wire down | 02766 Mcghen, Ryan | CM O&E SUP | Forklift contacted conductor. No i | 32.6408 | -117.1023 | 2020 | Other Contact
OMD0000764258-01 | Emer-Specl Req - Fire/Police/Gov | 2020-09-28 00:12 | 2020-09-27 22:27 | 2020-09-27 22:49 | N | Y | N | N | N | Actual Ignition |  | 120 V | Other/Undetermined | APPARTMENT FIRE | Vandalism | WA4-100 | Transformer | 50 |  | WA4 |  | 09424 Garcia, Raul | CM O&E SUP | APPARTMENT FIRE, CUT AT POLE FOR SA | 32.7462 | -117.1051 | 2020 | Other All
OMD0000769603-01 | Dmg/Wlite-Flash or Sparks | 2020-10-15 22:32 | 2020-10-15 22:24 | 2020-10-15 22:26 | N | N | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | fog | Weather Damaged Device | 158-220 | Transformer | 25 | P185129 | 158 |  | 02766 Mcghen, Ryan | CM O&E SUP | Normal tracking due to fog and mois | 32.5775 | -117.1187 | 2020 | Other All
OMD0000770037-01 | Emer-Specl Req - Fire/Police/Gov | 2020-10-17 08:37 | 2020-10-17 07:14 | 2020-10-17 07:47 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Weather Damaged Conductor | 374-87 | Transformer | 50 | P832706 | 374 | Bad service #4sscc | 02766 Mcghen, Ryan | CM O&E SUP | Need service crew to replace 35' of | 32.691 | -117.186 | 2020 | Conductor
OMD0000770254-01 | Dmg/Wlite-Tree on Wires | 2020-10-18 13:15 | 2020-10-18 12:03 | 2020-10-18 12:23 | N | N | N | N | N | Arching/Charring |  | 120 V | Vegetation Contact |  | Foreign Object Contact Services | 366-284 | Transformer | 50 | P737500 | 366 |  | 02766 Mcghen, Ryan | CM O&E SUP | Repaired bad spot in service where | 32.7542 | -117.1067 | 2020 | Veg
OMD0000771842-01 | Immediate Need - Fire/Police | 2020-10-24 11:36 | 2020-10-24 11:20 | 2020-10-24 11:20 | N | N | N | N | N | Arching/Charring |  | 208 V | Electric Facility | SERVICE BURNED OPEN MIDSPAN. | Weather Damaged Service | UNKNOWN | Switch |  | P2026073576 | 1418 | REPLACE DAMAGED 50' 3/0 4W SERVICE. STA 1418-582 DE-ENERGIZ | 21969 Delgadillo, Joseph | CM O&E SUP | DAMAGED 3/0 SERVICE MID-SPAN. CREW | 32.7206 | -117.11 | 2020 | Conductor
OMD0000774411-01 | Dmg Dim/Nolite-WireDown Pole to | 2020-11-03 14:36 | 2020-11-03 13:16 | 2020-11-03 13:44 | N | N | N | N | N | Arching/Charring |  | 240 V | Other/Undetermined | Service runs over a detached garage and i think the srvice was rubbing on a vent pipe at one time. | Service Down | 362-221 | Transformer | 25 |  | 362 | service burned open midspan. | 02766 Mcghen, Ryan | CM O&E SUP | Service burned open midspan. Needs | 32.7702 | -117.1178 | 2020 | Other Contact
OMD0000775053-01 | Transformer Outage | 2020-11-05 13:15 | 2020-11-05 12:21 | 2020-11-05 12:27 | N | N | N | N | N | Arching/Charring |  | 240 V | Other/Undetermined | Overloaded service. | Service Deenergized For Safety | GH2-119 | Transformer | 50 | Z1989773099 | GH2 | Melted service | 02766 Mcghen, Ryan | CM O&E SUP | Overloaded service to construction | 32.7101 | -117.1253 | 2020 | Other All
OMD0000775287-01 | Transformer Outage | 2020-11-06 12:09 | 2020-11-06 11:02 | 2020-11-06 11:56 | N | N | N | N | N | Arching/Charring |  | 240 V | Vegetation Contact |  | Tree Damaged Service | 323-61 | Transformer | 50 |  | 323 | TREE DAMAGED SERVICE, REPLACE WITH 45' #4 SSCC | 21969 Delgadillo, Joseph | CM O&E SUP | TREE DAMAGED SERVICE. CREW TO REPLA | 32.7077 | -117.0802 | 2020 | Veg
OMD0000775635-01 | Dmg Dim/Nolite - Explosion | 2020-11-07 14:50 | 2020-11-07 14:01 | 2020-11-07 14:28 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Weather Damaged Service | 377-155 | Transformer | 50 | P830915 | 377 | Damaged service. Backyarder | 02766 Mcghen, Ryan | CM O&E SUP | Service crew to replace 75' #6 sscc | 32.6948 | -117.1877 | 2020 | Non Conductor
OMD0000775955-01 | Emer-Specl Req - Fire/Police/Gov | 2020-11-08 14:29 | 2020-11-08 13:49 | 2020-11-08 14:10 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Weather Damaged Service | RD1-36 | Transformer | 25 | P173828 | RD1 |  | 02766 Mcghen, Ryan | CM O&E SUP | Service feeding 4774 College Ave. b | 32.7646 | -117.0674 | 2020 | Non Conductor
OMD0000775958-01 | Dmg Dim/Nolite - Flash or Sparks | 2020-11-08 15:02 | 2020-11-08 14:29 | 2020-11-08 14:29 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Weather Damaged Conductor | RD1-36 | Transformer | 25 | P173828 | RD1 | Service burned open midspan. Backyarder. Service is lashed | 02766 Mcghen, Ryan | CM O&E SUP | Service is lashed to guy wire and i | 32.7646 | -117.0674 | 2020 | Conductor
OMD0000780315-01 | Dmg Dim/Nolite-WireDown Pole to | 2020-11-25 15:02 | 2020-11-25 13:28 | 2020-11-25 13:34 | N | N | N | N | N | Arching/Charring |  | 240 V | Other/Undetermined | Point of support pulled away from home causing wire to slack and connections to get together. | Customer Problem | 1434-141 | Transformer | 50 | P234100J | 1434 |  | 02766 Mcghen, Ryan | CM O&E SUP | Customers point of attachment pulle |  |  | 2020 | Conductor
OMD0000782391-01 | Branch Outage | 2020-12-03 20:36 | 2020-12-03 19:23 | 2020-12-03 19:58 | Y | Y | N | N | N | Actual Ignition | 12 kV |  | Other/Undetermined | Lightning arrester caught fire | Device Damaged | F87016 | Fuse | 150A | p870450 | 1049 | LA caught on fire damaging cut-out | 05185 Moore, Adrian | CM O&E SUP | Need cut-out & LA replaced | 32.7209 | -117.0978 | 2020 | Other All
OMD0000784885-01 | Transformer Outage | 2020-12-11 09:36 | 2020-12-11 08:46 | 2020-12-11 09:21 | N | N | N | N | N | Arching/Charring |  | 120 V | Other/Undetermined | Could have been hit by trash truck or could have arched from old cracked insulation. | Weather Damaged Conductor | 366-124 | Transformer | 50 | P2141073583 | 366 | damaged service wire. 120v service 2 wire | 02766 Mcghen, Ryan | CM O&E SUP | Service wire brokre midspan. Not s | 32.7518 | -117.11 | 2020 | Other All
OMD0000785723-03 | Branch Outage | 2020-12-15 11:20 | 2020-12-15 09:52 | 2020-12-15 10:01 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Heat Device/Overload | 1434-10AE | Switch |  | P34684 | 1434 | Outage cir 1434. Need to replace all three lightning arrest | 02766 Mcghen, Ryan | CM O&E SUP | Two blown lightning arrestors on P3 | 32.7068 | -117.1206 | 2020 | Non Conductor
OMD0000786199-01 | Dmg Dim/Nolite-Pole Burning | 2020-12-17 08:08 | 2020-12-17 07:28 | 2020-12-17 07:28 | N | N | N | N | N | Arching/Charring |  | 240 V | Other/Undetermined | Overloaded service wire. | Conductor Damaged | 1434-409 | Three Phase Transformer | 500 | Temp power poles 415 31ST ST | 1434 | Overloaded service. Made repairs customer still in power bu | 02766 Mcghen, Ryan | CM O&E SUP | Overloaded service melted at connec | 32.7093 | -117.1269 | 2020 | Non Conductor
OMD0000786691-01 | Flickering Lights-Just Started | 2020-12-19 11:09 | 2020-12-19 10:01 | 2020-12-19 10:26 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Conductor Damaged | WA6-51 | Transformer | 25 | P2091473977 | WA6 | Bad service wire | 02766 Mcghen, Ryan | CM O&E SUP | Need service crew to replace servic | 32.7386 | -117.0971 | 2020 | Conductor
OMD0000788536-01 | Dmg/Wlite-Flash or Sparks | 2020-12-28 17:27 | 2020-12-28 14:34 | 2020-12-28 14:55 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Weather Damaged Connector | 493-472 | Three Phase Transformer | 75 | P839096 | 493 | Had a crew jumperout SCADA MATE switch 493-407. Need to rep | 02766 Mcghen, Ryan | CM O&E SUP | Need crew to jumper out switch 493- | 32.7559 | -117.1677 | 2020 | Non Conductor
OMD0000794421-02 | Branch Outage | 2021-01-21 22:27 | 2021-01-21 19:55 | 2021-01-21 19:55 | N | N | N | N | N | Arching/Charring | 4 kV |  | Electric Facility |  | Connector Damaged | 168-531F | Switch Position |  | W103452 | 168 | Failed straight splices | 02766 Mcghen, Ryan | CM O&E SUP | Straight splices failed in W103452 | 32.7458 | -117.0792 | 2021 | Other All
OMD0000796637-01 | Branch Outage | 2021-01-26 05:41 | 2021-01-26 03:26 | 2021-01-26 03:46 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Heat Device/Overload | F57652 | Fuse | 100A | P839790J | 42 |  | 02766 Mcghen, Ryan | CM O&E SUP | Replaced damaged kearney c/o door. | 32.6713 | -117.0954 | 2021 | Non Conductor
OMD0000798014-01 | Dmg Dim/Nolite-WireDown Pole to | 2021-01-29 04:19 | 2021-01-29 03:26 | 2021-01-29 03:38 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Weather Damaged Service | 364-175 | Transformer | 75 | P731861J | 364 | 120' #6sscc burned open midspan | 02766 Mcghen, Ryan | CM O&E SUP | Need service crew to replace 120' # | 32.744 | -117.1077 | 2021 | Conductor
OMD0000802587-02 | Branch Outage | 2021-02-14 18:35 | 2021-02-14 15:09 | 2021-02-14 16:25 | Y | Y | Y | N | N | Arching/Charring | 12 kV |  | Electric Facility | Bad 600a tee body & components. | Damaged Underground Cable | ES23 | Fuse |  | H120889 | 493 |  | 02819 Patrick, Damion | CM O&E SUP | Bad 1000KCMIL 600a Tee's in H120889 | 32.7518 | -117.1695 | 2021 | UG UG Cable
OMD0000803679-02 | Transformer Outage | 2021-02-18 10:02 | 2021-02-18 08:14 | 2021-02-18 08:35 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Connector Damaged | S1-78 | Transformer | 100 | P1972372885 | S1 |  | 02766 Mcghen, Ryan | CM O&E SUP | 100amp kearney C/O door burned in h | 32.6933 | -117.132 | 2021 | Non Conductor
OMD0000807678-03 | Circuit Outage | 2021-03-04 17:36 | 2021-03-04 14:45 | 2021-03-04 15:12 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Connector Damaged | MG-12KV-257 | Circuit |  | H1751117007 | 257 | Faulted Cable | 02766 Mcghen, Ryan | CM O&E SUP | Need Line crew to replace faulted 2 | 32.6378 | -117.0783 | 2021 | UG Connector
OMD0000807802-01 | No Lights in Part-Just Started | 2021-03-05 09:05 | 2021-03-05 08:07 | 2021-03-05 08:32 | N | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility |  | Device Damaged | 58-517 | Transformer | 75 | 2639 grand ave meter scoket | 58 |  | 00108 Alvarez, Marco | CM O&E SUP | pulled elect meter due to meteing s | 32.8011 | -117.2215 | 2021 | Other All
OMD0000810893-02 | Circuit Outage | 2021-03-18 04:38 | 2021-03-18 01:55 | 2021-03-18 02:07 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Weather Damaged Connector | MS-12KV-706 | Circuit |  | m2347673351 | 706 |  | 00108 Alvarez, Marco | CM O&E SUP |  | 32.809 | -117.1176 | 2021 | UG Connector
OMD0000820664-01 | Emer-Specl Req - Fire/Police/Govt | 2021-05-01 00:43 | 2021-05-01 00:30 | 2021-05-01 00:30 | Y | Y | N | Y | N | Arching/Charring |  | 120 V | Other/Undetermined | SRVIEC TO HOUSE 2374 MAY HAVE BEEN OVER LOADED WHICH MAY HAVE CAUSE WIRE TO MELT TOGETHER. MAY NEED TO GET MRP INVOLED. SECOND TIME SAME SERVICE BURNS DOWN WITHIN A WEEK. HOUSE MAY BE DEMANDING TOO MUCH LOAD. | Service Down | 165-481 | Transformer | 50 | P475133 | 165 | REPLACE ALL SERVICES AT P475133. DONT HOOK SERVICE TO 2473 5 | 10056 Gomez, Miguel | CM O&E SUP | SECONDARY SERVICE MAY HAVE BEEN OVE | 32.7318 | -117.0759 | 2021 | Conductor
OMD0000820664-02 | Emer-Specl Req - Fire/Police/Govt | 2021-04-30 23:12 | 2021-04-30 21:05 | 2021-04-30 21:31 | N | Y | N | Y | N | Arching/Charring |  | 120 V | Other/Undetermined | SERVICE MAY HAVE BEEN OVERLOADED. MAY NEED TO FOLLOW UP MRP. SECOND SERVICE TO BURN DOWN WITHIN A WEEK* | Service Down | 165-481 | Transformer | 50 | P475133 | 165 | NEED CREW TO C/O ALL SERVICES AT P475133. TOATL 5 SERVICES. | 10056 Gomez, Miguel | CM O&E SUP | SERVICE OVER LOADED BURNT WIRE DOWN | 32.7318 | -117.0759 | 2021 | Conductor
OMD0000825937-01 | Branch Outage | 2021-05-24 15:42 | 2021-05-24 15:27 | 2021-05-24 15:27 | N | N | N | Y | N | Actual Ignition |  | 120 V | Electric Facility |  | Tree Damaged Service | 365-34R | Recloser |  | P2105872505 | 365 | SECONDARY WIRE DOWN, CREW TO REPLACE W/300' #4 SSCC | 21969 Delgadillo, Joseph | CM O&E SUP | SECONDARY PS WIRE DOWN FROM P210587 | 32.7413 | -117.1438 | 2021 | Veg
OMD0000826070-01 | Branch Outage | 2021-05-25 07:25 | 2021-05-25 05:45 | 2021-05-25 07:11 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | TRACKING, MELTED INSULATOR. FLASHED OVER ON THE HUBBARD BRACE, BRANCH OUTAGE | Weather Damaged Device | F2407463 | Fuse | 150A | P81412 | 159 | DAMAGED INSULATOR, TEMP REPAIRS MADE. | 21969 Delgadillo, Joseph | CM O&E SUP | DAMAGED INSULATOR P81412, TEMP REPA | 32.577 | -117.1275 | 2021 | Non Conductor
OMD0000850281-01 | Transformer Outage | 2021-08-27 10:18 | 2021-08-27 09:16 | 2021-08-27 09:44 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Transformer Problem | 57-62 | Transformer | 50 | P932643 | 57 | blown up station 50 he 57-62 @ p932643 | 00108 Alvarez, Marco | CM O&E SUP | crew to c/o sta 57-62 50 he or 75 h | 32.8079 | -117.2517 | 2021 | Non Conductor
OMD0000852929-01 | Transformer Outage | 2021-09-07 20:39 | 2021-09-07 19:53 | 2021-09-07 20:06 | N | N | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | station leaking oil and not working | Heat Device/Overload | 57-111 | Transformer | 50 | p193818 | 57 | station outage | 00108 Alvarez, Marco | CM O&E SUP |  | 32.8065 | -117.258 | 2021 | Non Conductor
OMD0000853615-01 | Transformer Outage | 2021-09-09 22:24 | 2021-09-09 22:20 | 2021-09-09 22:20 | N | N | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | storm | Weather Damaged Device | 142-305 | Transformer | 50 | p479238 | 142 |  | 00108 Alvarez, Marco | CM O&E SUP | crew to c/o sta 142-305 P479238 | 32.7894 | -117.1562 | 2021 | Other All
OMD0000853618-01 | Emer-Specl Req - Fire/Police/Govt | 2021-09-09 22:20 | 2021-09-09 20:53 | 2021-09-09 22:14 | N | N | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | storm | Weather Damaged Device | 142-305 | Transformer | 50 | p479238 | 142 | 1-50 he | 00108 Alvarez, Marco | CM O&E SUP |  | 32.7894 | -117.1562 | 2021 | Other All
OMD0000853729-01 | Circuit Outage | 2021-09-10 11:42 | 2021-09-10 08:16 | 2021-09-10 09:07 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Weather Damaged Connector | TP-12KV-846 | Circuit |  | m2683869651 | 846 | daMAGED TEE'S | 00108 Alvarez, Marco | CM O&E SUP | crew to repair 1000 connections in | 32.8989 | -117.2399 | 2021 | UG Connector
OMD0000854045-01 | Dmg/Wlite-Other | 2021-09-11 14:07 | 2021-09-11 13:11 | 2021-09-11 13:45 | N | N | N | N | N | Arching/Charring |  | 120 V | Contact by Object | lightning | Weather Damaged Pole | 279-274 | Transformer | 50 | p834018 | 279 | lightning hit p834018 | 00108 Alvarez, Marco | CM O&E SUP | POLE CAN BE REPLACED ON A LATER DAT | 32.8354 | -117.2089 | 2021 | Other All
OMD0000854102-01 | Dmg/Wlite-Flash or Sparks | 2021-09-11 19:21 | 2021-09-11 18:41 | 2021-09-11 18:59 | N | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility |  | Weather Damaged Connector | 276-407 | Transformer | 50 | house | 276 |  | 00108 Alvarez, Marco | CM O&E SUP |  | 32.8347 | -117.2024 | 2021 | Non Conductor
OMD0000856393-01 | Emer-Specl Req - Fire/Police/Govt | 2021-09-22 06:13 | 2021-09-22 04:31 | 2021-09-22 04:31 | N | N | N | N | N | Arching/Charring |  | 120 V | Contact by Object | STRUCTRE FIRE | Foreign Object Contacted Wire | 80-153 | Transformer | 100 |  | 80 | FIRE AT ROAD ONE TOW YARD DAMAGED STREET LIGHT WIRE BETWEEN | 21969 Delgadillo, Joseph | CM O&E SUP | FIRE AT ROAD ONE TOW YARD DAMAGED S | 32.6948 | -117.1217 | 2021 | Other All
OMD0000857061-01 | Branch Outage | 2021-09-24 19:54 | 2021-09-24 18:46 | 2021-09-24 18:46 | N | N | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | lightning | Weather Damaged Transformer | F59024 | Fuse | 60A | P838583 | 43 | Lightning strike transformer bank | 69761 Simmons, Taylor | CM O&E SUP |  | 32.6625 | -117.1098 | 2021 | Other All
OMD0000857068-02 | Circuit Outage | 2021-09-24 17:58 | 2021-09-24 17:12 | 2021-09-24 17:12 | N | N | N | N | N | Arching/Charring | 12 kV |  | Vegetation Contact |  | Foreign Object Contacted Wire | OY-12KV-153 | Circuit |  | P729307 | 153 | LIGHTNING ARRESTORS BLOWN, CUTOUT DAMAGED. REPLACE DOUBLE OU | 21969 Delgadillo, Joseph | CM O&E SUP | DAMAGE TO LIGHTNING ARRESTORS, CREW | 32.5953 | -117.0641 | 2021 | Veg
OMD0000857182-01 | Emer-Specl Req - Fire/Police/Govt | 2021-09-24 20:15 | 2021-09-24 18:24 | 2021-09-24 19:41 | N | N | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | damaged cross arm | Weather Damaged Device | 701-63 | Transformer | 50 |  | 701 |  | 00108 Alvarez, Marco | CM O&E SUP |  | 32.7928 | -117.1269 | 2021 | Other All
OMD0000857203-01 | No Lights - Cause Unknown | 2021-09-24 22:45 | 2021-09-24 21:48 | 2021-09-24 22:16 | N | N | N | N | N | Arching/Charring | 12 kV | 120 V | Electric Facility |  | Weather Damaged Service | RD4-57 | Transformer | 50 | P275924 | RD4 | BURNED OPEN SERVICE | 69761 Simmons, Taylor | CM O&E SUP |  | 32.7565 | -117.0673 | 2021 | Non Conductor
OMD0000857501-02 | Circuit Outage | 2021-09-27 01:50 | 2021-09-26 20:18 | 2021-09-27 01:39 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Connector Damaged | MG-12KV-719 | Circuit |  | M1695574199 | 719 | BAD 600A T'S | 69761 Simmons, Taylor | CM O&E SUP |  | 32.6293 | -117.0889 | 2021 | UG Connector
OMD0000862618-01 | Dmg/Wlite-Flash or Sparks | 2021-10-15 16:43 | 2021-10-15 15:45 | 2021-10-15 16:40 | Y | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility | ALUM CONNECTION | Weather Damaged Connector | 342-1032 | Transformer | 25 | P170279 | 342 |  | 21969 Delgadillo, Joseph | CM O&E SUP | REPLACED BURNT ALUM CONNECTION | 32.7592 | -117.0743 | 2021 | Non Conductor
OMD0000866773-01 | Emer-Specl Req - Fire/Police/Govt | 2021-11-03 08:09 | 2021-11-03 07:10 | 2021-11-03 07:48 | N | N | N | N | N | Arching/Charring |  | 240 V | Contact by Object |  | Service Vandalism | LA3-97 | Transformer | 50 | p83557 | LA3 | #6 ssc 90' burnt open mid span and came down | 00108 Alvarez, Marco | CM O&E SUP | service damage, maybe tree trimming | 32.6744 | -117.0747 | 2021 | Other Contact
OMD0000867744-01 | Circuit Outage | 2021-11-08 03:45 | 2021-11-07 23:06 | 2021-11-07 23:27 | N | N | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | Bad 600a Tee's, water damage. | Connector Damaged | OT-12KV-100 | Circuit |  | M2180170583 | 100 | Bad 600a Tee's in M2180170583 | 02819 Patrick, Damion | CM O&E SUP | Bad 600a Tee's in M2180170583 | 32.7623 | -117.2078 | 2021 | UG Connector
OMD0000869349-01 | Branch Outage | 2021-11-15 20:47 | 2021-11-15 17:21 | 2021-11-15 17:45 | N | N | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | smoking in hh | Weather Damaged Conductor | F358139 | Fuse | 150A | h2296572126 | 142 | 200' solid cable | 00108 Alvarez, Marco | CM O&E SUP | crew to replace burned up cable 200 | 32.7887 | -117.1584 | 2021 | UG UG Cable
OMD0000871796-02 | Branch Outage | 2021-11-26 09:26 | 2021-11-26 06:55 | 2021-11-26 07:19 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Equipment Damaged Conductor | 376-527AE | Switch |  | P181324 | 376 | wire down | 69761 Simmons, Taylor | CM O&E SUP |  | 32.6783 | -117.1734 | 2021 | Conductor
OMD0000871800-01 | Emer-Specl Req - Fire/Police/Govt | 2021-11-26 09:20 | 2021-11-26 09:19 | 2021-11-26 09:19 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Weather Damaged Wire | 376-374 | Transformer | 300 | P181324 | 376 |  | 21969 Delgadillo, Joseph | CM O&E SUP |  | 32.6273 | -117.1304 | 2021 | Conductor
OMD0000872406-01 | Dmg/Wlite-Wire Down Pole to House | 2021-11-30 05:14 | 2021-11-30 04:52 | 2021-11-30 04:52 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility | OPEN WIRE SERVICE TWISTED, WIRE DOWN | Weather Damaged Service | 155-690 | Transformer | 50 | P835769 | 155 | DAMAGED OPEN WIRE SERVICE. REPLACE WITH 50' #6 SSCC | 21969 Delgadillo, Joseph | CM O&E SUP | OPEN WIRE SERVICE DOWN |  |  | 2021 | Conductor
OMD0000873371-01 | Circuit Outage | 2021-12-03 14:06 | 2021-12-03 12:21 | 2021-12-03 12:21 | N | N | N | N | N |  | 12 kV |  | Other/Undetermined | BIRD CONTACT CAUSED SPARKS | Foreign Object Contacted Device | BD-12KV-534 | Circuit |  |  | 534 | OH SWI IS DAMAGED | 39759 Hollins, Daryl | CM O&E SUP | CREW TO REPLACE DAMAGED SWI |  |  | 2021 | Animal
OMD0000873948-02 | Branch Outage | 2021-12-06 17:41 | 2021-12-06 14:31 | 2021-12-06 17:13 | Y | N | N | N | N |  | 12 kV |  | Electric Facility | PRI AL TO Cu CONN ON P104757. CORROSION | Customer Restored | F30002 | Fuse | 15A | P104757 | 67 |  | 03936 Llano, Brian | CM O&E SUP | CROW CONT STA 67-830. REFUSE 2-15A | 32.6782 | -116.7484 | 2021 | Non Conductor
OMD0000877450-01 | Emer-Specl Req - Fire/Police/Govt | 2021-12-16 10:01 | 2021-12-16 07:28 | 2021-12-16 09:54 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Device Damaged | BRM1-14 | Transformer | 50 | Z2145073204 | BRM1 | BURNED 900 AMP DISCONNECTS......CUTOUT STYLE | 69761 Simmons, Taylor | CM O&E SUP |  | 32.7527 | -117.1223 | 2021 | Non Conductor
OMD0000877759-01 | No Lights - Cause Unknown | 2021-12-17 00:28 | 2021-12-16 23:58 | 2021-12-17 00:22 | Y | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility |  | Weather Damaged Service | WA6-150 | Transformer | 25 | P930119 | WA6 | BLOWN ALUMINUM SERVICE | 69761 Simmons, Taylor | CM O&E SUP |  | 32.7348 | -117.1072 | 2021 | Non Conductor
OMD0000884796-01 | Transformer Outage | 2022-01-16 15:47 | 2022-01-16 14:51 | 2022-01-16 15:06 | N | N | N | N | N | Arching/Charring |  | 120 V | Other/Undetermined | melting sec connection | Weather Damaged Service | 277-356 | Transformer | 15 |  | 277 | bad sec service need to change out #6 ssc 120' | 00108 Alvarez, Marco | CM O&E SUP | crew to change out #6 ssc service f | 32.799 | -117.1829 | 2022 | Non Conductor
OMD0000885165-01 | Dmg/Wlite-Other | 2022-01-18 12:36 | 2022-01-18 10:10 | 2022-01-18 10:22 | N | N | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | burned tee connections | Weather Damaged Connector | 746-249 | Transformer | 750 | h2586970385 | 746 |  | 00108 Alvarez, Marco | CM O&E SUP |  | 32.8742 | -117.2152 | 2022 | UG Connector
OMD0000896680-01 | Dmg Dim/Nolite - Wire Hanging Low | 2022-03-13 18:30 | 2022-03-13 17:31 | 2022-03-13 17:44 | N | N | N | N | Y | Arching/Charring |  | 240 V | Contact by Object | equipment struck sec service and burned partially in half | Foreign Object Contact Services | 103-311 | Transformer | 25 | p833052 | 103 | construction crew hit sec service from pole to house to 4811 | 00108 Alvarez, Marco | CM O&E SUP | gate code 0007 to lock | 32.7777 | -117.1992 | 2022 | Other Contact
OMD0000901414-03 | Branch Outage | 2022-04-06 07:04 | 2022-04-06 03:04 | 2022-04-06 03:24 | N | N | N | N | N |  | 12 kV |  | Contact by Object |  | Motor Vehicle Contact with Xfmr | F2171882 | Fuse | 150A |  | 1482 | 2 single phase transformer hit off both pads. Damaged pri. & | 05185 Moore, Adrian | CM O&E SUP | 2 single phase transformers hit by | 32.7274 | -117.1694 | 2022 | UG Vehicle
OMD0000902310-01 | Transformer Outage | 2022-04-09 20:29 | 2022-04-09 17:06 | 2022-04-09 17:06 | N | N | N | N | N | Arching/Charring |  | 120 V | Other/Undetermined | wire broke at connection | Weather Damaged Connector | 51-228 | Transformer | 25 | p931003 | 51 | sec wire #4 sol | 00108 Alvarez, Marco | CM O&E SUP |  | 32.7302 | -117.2452 | 2022 | Non Conductor
OMD0000903769-01 | Emer-Specl Req - Fire/Police/Govt | 2022-04-17 08:42 | 2022-04-17 04:54 | 2022-04-17 05:12 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | P834093 TRACKING FROM M0ISTURE | Device Damaged | 279-51 | Transformer | 50 | P834093 | 279 | 1 repl 12 kv 10ft xarm P834093 | 68063 Piraino, Pete | CM O&E SUP | CALLED CREW TO REPL 10FT XARM | 32.836 | -117.2061 | 2022 | Non Conductor
OMD0000905954-01 | Emer-Specl Req - Fire/Police/Govt | 2022-04-25 16:49 | 2022-04-25 16:49 | 2022-04-25 16:49 | N | N | N | N | Y | Arching/Charring |  | 120 V | Other/Undetermined | Trash fire by base of pole | Fire Damaged Pole | 361-233 | Transformer | 200 | P104647 | 361 |  | 05185 Moore, Adrian | CM O&E SUP | Rubbish fire extinguished @ base of | 32.7488 | -117.1308 | 2022 | Other All
OMD0000910514-01 | Branch Outage | 2022-05-15 10:32 | 2022-05-15 08:25 | 2022-05-15 08:48 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Heat Device/Overload | 445-894R | Recloser |  | P203129 | 445 | Flashed over transformer, 445-722. Need to replace station | 02766 Mcghen, Ryan | CM O&E SUP | Need crew to replace station 445-72 | 32.6709 | -116.3193 | 2022 | Non Conductor
OMD0000916312-03 | Circuit Outage | 2022-06-09 03:14 | 2022-06-09 00:21 | 2022-06-09 03:12 | N | N | N | N | N | Arching/Charring | 4 kV |  | Contact by Object |  | Foreign Object Contacted Wire | AD-4KV-AD1 | Circuit |  |  | AD1 |  | 69761 Simmons, Taylor | CM O&E SUP | DAF filled out by Dotson |  |  | 2022 | Other Contact
OMD0000916563-02 | Branch Outage | 2022-06-10 06:18 | 2022-06-10 02:16 | 2022-06-10 02:35 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Damaged Underground Cable | 257-31AE | Switch |  | H1751117002 | 257 | 320' FAULTED 750 AL | 69761 Simmons, Taylor | CM O&E SUP |  | 32.6365 | -117.0832 | 2022 | UG UG Cable
OMD0000917902-01 | Branch Outage | 2022-06-16 09:22 | 2022-06-16 07:32 | 2022-06-16 07:32 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | Bad 900a switch on Phase 1. | Heat Device/Overload | 463-558 | Switch |  | Z192688 | 463 |  | 02819 Patrick, Damion | CM O&E SUP | Bad switch on Z192688...circuit Out | 32.5642 | -117.0324 | 2022 | Non Conductor
OMD0000917902-02 | Branch Outage | 2022-06-16 08:25 | 2022-06-16 06:15 | 2022-06-16 08:03 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Heat Device/Overload | 463-558 | Switch |  | 463-558 | 463 | swi.460-2 @ P84762 is showing signs of heat due to poor cont | 05185 Moore, Adrian | CM O&E SUP | Damaged hook-stick swi.463-558 | 32.5642 | -117.0324 | 2022 | Non Conductor
OMD0000918188-01 | Dmg/Wlite-Other | 2022-06-16 17:53 | 2022-06-16 17:06 | 2022-06-16 17:21 | N | N | N | N | N |  | 12 kV |  | Other/Undetermined | Homless Fire | Fire Damaged Pole | 44-363 | Transformer | 75 | p1784173929 | 44 | Pole will need to be follow-up on. May need to be replaced. | 05185 Moore, Adrian | CM O&E SUP | Pole will need to be follow-up on. | 32.6547 | -117.0955 | 2022 | Other All
OMD0000919983-01 | Circuit Outage | 2022-06-23 13:23 | 2022-06-23 10:30 | 2022-06-23 12:59 | N | N | N | N | N | Arching/Charring | 4 kV |  | Contact by Object | WIRE DOWN | Moter Vehicle Contact with Pole | NC-4KV-NC3 | Circuit |  | P738995 | NC3 | CAR VS POLE NCPD INC#222493 4KV NC3 | 21969 Delgadillo, Joseph | CM O&E SUP |  | 32.6806 | -117.1098 | 2022 | Other Contact
OMD0000922990-01 | Emer-Specl Req - Fire/Police/Govt | 2022-07-02 17:44 | 2022-07-02 15:14 | 2022-07-02 17:40 | N | N | N | N | N |  | 12 kV |  | Electric Facility | squirrel got across pothead and caused sm. brush fire | Foreign Object Contacted Device | 365-329 | Three Phase Transformer | 150 | P2107872488 | 365 |  | 12558 Simmons, Anthony | CM O&E SUP | squirrel gort across pothead. cause | 32.7428 | -117.1456 | 2022 | OH to UG
OMD0000923762-01 | Emer-Specl Req - Fire/Police/Govt | 2022-07-07 03:41 | 2022-07-06 23:48 | 2022-07-07 00:04 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | plastic stand off burned off of pin | Weather Damaged Device | 545-348 | Transformer | 50 | p932963 | 545 | plastic stand off burned off of the pin and needs to be repl | 00108 Alvarez, Marco | CM O&E SUP | crew to replace burned up stand off | 32.7873 | -117.2541 | 2022 | Non Conductor
OMD0000925553-01 | Emer-Specl Req - Fire/Police/Govt | 2022-07-14 13:53 | 2022-07-14 13:53 | 2022-07-14 13:53 | N | N | N | N | N | Arching/Charring | 4 kV |  | Electric Facility |  | Connector Damaged | 80-412 | Transformer | 50 | p75822 | 80 | Need crew to inspect & change out burnt up 'H' body connecti | 05185 Moore, Adrian | CM O&E SUP | Need crew to inspect & change out b | 32.6994 | -117.0938 | 2022 | Non Conductor
OMD0000927273-01 | No Lights - Cause Unknown | 2022-07-21 15:49 | 2022-07-21 13:54 | 2022-07-21 14:06 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Connector Damaged | 1297-253 | Transformer | 100 | p2152272893 | 1297 | 1/O 3 phase RTS is overloaded & keeps burning connections. S | 05185 Moore, Adrian | CM O&E SUP | 1/O 3 phase RTS is overloaded & kee | 32.7547 | -117.1327 | 2022 | Non Conductor
OMD0000927614-01 | Dmg/Wlite-Flash or Sparks | 2022-07-22 22:31 | 2022-07-22 20:52 | 2022-07-22 21:04 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Transformer Problem | 133-52 | Transformer | 15 | p1965273073 | 133 | Arcing & sparking & hi-side of cut-out. 15 kva HE style tran | 05185 Moore, Adrian | CM O&E SUP | Arcing & sparking & hi-side of cut- | 32.7038 | -117.1262 | 2022 | Non Conductor
OMD0000929173-01 | Dmg/Wlite-Flash or Sparks | 2022-07-29 22:14 | 2022-07-29 20:37 | 2022-07-29 20:49 | N | N | N | N | N | Arching/Charring | 12 kV | 208 V | Other/Undetermined | sec. connections touched and melted at weatherhead | Connector Damaged | 361-64 | Transformer | 100 | P839055 | 361 |  | 12558 Simmons, Anthony | CM O&E SUP | connections touched together at wea | 32.7543 | -117.1456 | 2022 | Non Conductor
OMD0000929336-01 | Branch Outage | 2022-07-31 04:49 | 2022-07-31 02:24 | 2022-07-31 02:49 | N | N | N | N | N | Arching/Charring | 12 kV |  | Contact by Object | mylar balloons | Vandalism | F86341 | Fuse | 200A |  | 1434 |  | 69761 Simmons, Taylor | CM O&E SUP |  | 32.7052 | -117.1168 | 2022 | Balloon
OMD0000930897-01 | Transformer Outage | 2022-08-06 18:18 | 2022-08-06 17:03 | 2022-08-06 17:24 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Connector Damaged | 1297-159 | Transformer | 150 | p231981 | 1297 |  | 05185 Moore, Adrian | CM O&E SUP | replaced burnt connection @ the pol | 32.7547 | -117.1292 | 2022 | Non Conductor
OMD0000932236-01 | Emer-Specl Req - Fire/Police/Govt | 2022-08-12 17:33 | 2022-08-12 14:38 | 2022-08-12 14:51 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Weather Damaged Device | 412-72 | Transformer | 15 | P678298 | 412 | 900a DISCONN DAM @ SWI 412-15 CAUSING SMALL FIRE @ THE BOTTO | 03936 Llano, Brian | CM O&E SUP | 900a DISCONN DAM @ SWI 412-15 CAUSI | 32.7963 | -116.9198 | 2022 | Non Conductor
OMD0000938714-01 | Emer-Specl Req - Fire/Police/Govt | 2022-09-04 10:31 | 2022-09-04 09:15 | 2022-09-04 09:15 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Service Deenergized For Safety | 374-191 | Transformer | 50 | P830665 | 374 | Sec Service and underarm fiber burned/melting at arrival. Li | 11071 Rivera, Steven | CM O&E SUP |  | 32.6933 | -117.1791 | 2022 | Non Conductor
OMD0000938881-01 | Emer-Specl Req - Fire/Police/Govt | 2022-09-04 18:27 | 2022-09-04 17:55 | 2022-09-04 17:55 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Weather Damaged Transformer | 377-75 | Transformer | 50 | P1956471519 | 377 | XFRMR Overloaded and Detonated | 11071 Rivera, Steven | CM O&E SUP |  | 32.7004 | -117.1759 | 2022 | Non Conductor
OMD0000941070-01 | Emer-Specl Req - Fire/Police/Govt | 2022-09-09 13:39 | 2022-09-09 12:00 | 2022-09-09 12:00 | N | N | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | WHEN ARRIVED ON SCENE, JUMPER WAS BLOWN IN THE CLEAR. UNDETERMINED WHAT CAUSED JUMPER TO COME UNDONE, MAYBE OLD CONNECTIONS AND BEING CLOSE TO THE BAY/WATER | Weather Damaged Connector | 131-256 | Three Phase Transformer | 500 | P1944272429 | 131 | MAKE REPAIRS TO OVER THE ARM JUMPERS | 10056 Gomez, Miguel | CM O&E SUP | CREW TO REPLACE OVER THE ARM JUMPER | 32.6968 | -117.1467 | 2022 | Non Conductor
OMD0000943705-01 | Dmg/Wlite-Flash or Sparks | 2022-09-20 08:01 | 2022-09-20 07:03 | 2022-09-20 07:15 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Heat Device/Overload | 159-539 | Transformer | 50 | P283282 | 159 | DAMAGED MIDDLE PHASE HOOKSTICK SWITCH, 159-4 P283282. REPLAC | 21969 Delgadillo, Joseph | CM O&E SUP | DAMAGED SWITCH 159-4 CREW TO REPLAC | 32.5772 | -117.0969 | 2022 | Non Conductor
OMD0000947632-01 | Dmg/Wlite-Flash or Sparks | 2022-10-04 20:43 | 2022-10-04 20:43 | 2022-10-04 20:43 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Connector Damaged | 155-636 | Transformer | 37.5 | P281302 | 155 | damage disconnect | 12558 Simmons, Anthony | CM O&E SUP | failed disconnect. crew to replace | 32.6199 | -117.0363 | 2022 | Non Conductor
OMD0000953463-01 | No Lights in Part-Just Started | 2022-10-30 09:10 | 2022-10-30 04:53 | 2022-10-30 06:40 | N | Y | N | N | N | Arching/Charring |  | 120 V | Electric Facility | Open wire PS leg burned itself in the clear. | Connector Damaged | 154-358 | Transformer | 25 | P183009J | 154 |  | 02819 Patrick, Damion | CM O&E SUP | Partial lights due to secondary ope | 32.6192 | -117.0572 | 2022 | Non Conductor
OMD0000955332-03 | Circuit Outage | 2022-11-07 12:50 | 2022-11-06 23:51 | 2022-11-07 00:14 | Y | Y | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | Bad connection | Connector Damaged | B-12KV-104 | Circuit |  | M2021671631 | 104 | Bad 600a Tee's in M2021671631...full set. | 02819 Patrick, Damion | CM O&E SUP | Bad 600a Tee's in M2021671631. | 32.7188 | -117.1732 | 2022 | UG Connector
OMD0000956109-01 | Dmg/Wlite-Other | 2022-11-08 23:02 | 2022-11-08 21:59 | 2022-11-08 21:59 | Y | N | N | N | N |  | 12 kV |  | Electric Facility |  | Equipment Contacted Conductor | 158-126 | Transformer | 25 | P88606 | 158 | jumper burned through a clamptop insulator allowing jumper t | 02819 Patrick, Damion | CM O&E SUP | jumper burned through a clamptop in | 32.5874 | -117.1082 | 2022 | Non Conductor
OMD0000957218-01 | Emer-Specl Req - Fire/Police/Govt | 2022-11-12 17:58 | 2022-11-12 17:01 | 2022-11-12 17:18 | N | N | N | N | N | Arching/Charring |  | 120 V | Other/Undetermined | FIRE DO TO HOMELESS | Vandalism | FM2-189 | Transformer | 75 |  | FM2 | FIRE CAUSED BY HOMLESS MELTED THE FACE OF METER # 5838229, N | 09424 Garcia, Raul | CM O&E SUP | FIRE CAUSED BY HOMELESS MELTED THE | 32.7568 | -117.09 | 2022 | Other All
OMD0000957227-01 | Dmg Dim/Nolite - Flash or Sparks | 2022-11-13 00:14 | 2022-11-12 20:19 | 2022-11-12 20:35 | N | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility | HOT NEUTRAL AT HOUSE NOB MAKING CONTACT WITH HOUSE | Conductor Damaged | LA1-52 | Transformer | 50 | p86375 | LA1 |  | 09424 Garcia, Raul | CM O&E SUP | C/O TWO DAMAGED SERVICE'S, AT POLE | 32.6756 | -117.0733 | 2022 | Other Contact
OMD0000959571-03 | Branch Outage | 2022-11-22 09:22 | 2022-11-22 06:20 | 2022-11-22 07:02 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Connector Damaged | 75-32R | Recloser |  | M121371 | 75 |  | 02766 Mcghen, Ryan | CM O&E SUP | Faulted Tee parts M121371 | 32.7219 | -116.8809 | 2022 | UG Connector
OMD0000959676-01 | Flickering Lights-Just Started | 2022-11-22 13:03 | 2022-11-22 11:36 | 2022-11-22 11:47 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Transformer Problem | 431-94 | Transformer | 50 | P737989 | 431 | damaged bushing on transformer. replace station | 12558 Simmons, Anthony | CM O&E SUP | transformer bushing damaged. replac | 32.7522 | -117.0961 | 2022 | Non Conductor
OMD0000960154-01 | Branch Outage | 2022-11-23 13:05 | 2022-11-23 11:24 | 2022-11-23 11:44 | N | N | N | N | N | Arching/Charring | 12 kV | 208 V | Contact by Object |  | Vandalism | F87691 | Fuse | 150A |  | 169 | CAR CONTACT WITH 3 PHASE UG STATION, PRIMARY AND SEC. WIRE W | 09424 Garcia, Raul | CM O&E SUP | CAR VS TRANSFORMER | 32.7501 | -117.0701 | 2022 | UG Vehicle
OMD0000960822-01 | Emer-Specl Req - Fire/Police/Govt | 2022-11-28 06:41 | 2022-11-28 06:11 | 2022-11-28 06:11 | Y | N | N | N | N | Arching/Charring | 4 kV |  | Electric Facility |  | Wire Down | MNR3-88 | Transformer | 50 | P733456 | MNR3 | PRIMARYNEUTRAL WIRE DOWN R/O 4156 E CANTERBURY DR. | 21969 Delgadillo, Joseph | CM O&E SUP | PRIMARYNEUTRAL WIRE DOWN R/O 4156 E | 32.7669 | -117.1058 | 2022 | Non Conductor
OMD0000961045-01 | Dmg/Wlite-Flash or Sparks | 2022-11-28 20:31 | 2022-11-28 18:34 | 2022-11-28 18:53 | N | N | N | N | Y | Arching/Charring | 12 kV |  | Other/Undetermined | Possible corrosion & over-load on the hi-side of a hook-stick | Heat Device/Overload | 43-488 | Transformer | 100 |  | 43 | Hook stick switch on the street side is currently glowing on | 05185 Moore, Adrian | CM O&E SUP | swi.43-463 on P193995 has a hook-st | 32.6744 | -117.1081 | 2022 | Non Conductor
OMD0000963330-01 | Emer-Specl Req - Fire/Police/Govt | 2022-12-07 21:10 | 2022-12-07 20:05 | 2022-12-07 20:19 | N | N | N | N | Y | Arching/Charring | 12 kV |  | Electric Facility |  | Connector Damaged | 43-1039 | Transformer | 65 | p1868773657 | 43 | Will need to follow-up & replace 'h' bodies & copper stir-up | 05185 Moore, Adrian | CM O&E SUP | Will need to follow-up & replace 'h | 32.6774 | -117.1069 | 2022 | Non Conductor
OMD0000656891-01 | Dmg/Wlite-Explosion | 2019-09-01 09:13 | 2019-09-01 08:03 | 2019-09-01 09:03 | Y | N | N | N | N | Actual Ignition | 12 kV |  | Other/Undetermined | A CAPACITOR CAUGHT FIRE THERE WAS A LITTLE FIRE INSIDE THE INCLOSER THAT I PUT OUT WITH MY FIRE EXTINGGUISHER | Device Deenergized for Safety | 903-44 | Three Phase Transformer | 3000 | D210303 | 903 |  | 01826 Fowley, Jack | NC O&E SUP | A CAPACITOR CAUGHT FIRE THERE WAS A | 33.2125 | -117.3036 | 2019 | UG transformer
OMD0000966998-01 | No Lights in Part-Just Started | 2022-12-21 20:42 | 2022-12-21 20:40 | 2022-12-21 20:40 | N | N | N | N | N | Arching/Charring |  | 120 V | Other/Undetermined | secondary molds | Connector Damaged | 431-422 | Transformer | 25 |  | 431 |  | 69761 Simmons, Taylor | CM O&E SUP | changed molds | 32.7532 | -117.0927 | 2022 | Non Conductor
OMD0000967003-01 | Emer-Specl Req - Fire/Police/Govt | 2022-12-21 20:24 | 2022-12-21 19:45 | 2022-12-21 19:56 | Y | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility | INSULINK CONNECTOR FAILED | Service Down | HP1-124 | Transformer | 25 | P184273 | HP1 | DAMAGED SPLICE CONNECTION,, SERVICE DOWN. 70' #6 SSCC @ 66, | 21969 Delgadillo, Joseph | CM O&E SUP | DAMAGED SPLICE CONNECTION CAUSED FI | 32.6271 | -117.0588 | 2022 | Non Conductor
OMD0000967163-01 | Circuit Outage | 2022-12-22 13:20 | 2022-12-22 11:14 | 2022-12-22 13:11 | N | N | N | N | N | Arching/Charring | 12 kV |  | Contact by Object |  | Foreign Object Contacted Device | F-12KV-364 | Circuit |  |  | 364 | 364-49R damaged due to a squirrel commiting suicide and will | 69761 Simmons, Taylor | CM O&E SUP |  |  |  | 2022 | Animal
OMD0000967581-01 | Transformer Outage | 2022-12-25 12:24 | 2022-12-25 10:40 | 2022-12-25 11:01 | N | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility |  | Transformer Problem | HL1-8 | Transformer | 25 | P739915 | HL1 | HL1-8 transformer is bad. made temporary jumpers off of bank | 12558 Simmons, Anthony | CM O&E SUP | sent follow up made temp jumpers to | 32.7044 | -117.1113 | 2022 | Non Conductor
OMD0000968687-01 | Branch Outage | 2023-01-01 00:08 | 2022-12-31 22:28 | 2022-12-31 23:41 | N | N | N | N | N | Arching/Charring | 12 kV |  | Contact by Object |  | Conductor Damaged | F85960 | Fuse | 150A |  | 1434 | wire down and broken cutout | 69761 Simmons, Taylor | CM O&E SUP |  | 32.7118 | -117.1071 | 2023 | Other Contact
OMD0000973574-01 | Dim Lite-Cause Unknown Just Start | 2023-01-16 18:37 | 2023-01-16 18:23 | 2023-01-16 18:23 | N | N | N | N | N | Arching/Charring |  | 120 V | Other/Undetermined | ALUMINUM SERVICE WIRE DOWN WHEN ARRIVED ON SCEEN. SECONDARY SERVICE WIRE. | Weather Damaged Conductor | 42-220 | Transformer | 37.5 |  | 42 | SERVICE OVERHEAD CHANGE OUT INSTALL #4 CU SERVICE WIRE | 10056 Gomez, Miguel | CM O&E SUP | SECONDARY SERVICE CHANGE OUT | 32.6856 | -117.0717 | 2023 | Conductor
OMD0000977348-01 |  | 2023-01-27 23:49 | 2023-01-27 23:05 | 2023-01-27 23:29 | N | N | N | N | N |  |  | 240 V | Other/Undetermined | homeless camp fire | Fire Damaged Pole | 130-118 | Transformer | 150 |  | 130 | Homeless fire next to p232658. Pole is a newer steel pole th | 05185 Moore, Adrian | CM O&E SUP | Homeless fire next to p232658. Pole | 32.6875 | -117.1174 | 2023 | Other All
OMD0000977350-01 | Emer-Specl Req - Fire/Police/Govt | 2023-01-28 01:27 | 2023-01-28 00:37 | 2023-01-28 00:53 | N | N | N | N | N |  |  | 120 V | Other/Undetermined | Electrical exterior light fixture | Customer Problem | 334-187 | Three Phase Transformer | 150 |  | 334 |  | 05185 Moore, Adrian | CM O&E SUP | Structure fire caused by electrical | 32.5592 | -117.0598 | 2023 | Other All
OMD0000979371-01 | Branch Outage | 2023-02-07 10:30 | 2023-02-07 08:23 | 2023-02-07 08:49 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Heat Device/Overload | 524-50R | Recloser |  | P773630 | 524 |  | 02766 Mcghen, Ryan | CM O&E SUP | 15a CMU fuse blew and did not open. |  |  | 2023 | Non Conductor
OMD0000979385-01 | Branch Outage | 2023-02-07 10:32 | 2023-02-07 10:30 | 2023-02-07 10:30 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Heat Device/Overload | F2479738 | Fuse | 15A | P773630 | 524 |  | 02766 Mcghen, Ryan | CM O&E SUP | 15a CMU fuse blew and did not open. |  |  | 2023 | Non Conductor
OMD0000980578-01 | Emer-Specl Req - Fire/Police/Govt | 2023-02-11 15:22 | 2023-02-11 14:53 | 2023-02-11 15:06 | N | N | N | N | Y |  | 12 kV |  | Other/Undetermined | trash & wood | Fire Damaged Pole | 130-122 | Transformer | 25 | p232658 | 130 |  | 05185 Moore, Adrian | CM O&E SUP | Another homeless encampment fire on | 32.6868 | -117.1164 | 2023 | Other All
OMD0000980705-01 | Emer-Specl Req - Fire/Police/Govt | 2023-02-12 20:44 | 2023-02-12 20:11 | 2023-02-12 20:41 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Weather Damaged Service | 412-394 | Transformer | 50 | P670272 | 412 |  | 02766 Mcghen, Ryan | CM O&E SUP | Need to replace service that feeds | 32.7845 | -116.922 | 2023 | Non Conductor
OMD0000980707-01 | Dmg Dim/Nolite-WireDown Pole to H | 2023-02-12 20:49 | 2023-02-12 20:44 | 2023-02-12 20:44 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Weather Damaged Service | 412-394 | Transformer | 50 | P670272 | 412 | Need service crew to replace 100' #2ssca. Customer out of po | 02766 Mcghen, Ryan | CM O&E SUP | Need service crew to replace 100' # | 32.7845 | -116.922 | 2023 | Non Conductor
OMD0000980710-01 | Dmg Dim/Nolite - Flash or Sparks | 2023-02-12 21:31 | 2023-02-12 20:49 | 2023-02-12 21:16 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Weather Damaged Service | 74-112 | Transformer | 50 | P270072J | 74 |  | 02766 Mcghen, Ryan | CM O&E SUP | Need service crew to replace servic | 32.7841 | -116.9626 | 2023 | Non Conductor
OMD0000980711-01 | Dmg Dim/Nolite - Explosion | 2023-02-12 21:52 | 2023-02-12 21:31 | 2023-02-12 21:31 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Weather Damaged Service | 548-199 | Transformer | 50 | P270072J | 548 | Need service crew to replace OH service. | 02766 Mcghen, Ryan | CM O&E SUP | Need service crew to replace OH ser | 32.784 | -116.9628 | 2023 | Non Conductor
OMD0000981269-01 | Branch Outage | 2023-02-15 01:05 | 2023-02-14 22:52 | 2023-02-15 00:47 | N | N | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | WIRE ARCING ON THE PAVEMENT | Conductor Damaged | F4920 | Fuse | 20A | P254493 | 159 | 60' OF 6/3 CU BURNED OPEN 3 CUTOUTS AND DOORS | 39759 Hollins, Daryl | CM O&E SUP | CREW TO REPLACE 60' OF 6/3 CU WIRE | 32.5795 | -117.1296 | 2023 | Conductor
OMD0000981283-01 | Branch Outage | 2023-02-15 08:31 | 2023-02-15 00:31 | 2023-02-15 01:11 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Weather Damaged UG Cable | F87540 | Fuse | 100A | M2138476612 | 759 |  | 02766 Mcghen, Ryan | CM O&E SUP | Bad run of 3 phase cable between M2 | 32.7511 | -117.0131 | 2023 | UG UG cable
OMD0000982795-01 | Dmg Dim/Nolite-WireDown Pole to H | 2023-02-21 20:56 | 2023-02-21 20:01 | 2023-02-21 20:22 | Y | N | N | N | N | Arching/Charring |  | 240 V | Contact by Object | Charred up a small section of the customers vinyl fence | Weather Damaged Service | 320-151 | Transformer | 25 | p732056 | 320 | Burnt down service from pole to house | 05185 Moore, Adrian | CM O&E SUP | Burnt down #6 Str. service. Need ne | 32.694 | -117.0386 | 2023 | Conductor
OMD0000983916-01 | No Lights - Cause Unknown | 2023-02-23 10:08 | 2023-02-23 09:54 | 2023-02-23 09:56 | N | N | N | N | Y | Arching/Charring |  | 240 V | Other/Undetermined | broken insulation on service wire | Weather Damaged Service | 142-180 | Transformer | 50 |  | 142 | #6 sscc burned opened to the ground | 00108 Alvarez, Marco | CM O&E SUP |  | 32.7925 | -117.1409 | 2023 | Non Conductor
OMD0000983971-01 | Dmg/Wlite-Pole Burning | 2023-02-23 12:45 | 2023-02-23 12:40 | 2023-02-23 12:40 | N | N | N | N | N | Arching/Charring | 12 kV |  | Contact by Object |  | Foreign Object Contact Conductor | 536-176 | Three Phase Transformer | 300 |  | 536 |  | 39759 Hollins, Daryl | CM O&E SUP | BIRD'S NEST CAUSED RESTORER TO TRIP | 32.5814 | -116.9195 | 2023 | Other Contact
OMD0000983993-02 | Branch Outage | 2023-02-23 13:02 | 2023-02-23 11:47 | 2023-02-23 12:00 | N | N | N | N | N | Arching/Charring | 12 kV | 240 V | Electric Facility | over arm jumper on x arm | Fire Damaged Pole | F103322 | Fuse | 30A | p63016 | 65 |  | 00108 Alvarez, Marco | CM O&E SUP | crew to work on pole that caught fi | 32.864 | -117.2382 | 2023 | Non Conductor
OMD0000984128-01 | Dmg Dim/Nolite-Wire Down P to P | 2023-02-23 17:19 | 2023-02-23 16:01 | 2023-02-23 16:10 | N | N | N | N | N | Arching/Charring |  | 240 V | Other/Undetermined | sec service burned midspan | Foreign Object Contact Services | 480-502 | Transformer | 50 |  | 480 | replace 100' #6 sscc | 00108 Alvarez, Marco | CM O&E SUP |  | 32.7323 | -117.251 | 2023 | Conductor
OMD0000984153-01 | Non Outage Order | 2023-02-23 15:26 | 2023-02-23 15:14 | 2023-02-23 15:14 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Weather Damaged Pole | 65-67 | Transformer | 50 | p63016 | 65 | fire on pole burned 10' x arms and other stuff | 00108 Alvarez, Marco | CM O&E SUP | crew to replace what is neeeded on | 32.8645 | -117.2382 | 2023 | Non Conductor
OMD0000984179-01 | Branch Outage | 2023-02-23 19:31 | 2023-02-23 19:30 | 2023-02-23 19:30 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Weather Damaged Device | F128732 | Fuse | 30A | P379667 | 380 |  | 02766 Mcghen, Ryan | CM O&E SUP | 100a kearney fuse holder burned in | 32.7962 | -117.0712 | 2023 | Non Conductor
OMD0000984183-01 | Branch Outage | 2023-02-23 19:30 | 2023-02-23 17:41 | 2023-02-23 17:49 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Weather Damaged Device | F128732 | Fuse | 30A | P379667 | 380 |  | 02766 Mcghen, Ryan | CM O&E SUP | 100a kearney fuse holder burned in | 32.7962 | -117.0712 | 2023 | Non Conductor
OMD0000984220-01 | No Lights - Cause Unknown | 2023-02-24 01:30 | 2023-02-24 00:47 | 2023-02-24 01:03 | N | N | N | N | Y | Arching/Charring |  | 240 V | Other/Undetermined | rain | Weather Damaged Service | 278-382 | Transformer | 37.5 |  | 278 | 45' #6 sscc burned open | 00108 Alvarez, Marco | CM O&E SUP | crew to replace 50 #6 sscc | 32.8412 | -117.1772 | 2023 | Non Conductor
OMD0000986427-01 | Dmg Dim/Nolite - Flash or Sparks | 2023-03-01 16:50 | 2023-03-01 15:06 | 2023-03-01 15:27 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Equipment Contacted Conductor | 412-84 | Transformer | 50 | P478817J | 412 | Arm guy is coming in contact with primary conductor and RTS | 02766 Mcghen, Ryan | CM O&E SUP | Arm guy is coming in contact with p | 32.792 | -116.9203 | 2023 | Conductor
OMD0000986507-01 | Emer-Specl Req - Fire/Police/Govt | 2023-03-01 18:19 | 2023-03-01 18:10 | 2023-03-01 18:10 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | SRCING MARKS ON THE ASPHALT | Weather Damaged Conductor | 256-88 | Transformer | 75 |  | 256 |  | 39759 Hollins, Daryl | CM O&E SUP | PRIMARY LINE WAS DOWN FROM HIGH WIN | 32.6294 | -117.0934 | 2023 | Conductor
OMD0000987667-01 | Emer-Specl Req - Fire/Police/Govt | 2023-03-04 08:13 | 2023-03-04 08:08 | 2023-03-04 08:08 | N | N | N | N | N | Arching/Charring |  | 120 V | Other/Undetermined | customer extension cord | Customer Problem | 323-183 | Transformer | 25 |  | 323 |  | 05185 Moore, Adrian | CM O&E SUP | Extension cord feeding electric fir | 32.7128 | -117.0739 | 2023 | Other All
OMD0000991735-01 | Emer-Specl Req - Fire/Police/Govt | 2023-03-20 00:32 | 2023-03-19 21:15 | 2023-03-19 21:32 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Weather Damaged Device | 130-145 | Transformer | 75 | p232680 | 130 |  | 05185 Moore, Adrian | CM O&E SUP | Swith 130-4 was defective. OPened & | 32.6929 | -117.1255 | 2023 | Non Conductor
OMD0000996058-01 | Transformer Outage | 2023-04-03 07:35 | 2023-04-03 06:43 | 2023-04-03 06:50 | N | N | N | N | N | Arching/Charring | 4 kV |  | Contact by Object | crow | Foreign Object Contact Conductor | MT1-167 | Transformer | 75 | P232512 | MT1 |  | 02766 Mcghen, Ryan | CM O&E SUP | Bird contact high side of MT1-167. | 32.734 | -117.173 | 2023 | Animal
OMD0000996308-01 | Emer-Specl Req - Fire/Police/Govt | 2023-04-03 18:27 | 2023-04-03 16:12 | 2023-04-03 16:26 | Y | N | N | N | N |  |  | 208 V | Electric Facility |  | Weather Damaged Service | 1448-151 | Three Phase Transformer | 300 | 3377 Carmel Mountain Rd | 1448 | burn run of 500mcm 4 wire ug sec service 35' may have affect | 00108 Alvarez, Marco | CM O&E SUP | crew to replace 3 runs of 500 mcm a | 32.917 | -117.2351 | 2023 | UG transformer
OMD0000996577-02 | Circuit Outage | 2023-04-04 11:17 | 2023-04-04 09:00 | 2023-04-04 10:37 | N | N | N | N | N | Arching/Charring | 12 kV |  | Contact by Object | dig in | Foreign Object Contact UG Cable | VN-12KV-1482 | Circuit |  | M20629720009 | 1482 |  | 02766 Mcghen, Ryan | CM O&E SUP | Dig in between M20629720009 and |  |  | 2023 | UG Other Contact
OMD0000997975-02 | Circuit Outage | 2023-04-10 00:39 | 2023-04-09 19:30 | 2023-04-09 20:02 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Connector Damaged | CR-12KV-81 | Circuit |  | H110744 | 81 | Damaged components in H110744. | 02819 Patrick, Damion | CM O&E SUP | Damaged components in H110744. | 32.6943 | -117.1701 | 2023 | UG Connector
OMD0000998421-01 | Dmg/Wlite-Other | 2023-04-11 13:12 | 2023-04-11 11:09 | 2023-04-11 11:33 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Equipment Contacted Device | 57-479 | Transformer | 50 | house | 57 |  | 00108 Alvarez, Marco | CM O&E SUP | electrican needs to work on panel | 32.8036 | -117.2529 | 2023 | Non Conductor
OMD0001003555-01 | Dmg Dim/Nolite - Other | 2023-05-01 14:11 | 2023-05-01 12:46 | 2023-05-01 12:58 | N | N | N | N | N | Arching/Charring |  | 120 V | Other/Undetermined | Loose connection | Weather Damaged Connector | 545-113 | Transformer | 50 |  | 545 |  | 00108 Alvarez, Marco | CM O&E SUP |  | 32.7739 | -117.2504 | 2023 | Non Conductor
OMD0001003993-01 | Dmg Dim/Nolite-WireDown Pole to H | 2023-05-03 12:36 | 2023-05-03 11:41 | 2023-05-03 12:18 | N | N | N | N | N | Arching/Charring |  | 240 V | Vegetation Contact |  | Tree Damaged Service | 548-205 | Transformer | 75 |  | 548 | Tree crew w0rking at 1499 Sierra Cir cut limb that took out | 02766 Mcghen, Ryan | CM O&E SUP | Tree crew working at 1499 Sierra Ci | 32.7777 | -116.9703 | 2023 | Other All
OMD0001004610-03 | Substation Outage | 2023-05-06 18:20 | 2023-05-06 18:20 | 2023-05-06 18:20 | N | N | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | Sparks coming off of UG cable at W123430. | Damaged Underground Cable | IB-12KV-BT | Substation |  | W123430 | IMPE | Bad UG cable from W123430 to D1474374300 (290' #2 PID). | 02819 Patrick, Damion | CM O&E SUP | Bad UG cable from W123430 to D14743 | 32.569 | -117.0842 | 2023 | UG UG Cable
OMD0001004836-01 | Emer-Specl Req - Fire/Police/Govt | 2023-05-06 20:40 | 2023-05-06 20:14 | 2023-05-06 20:14 | N | N | N | N | Y | Arching/Charring | 12 kV | 240 V | Other/Undetermined | Homeless started fire at 4332 Georgia St., SD. | Service Deenergized For Safety | 361-277 | Transformer | 65 | P837587 | 361 | Damaged 25' 1/0 3phase sec. service...D/E sta. 361-277 for s | 02819 Patrick, Damion | CM O&E SUP | Structure fire at 4332 Georgia St., | 32.7558 | -117.1455 | 2023 | Other All
OMD0001005907-01 | Emer-Antenna/Metal Object on Wire | 2023-05-11 17:03 | 2023-05-11 15:29 | 2023-05-11 15:50 | N | N | N | N | Y | Arching/Charring | 12 kV |  | Other/Undetermined | dirt in the cutouts in the air | Weather Damaged Device | 52-124 | Transformer | 25 | p2116969261 | 52 | arching cutouts | 00108 Alvarez, Marco | CM O&E SUP |  | 32.7441 | -117.2509 | 2023 | Non Conductor
OMD0001007388-01 | Dmg/Wlite-Flash or Sparks | 2023-05-16 18:40 | 2023-05-16 17:56 | 2023-05-16 18:13 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Foreign Object Contact Services | 546-136 | Transformer | 50 | p837119 | 546 | ps leg touching guywire holding sec service to 3657 Promonto | 00108 Alvarez, Marco | CM O&E SUP | crew to fix guy wire from touching | 32.7869 | -117.2364 | 2023 | Other Contact
OMD0001009991-01 | Dmg Dim/Nolite - Explosion | 2023-05-29 17:13 | 2023-05-29 15:55 | 2023-05-29 16:12 | Y | Y | N | N | N |  | 12 kV | 480 V | Electric Facility | Shorted out test-blocks below meter socket. | Service Deenergized For Safety | 152-831 | Transformer | 50 | p832522 | 152 |  | 05185 Moore, Adrian | CM O&E SUP | Cust.panel caught fire damaging for | 32.5911 | -117.0534 | 2023 | Non Conductor
OMD0001012335-03 | Circuit Outage | 2023-06-08 13:28 | 2023-06-08 07:57 | 2023-06-08 10:34 | Y | Y | N | Y | N | Arching/Charring | 12 kV |  | Electric Facility |  | Connector Damaged | BD-12KV-1160 | Circuit |  | h116651 | 1160 | Fault in H116651...cable components. | 02819 Patrick, Damion | CM O&E SUP | 12KV cir. 1160, bad 600a Tee compon | 32.5603 | -116.9571 | 2023 | UG Connector
OMD0001013079-01 | Emer-Specl Req - Fire/Police/Govt | 2023-06-11 11:00 | 2023-06-11 10:11 | 2023-06-11 10:36 | N | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility | stranded service failed in rain | Weather Damaged Conductor | 326-79 | Transformer | 37.5 | P677432 | 326 | Bad service | 69761 Simmons, Taylor | CM O&E SUP |  | 32.7062 | -117.0503 | 2023 | Conductor
OMD0001013535-01 | Emer-Specl Req - Fire/Police/Govt | 2023-06-13 04:36 | 2023-06-13 04:23 | 2023-06-13 04:23 | N | N | N | N | Y |  | 12 kV | 120 V | Other/Undetermined | washing tub was being used as a fire pit | Vandalism | 162-700 | Transformer | 25 |  | 162 | structure fire at 3260 main st, both meters were pulled and | C2213 Johnson, Justin | CM O&E SUP | structure fire at 3260 main st, bot | 32.741 | -117.032 | 2023 | Other All
OMD0001013781-02 | Branch Outage | 2023-06-14 06:28 | 2023-06-13 22:05 | 2023-06-13 22:23 | Y | Y | Y | Y | N | Arching/Charring | 12 kV |  | Electric Facility |  | Connector Damaged | 325-1229F | Switch Position |  | H105714 | 325 |  | 02819 Patrick, Damion | CM O&E SUP | 12KV cir. 325, bad 600a connections | 32.6885 | -117.0478 | 2023 | UG Connector
OMD0001016764-01 | Branch Outage | 2023-06-27 10:29 | 2023-06-27 06:27 | 2023-06-27 07:07 | Y | Y | Y | Y | N |  | 12 kV |  | Electric Facility | POSS BIRD | Foreign Object in Transformer | F129156 | Fuse | 15A | STA 381-287 | 381 | BIRD DAM STA's 381-287 P479622 | 03936 Llano, Brian | CM O&E SUP | BIRD DAM STA's 381-287 P479622 | 32.8028 | -117.0887 | 2023 | Animal
OMD0001016944-01 | Dmg/Wlite-Other | 2023-06-27 19:22 | 2023-06-27 16:40 | 2023-06-27 17:02 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Connector Damaged | 323-60 | Transformer | 75 | P377217 | 323 |  | 02766 Mcghen, Ryan | CM O&E SUP | Improperly installed secondary conn | 32.708 | -117.0789 | 2023 | Non Conductor
OMD0001024382-01 | Dmg/Wlite-Wire Down Pole to Pole | 2023-07-26 20:16 | 2023-07-26 20:12 | 2023-07-26 20:12 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Weather Damaged Service | 364-256 | Transformer | 50 | P736132 | 364 |  | 02766 Mcghen, Ryan | CM O&E SUP | OH service needs to be changed out. | 32.7487 | -117.1162 | 2023 | Conductor
OMD0001024383-01 | Transformer Outage | 2023-07-26 20:12 | 2023-07-26 19:46 | 2023-07-26 19:52 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Weather Damaged Conductor | 364-256 | Transformer | 50 | P736132 | 364 | Bad OH service | 02766 Mcghen, Ryan | CM O&E SUP | Need sercice crew to replace OH ser | 32.7487 | -117.1162 | 2023 | Conductor
OMD0001025605-01 | Non Outage Order | 2023-08-01 00:59 | 2023-07-31 21:49 | 2023-07-31 22:12 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | top side of swi 702-1 | Heat Device/Overload | 702-1 | Switch |  | P379490 | 702 | glowing top of 900 amp disconnect | 00108 Alvarez, Marco | CM O&E SUP |  | 32.7838 | -117.1358 | 2023 | Non Conductor
OMD0000660366-01 | Transformer Outage | 2019-09-13 09:14 | 2019-09-13 07:57 | 2019-09-13 08:26 | N | N | N | N | N | Arching/Charring | 12 kV | 208 V | Electric Facility | lugs melted off on service, all contained within xfmr enclosure | Connector Damaged | 715-120 | Transformer | 75 | D134564 | 715 | 1 lug on 500 service and 1 lug on 1/0 service are melted, an | 03033 Laws, Jeffery | RA O&E SUP | Crew dispatched to c/o xfmr & repai | 32.8092 | -117.1168 | 2019 | UG Transformer
OMD0001027848-01 | Emer-Specl Req - Fire/Police/Govt | 2023-08-10 04:54 | 2023-08-09 22:15 | 2023-08-09 23:47 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Weather Damaged UG Cable | 357-205 | Transformer | 50 | P777548 | 357 | burned cable at pothead 120' #2 cu | 00108 Alvarez, Marco | CM O&E SUP |  | 32.8194 | -116.7967 | 2023 | OH to UG
OMD0001029144-01 | Dmg Dim/Nolite - Other | 2023-08-15 10:02 | 2023-08-15 08:44 | 2023-08-15 09:01 | N | N | N | N | N | Arching/Charring |  | 240 V | Other/Undetermined | load from business | Weather Damaged Conductor | 71-145 | Transformer | 87.5 |  | 71 | power leg burnt up again from pole to pole 2nd time | 00108 Alvarez, Marco | CM O&E SUP |  | 32.8132 | -116.9683 | 2023 | Other All
OMD0001030814-01 | Emer-Specl Req - Fire/Police/Govt | 2023-08-20 15:44 | 2023-08-20 15:09 | 2023-08-20 15:19 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Weather Damaged Service | 1434-237 | Transformer | 25 | P170019J | 1434 | Bad OH Service. Customer out of power. | 02766 Mcghen, Ryan | CM O&E SUP | Need to replace OH service. | 32.7138 | -117.1103 | 2023 | Conductor
OMD0001030828-01 | Emer-Specl Req - Fire/Police/Govt | 2023-08-20 16:24 | 2023-08-20 16:02 | 2023-08-20 16:02 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Weather Damaged Service | 431-150 | Transformer | 50 | P739527 | 431 | Bad OH Service. Customer out of power. | 02766 Mcghen, Ryan | CM O&E SUP | Need to replace OH service. | 32.7545 | -117.0853 | 2023 | Conductor
OMD0001030910-01 | No Lights in Part-Just Started | 2023-08-20 17:20 | 2023-08-20 16:41 | 2023-08-20 16:47 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Weather Damaged Service | RD4-68 | Transformer | 25 | P176127 | RD4 | Bad OH service. Customer out of power. | 02766 Mcghen, Ryan | CM O&E SUP | Need to replace OH service. | 32.7572 | -117.0675 | 2023 | Conductor
OMD0001030934-01 | No Lights in Part-Just Started | 2023-08-20 17:58 | 2023-08-20 17:21 | 2023-08-20 17:29 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Weather Damaged Service | 168-311 | Transformer | 50 | P670614 | 168 | Bad OH service. Customer out of power. | 02766 Mcghen, Ryan | CM O&E SUP | Need to replace OH service. | 32.7676 | -117.0783 | 2023 | Conductor
OMD0001031147-01 | Dmg Dim/Nolite-WireDown Pole to H | 2023-08-20 22:12 | 2023-08-20 21:27 | 2023-08-20 21:40 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Weather Damaged Service | EO3-100 | Transformer | 25 | P475155 | EO3 | Bad OH service. Customer out of power. | 02766 Mcghen, Ryan | CM O&E SUP |  | 32.7106 | -117.0668 | 2023 | Conductor
OMD0001035822-01 | Dmg/Wlite-Flash or Sparks | 2023-09-04 22:54 | 2023-09-04 20:06 | 2023-09-04 20:21 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Device Deenergized for Safety | 732-150 | Transformer | 25 | P571642 | 732 | burned up disconnects | 00108 Alvarez, Marco | CM O&E SUP | crew to replace swi 732-13, 3- 900a | 32.7285 | -116.9876 | 2023 | Non Conductor
OMD0001035833-01 | Dmg Dim/Nolite - Flash or Sparks | 2023-09-05 00:17 | 2023-09-04 23:08 | 2023-09-04 23:22 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Weather Damaged Connector | 524-707 | Transformer | 25 | p172663 | 524 | replace sec on sta pole 524-707 P172663 and sec connections | 00108 Alvarez, Marco | CM O&E SUP | need to rplc sec connections at sta | 32.7353 | -116.8892 | 2023 | Non Conductor
OMD0001036195-01 | Emer-Specl Req - Fire/Police/Govt | 2023-09-06 12:47 | 2023-09-06 08:12 | 2023-09-06 08:50 | Y | N | N | Y | N |  | 12 kV |  | Other/Undetermined | TREE FELL ACROSS PRIMARY LINE. LINE BURNED OPEN | Tree Damaged Conductor | 152-962 | Transformer | 50 | P89783 TO P89784 | 152 | 500' OF 6/3 WIRE BURNED OPEN | 39759 Hollins, Daryl | CM O&E SUP | CREW IS ON SCENE RESTORING SERVICE | 32.6034 | -117.0439 | 2023 | Veg
OMD0001040311-01 | Emer-Specl Req - Fire/Police/Govt | 2023-09-20 21:06 | 2023-09-20 20:00 | 2023-09-20 20:12 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Connector Damaged | 703-251 | Transformer | 50 | z234862 | 703 | Damaged 'H' body connection on south side/line side lead on | 05185 Moore, Adrian | CM O&E SUP | replace damaged 'h' body connection | 32.7672 | -117.132 | 2023 | Non Conductor
OMD0001040497-01 | Emer-Specl Req - Fire/Police/Govt | 2023-09-21 16:15 | 2023-09-21 13:36 | 2023-09-21 13:40 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Foreign Object Contact Conductor | 41-78 | Transformer | 50 | p835152 | 41 |  | 05185 Moore, Adrian | CM O&E SUP | D.Patrick submitted DAF | 32.6661 | -117.0992 | 2023 | Other Contact
OMD0001041762-01 | No Lights - Outage Not Restored | 2023-09-27 00:08 | 2023-09-26 22:56 | 2023-09-26 23:07 | Y | Y | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Connector Damaged | 154-144 | Transformer | 70 | p183357 | 154 |  | 05185 Moore, Adrian | CM O&E SUP | Burnt open connection on p183357 on | 32.6174 | -117.0571 | 2023 | Non Conductor
OMD0001042592-01 | Emer-Specl Req - Fire/Police/Govt | 2023-09-29 13:47 | 2023-09-29 13:47 | 2023-09-29 13:47 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Service Deenergized For Safety | 1482-177 | Transformer | 50 | P137018 | 1482 |  | 02766 Mcghen, Ryan | CM O&E SUP | Service burned down across street. | 32.7302 | -117.1677 | 2023 | Other All
OMD0001043832-01 | Circuit Outage | 2023-10-05 15:05 | 2023-10-05 07:02 | 2023-10-05 07:29 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Connector Damaged | GHL-12KV-1437 | Circuit |  | M121046 | 1437 | Damaged T componets in M121046 | 02766 Mcghen, Ryan | CM O&E SUP | Damaged T componets in M121046. | 32.7131 | -117.131 | 2023 | UG Connector
OMD0001052325-01 | Emer-Specl Req - Fire/Police/Govt | 2023-11-09 18:00 | 2023-11-09 16:23 | 2023-11-09 16:34 | Y | N | N | N | N | Arching/Charring |  | 240 V | Other/Undetermined | electrical space heater | Service Deenergized For Safety | 366-79 | Transformer | 50 |  | 366 | Damged service caused by electrcial fire. Creating DAF in or | 05185 Moore, Adrian | CM O&E SUP | Structure fire caused by electric | 32.7507 | -117.115 | 2023 | Other All
OMD0001053986-01 | Emer-Specl Req - Fire/Police/Govt | 2023-11-15 23:41 | 2023-11-15 22:57 | 2023-11-15 23:17 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Weather Damaged Service | 326-67 | Transformer | 50 | P672786 | 326 | Bad OH service | 02766 Mcghen, Ryan | CM O&E SUP | Need service crew to replace 75' #6 | 32.707 | -117.0439 | 2023 | Conductor
OMD0001062071-01 | Dmg/Wlite-Xfmr/Grn Box Flash/Sprk | 2023-12-19 20:14 | 2023-12-19 19:05 | 2023-12-19 19:19 | N | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility |  | Connector Damaged | MT1-108 | Transformer | 75 | P235235 | MT1 |  | 69761 Simmons, Taylor | CM O&E SUP | replaced connection at pole | 32.7408 | -117.179 | 2023 | Non Conductor
OMD0001063041-01 | Transformer Outage | 2023-12-24 15:57 | 2023-12-24 14:04 | 2023-12-24 14:13 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | blown fuse | Heat Device/Overload | 366-70 | Transformer | 75 | P2143773433 | 366 |  | 69761 Simmons, Taylor | CM O&E SUP |  | 32.7526 | -117.115 | 2023 | Non Conductor
OMD0001064095-01 | Emer-Specl Req - Fire/Police/Govt | 2023-12-30 14:55 | 2023-12-30 13:52 | 2023-12-30 14:32 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Weather Damaged Service | 326-64 | Transformer | 25 | P672777j | 326 |  | 02766 Mcghen, Ryan | CM O&E SUP | Mulch | 32.7054 | -117.0436 | 2023 | Undetermined
OMD0001064102-01 | Transformer Outage | 2023-12-30 15:01 | 2023-12-30 14:56 | 2023-12-30 14:56 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Weather Damaged Service | 326-64 | Transformer | 25 | P672777j | 326 | Damaged copper stranded service. | 02766 Mcghen, Ryan | CM O&E SUP | Wire came down in some mulch at bas | 32.7054 | -117.0436 | 2023 | Conductor
OMD0001066892-01 | Dmg/Wlite-Flash or Sparks | 2024-01-11 03:22 | 2024-01-11 01:52 | 2024-01-11 02:09 | N | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility | WEATHERED STREET LIGHT SERVICE WIRE, PS, GOT INTO NEUTRAL. RAIN CONDITIONS | Weather Damaged Conductor | 325-225 | Transformer | 25 | P186188 | 325 | SERVICE CREW TO MAKE REPAIRS TO STREET LIGHT AND NEUTRAL WIR | 10056 Gomez, Miguel | CM O&E SUP | STREET LIGHT WIRE GOT INTO NEUTRAL. | 32.6726 | -117.0536 | 2024 | Other Contact
OMD0001067576-01 | Circuit Outage | 2024-01-13 05:34 | 2024-01-13 05:21 | 2024-01-13 05:21 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Device Damaged | LJ-12KV-570 | Circuit |  | P191716 | 570 | Damaged Load Break gang switch 570-49 on P191716. | 02766 Mcghen, Ryan | CM O&E SUP | Need Line crew to replace a damaged | 32.846 | -117.2724 | 2024 | Non Conductor
OMD0001069277-01 | Emer-Specl Req - Fire/Police/Govt | 2024-01-19 00:41 | 2024-01-18 23:19 | 2024-01-18 23:43 | N | N | N | N | Y | Arching/Charring | 12 kV | 240 V | Other/Undetermined | Dumpster fire | Fire Damaged Pole | 257-541 | Transformer | 50 | P80558 | 257 | Damaged ground wire. | 02819 Patrick, Damion | CM O&E SUP | Dumpster fire, removed meter & D/E | 32.641 | -117.0793 | 2024 | Other All
OMD0000662455-01 | Flickering Lights-Just Started | 2019-09-21 16:18 | 2019-09-21 14:51 | 2019-09-21 15:21 | N | N | N | N | N | Arching/Charring |  | 120 V | Other/Undetermined | SEC UG CONNECTION IN TRANSFORMER...ON FLAG AND LUG... | Connector Damaged | 985-361 | Transformer | 75 | D108445 | 985 | CHECKED PANEL AND 3312...ALL CHECKED GOOD... DID FIND A BAD | 00462 Macias, Damian | OC O&E SUP | CHECKED PANEL AND 3312...ALL CHECKE | 33.599 | -117.6401 | 2019 | UG Connector
OMD0001075071-01 | Emer-Specl Req - Fire/Police/Govt | 2024-02-07 01:04 | 2024-02-06 20:09 | 2024-02-06 20:09 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Weather Damaged Device | 240-638 | Transformer | 25 | p777860 | 240 | burned x arm 12kv arm needs to be changed out | 00108 Alvarez, Marco | CM O&E SUP | crew to c/o 12kv x arm that burned | 32.8737 | -116.9089 | 2024 | Non Conductor
OMD0001075806-01 | Branch Outage | 2024-02-09 08:45 | 2024-02-09 08:45 | 2024-02-09 08:45 | Y | Y | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | bad 600a Tee body. | Connector Damaged | 90-44AE | Switch |  |  | 90 | Bad 600a Tee body. | 02819 Patrick, Damion | CM O&E SUP | Bad 600a Tee body at H130848. | 32.7542 | -117.1412 | 2024 | UG Connector
OMD0001075825-01 | Emer-Specl Req - Fire/Police/Govt | 2024-02-09 01:00 | 2024-02-09 00:50 | 2024-02-09 00:50 | Y | Y | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | Bad switch | Device Damaged | 90-342 | Transformer | 100 |  | 90 | Compartment #2 of 90-49, at D216998 failed...bad switch. | 02819 Patrick, Damion | CM O&E SUP | Compartment #2 of 90-49, at D216998 | 32.754 | -117.1332 | 2024 | Non Conductor
OMD0001077062-01 | Emer-Specl Req - Fire/Police/Govt | 2024-02-13 09:32 | 2024-02-13 09:32 | 2024-02-13 09:32 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Device Damaged | 128-54 | Transformer | 75 | p1929572510 | 128 | burnt open vertical swicth | 05185 Moore, Adrian | CM O&E SUP | swi. 371-1 needs to be replaced. Al | 32.6936 | -117.1437 | 2024 | Non Conductor
OMD0001083986-01 | Transformer Outage | 2024-03-11 22:46 | 2024-03-11 21:03 | 2024-03-11 21:09 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Connector Damaged | 362-324 | Transformer | 75 | H2216273484 | 362 | damaged molds needs replacemnet | 12558 Simmons, Anthony | CM O&E SUP | molds in hand hole are damaged need | 32.7633 | -117.1098 | 2024 | UG Connector
OMD0001085500-02 | Branch Outage | 2024-03-16 08:31 | 2024-03-16 07:00 | 2024-03-16 07:47 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Heat Device/Overload | F5097 | Fuse | 50A | P830906 | 377 |  | 02766 Mcghen, Ryan | CM O&E SUP | !00a fuse door burnt in half. DAF | 32.6934 | -117.1894 | 2024 | Non Conductor
OMD0001085535-01 | Branch Outage | 2024-03-16 13:29 | 2024-03-16 11:06 | 2024-03-16 12:11 | N | N | N | N | N | Arching/Charring | 12 kV |  | Contact by Object |  | Foreign Object Contact Conductor | 1297-35F | Switch Position |  | P232411 | 1297 | Contractor installing gutters on roof of 6 story building ma | 02766 Mcghen, Ryan | CM O&E SUP | Contractor installing gutters on ro | 32.7546 | -117.1303 | 2024 | Other Contact
OMD0001089220-01 | Emer-Specl Req - Fire/Police/Govt | 2024-03-30 20:01 | 2024-03-30 19:46 | 2024-03-30 19:46 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | GUY WIRE LAYING ON PRIMARY TRACKING TO PHONE | Fire Damaged Pole | 80-597 | Transformer | 25 | P1913273433 | 80 | POLE FIRE | 69761 Simmons, Taylor | CM O&E SUP | POLE FIRE | 32.6902 | -117.1152 | 2024 | Non Conductor
OMD0001089221-03 | Branch Outage | 2024-03-31 02:34 | 2024-03-30 20:41 | 2024-03-30 21:00 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Connector Damaged | 342-521AE | Switch |  | M2153274400 | 342 | BLOWN 600A TEES | 69761 Simmons, Taylor | CM O&E SUP |  | 32.7506 | -117.0796 | 2024 | UG Connector
OMD0001089375-01 | No Lights - Cause Unknown | 2024-03-31 17:07 | 2024-03-31 16:16 | 2024-03-31 16:41 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility | Faulty UG service cable inside conduit | Weather Damaged UG Cable | 532-96 | Transformer | 25 | sh28557 | 532 | 2 ps legs burnt open inside the conduit | 05185 Moore, Adrian | CM O&E SUP | burnt open UG sec. service going f | 32.5793 | -117.0917 | 2024 | UG Switch
OMD0000665535-01 | No Lights - Cause Unknown | 2019-10-03 17:31 | 2019-10-03 16:02 | 2019-10-03 16:18 | N | N | N | N | N | Arching/Charring |  | 208 V | Electric Facility | bad conn | Weather Damaged Connector | 946-163 | Three Phase Transformer | 150 | d2282576993 | 946 | melted lug at sta | 52851 Mackley, Scott | BC O&E SUP |  | 32.7918 | -117.0038 | 2019 | UG Connector
OMD0001094553-01 | Voltage Problem-Low/Just Start | 2024-04-20 15:41 | 2024-04-20 14:22 | 2024-04-20 14:47 | N | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility |  | Connector Damaged | 152-847 | Transformer | 50 | P86289J | 152 |  | 69761 Simmons, Taylor | CM O&E SUP |  | 32.5937 | -117.0461 | 2024 | Non Conductor
OMD0001105826-01 | Momentary Outage | 2024-06-07 23:17 | 2024-06-07 20:45 | 2024-06-07 20:45 | N | N | N | N | N | Arching/Charring | 12 kV |  | Contact by Object |  | Foreign Object Contact Conductor | OY-12KV-155 | Circuit |  | P280081 | 155 | Mylar balloons made contact with primary conductors on P2800 | 02766 Mcghen, Ryan | CM O&E SUP | Mylar balloons made contact with pr | 32.6039 | -117.0328 | 2024 | Balloon
OMD0001108582-01 | Dmg/Wlite-Xfmr/Grn Box Flash/Sprk | 2024-06-19 20:32 | 2024-06-19 18:28 | 2024-06-19 18:37 | N | N | N | N | N | Arching/Charring |  | 240 V | Other/Undetermined | Customer meter socket | Customer Problem | 257-101 | Transformer | 100 |  | 257 |  | 05185 Moore, Adrian | CM O&E SUP | Damaged 3 phase meter & socket. Iso | 32.6387 | -117.0784 | 2024 | Non Conductor
OMD0000666959-01 | Flickering Lights-Just Started | 2019-10-09 17:59 | 2019-10-09 16:44 | 2019-10-09 17:05 | N | N | N | N | Y | Arching/Charring | 12 kV | 120 V | Other/Undetermined | bad/hot/burnt sec connection in transformer, crew enroute to make repairs | Connector Damaged | 831-128 | Transformer | 50 | D2856870254 | 831 | burnt/bad (1) 3/0 sec lug & (1) 1/0 sec lug in station 831-1 | 23170 Doshier, Richard | OC O&E SUP | issued f/u for crew to replace bad/ | 32.9475 | -117.2205 | 2019 | UG Connector
OMD0001109257-01 | Emer-Specl Req - Fire/Police/Govt | 2024-06-23 11:21 | 2024-06-23 06:01 | 2024-06-23 06:22 | N | N | N | N | N | Arching/Charring | 12 kV |  | Contact by Object | CAR HITS POLE. WIRE DOWN | Foreign Object Contacted Device | 256-128 | Transformer | 25 |  | 256 |  | 10056 Gomez, Miguel | CM O&E SUP | CAR HITS POLE. WIRE DOWN ON FREEWAY | 32.6183 | -117.0907 | 2024 | Vehicle
OMD0001112873-01 | Dmg Dim/Nolite - Flash or Sparks | 2024-07-07 23:38 | 2024-07-07 21:33 | 2024-07-07 22:59 | N | N | N | N | Y | Arching/Charring |  | 120 V | Other/Undetermined | ALUMINUM CONNECTION ON OPEN WIRE SECONDARY. BAD CONNECTION CAUSED IT TO BURN ITSELF IN CLEAR | Weather Damaged Connector | 377-174 | Transformer | 50 | P839269 | 377 | OPEN WIRE SEC DOWN. FAILD ALUMINUM CONNECTION TAPPED TO OPEN | 10056 Gomez, Miguel | CM O&E SUP | FAILED CONNECTION AT OPEN WIRE SECO | 32.7008 | -117.1775 | 2024 | Conductor
OMD0001114112-02 | Branch Outage | 2024-07-12 17:33 | 2024-07-12 08:46 | 2024-07-12 10:57 | N | N | N | N | N | Arching/Charring | 4 kV |  | Electric Facility |  | Weather Damaged UG Cable | BS1-7 | Switch Position |  | M2017072168 | BS1 |  | 02766 Mcghen, Ryan | CM O&E SUP | Damaged lead cable in M2017072168. | 32.7167 | -117.1539 | 2024 | UG UG Cable
OMD0001114809-02 | Branch Outage | 2024-07-15 16:27 | 2024-07-15 14:21 | 2024-07-15 15:23 | N | N | N | N | N | Arching/Charring | 12 kV |  | Contact by Object |  | Foreign Object Contact Conductor | F2010041 | Fuse | 75A |  | 552 | 6/3 copper wire needs to be replaced next to p273255 | 00108 Alvarez, Marco | CM O&E SUP | crew to replace wire sections that | 32.8023 | -116.9759 | 2024 | Other Contact
OMD0001117461-01 | Emer-Specl Req - Fire/Police/Govt | 2024-07-25 10:18 | 2024-07-25 08:41 | 2024-07-25 09:09 | N | N | N | N | N | Arching/Charring |  | 240 V | Other/Undetermined | FAILED CONNECTION AT SERVICE. SERVICE FEEDING COMMERCIAL CUSTOMER HAS TOO MUCH LOAD, FOLLOW UP EMAIL WILL BE SENT OUT. REPLACED CONNECTION. | Weather Damaged Connector | MT1-106 | Transformer | 100 |  | MT1 |  | 10056 Gomez, Miguel | CM O&E SUP | MADE REPAIRS TO ALUMINUM CONNECTION | 32.7403 | -117.1783 | 2024 | Non Conductor
OMD0001117969-01 | Emer-Specl Req - Fire/Police/Govt | 2024-07-26 18:44 | 2024-07-26 16:05 | 2024-07-26 16:27 | N | N | N | Y | N |  |  | 240 V | Electric Facility | TREE BRANCH CAME DOWN ON SERVICE. RIPPED SERVICE FROM HOUSE AND WELDED SERVICE TOGETHER. 2 FIRE SPOTS, NEXT TO PANEL AND IN FRONT YARD. | Tree Damaged Service | 532-280 | Transformer | 25 | P81497 | 532 | TREE BRANCH RIPPED SRVICE FROM HOUSE. CREW TO REPLACE SERVIC | 10056 Gomez, Miguel | CM O&E SUP | NEED CREW TO REPLACE SERVICE WIRE F | 32.572 | -117.0755 | 2024 | Veg
OMD0001118488-01 | Flickering Lights-Just Started | 2024-07-29 12:03 | 2024-07-29 10:03 | 2024-07-29 10:42 | N | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility |  | Connector Damaged | 1297-187 | Transformer | 50 | P2185172991 | 1297 |  | 12558 Simmons, Anthony | CM O&E SUP | connector was damaged and partially | 32.7639 | -117.1294 | 2024 | Non Conductor
OMD0001118907-01 | Transformer Outage | 2024-07-30 17:21 | 2024-07-30 14:39 | 2024-07-30 14:39 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Connector Damaged | 363-631 | Transformer | 175 | P195397 | 363 | damaged secondary connections on pole. change out underarm f | 12558 Simmons, Anthony | CM O&E SUP | . The secondary connections failed | 32.7473 | -117.1296 | 2024 | Non Conductor
OMD0001120715-01 | Transformer Outage | 2024-08-06 19:59 | 2024-08-06 18:20 | 2024-08-06 18:46 | N | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility |  | Conductor Damaged | WA5-146 | Transformer | 25 | P371978 | WA5 | melted fiber needs replacement | 12558 Simmons, Anthony | CM O&E SUP | sec. fiber melted needs replacement | 32.7377 | -117.0783 | 2024 | Conductor
OMD0001126782-01 | Emer-Specl Req - Fire/Police/Govt | 2024-08-28 05:03 | 2024-08-28 03:50 | 2024-08-28 04:09 | Y | Y | Y | Y | N |  |  |  | Electric Facility |  | Device Deenergized for Safety | 1162-399M | Primary Meter | 12.0 kV | Z83996 | 1162 |  | 05185 Moore, Adrian | CM O&E SUP | TL23042 tripped open & fire @ Z8399 | 32.5881 | -116.9213 | 2024 | Non Conductor
OMD0001128626-01 | Emer-Specl Req - Fire/Police/Govt | 2024-09-04 19:08 | 2024-09-04 18:43 | 2024-09-04 18:56 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Weather Damaged Conductor | 365-71 | Transformer | 75 | p232359 | 365 | Need to replace 4/O lo-side THW leads w/ 500 THW Insulation | 05185 Moore, Adrian | CM O&E SUP | Need to replace 4/O lo-side THW lea | 32.7499 | -117.132 | 2024 | Conductor
OMD0001130417-01 | Branch Outage | 2024-09-09 09:45 | 2024-09-09 07:54 | 2024-09-09 08:58 | N | N | N | N | N | Arching/Charring |  | 240 V | Other/Undetermined | overload- melting of insolation on sec wires | Transformer Problem | F156830 | Fuse | 15A |  | 548 | bad sta 548-217 | 00108 Alvarez, Marco | CM O&E SUP |  | 32.7787 | -116.964 | 2024 | Non Conductor
OMD0001136000-01 |  | 2024-09-25 13:58 | 2024-09-25 13:49 | 2024-09-25 13:49 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility | SECONDARY MOLD | Weather Damaged Connector | 363-626 |  |  | SH355466 | 363 | DAMAGED MOLDS SH355466 FED FROM STA 363-626. OVERLOADED, BOT | 21969 Delgadillo, Joseph | CM O&E SUP | CREW TO PEPLACE MOLDS SH355466 | 32.7415 | -117.1299 | 2024 | UG Connector
OMD0001138073-01 | Dmg/Wlite-Flash or Sparks | 2024-10-03 11:07 | 2024-10-03 09:41 | 2024-10-03 09:59 | N | Y | N | N | N | Arching/Charring | 12 kV | 240 V | Other/Undetermined | possible connection/load | Device Damaged | 159-174 | Transformer | 50 | P88860 | 159 | The X1 bushing on the secondary is a lil charred. All custo | 02819 Patrick, Damion | CM O&E SUP | A customer called in about this XFM | 32.5799 | -117.1288 | 2024 | Non Conductor
OMD0001142171-02 | Substation Outage | 2024-10-19 23:30 | 2024-10-19 23:30 | 2024-10-19 23:30 | N | N | N | N | N | Arching/Charring |  |  | Electric Facility |  | Weather Damaged Device | B-69KV-BK 31 | Substation |  | bank 30 sta B | STAT |  | 00108 Alvarez, Marco | CM O&E SUP |  |  |  | 2024 | Non Conductor
OMD0001143104-01 | Emer-Specl Req - Fire/Police/Govt | 2024-10-23 15:04 | 2024-10-23 12:52 | 2024-10-23 13:03 | N | N | N | Y | N |  | 12 kV |  | Vegetation Contact |  | Conductor Damaged | 168-422 | Transformer | 25 | p771099 | 168 | Tree limb made contact w/ 12kv phase causing limb to catch f | 05185 Moore, Adrian | CM O&E SUP | Tree limb made contact w/ 12kv phas | 32.7755 | -117.0873 | 2024 | Veg
OMD0001143886-01 | Emer-Specl Req - Fire/Police/Govt | 2024-10-28 08:14 | 2024-10-28 04:31 | 2024-10-28 05:01 | N | N | N | N | N | Arching/Charring |  | 120 V | Contact by Object |  | Vandalism | 431-194 | Transformer | 125 | P930274 | 431 | fire caused wires to be severly annealed. needs replacement | 12558 Simmons, Anthony | CM O&E SUP | vandalism. homeless was attempting | 32.7498 | -117.095 | 2024 | Other Contact
OMD0001145548-01 | Emer-Specl Req - Fire/Police/Govt | 2024-11-02 23:27 | 2024-11-02 22:55 | 2024-11-02 23:08 | Y | N | N | N | N | Arching/Charring |  | 240 V | Other/Undetermined | RAIN/WEATHER POSSIBLE CAUSE | Weather Damaged Wire | 940-314 | Transformer | 50 |  | 940 | REPLACE SERVICE. MIDSPAN TO HOUSE | 10056 Gomez, Miguel | CM O&E SUP | SERVICE CREW TO REPLACE SECONDARY S | 32.6437 | -116.988 | 2024 | Conductor
OMD0001145549-01 | Emer-Specl Req - Fire/Police/Govt | 2024-11-02 22:26 | 2024-11-02 22:01 | 2024-11-02 22:07 | Y | Y | N | N | N | Arching/Charring |  | 240 V | Other/Undetermined | OLD SERVICE, RAIN/WEATHER MAY HAVE BEEN THE CAUSE | Weather Damaged Conductor | 719-113 | Transformer | 50 |  | 719 | REPLACE SERVICE, POLE TO HOUSE | 10056 Gomez, Miguel | CM O&E SUP | SERVICE CREW TO REPLACE OH SERVICE | 32.619 | -117.077 | 2024 | Conductor
OMD0001145660-01 | Transformer Outage | 2024-11-03 08:23 | 2024-11-03 08:11 | 2024-11-03 08:11 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Weather Damaged Service | SR4-70 | Transformer | 25 | P378229 | SR4 | Bad OH service. Truck accessible. Also need to replace #2 a | 02766 Mcghen, Ryan | CM O&E SUP | Copper stranded service came down o | 32.7449 | -117.0757 | 2024 | Conductor
OMD0001145662-01 | No Lights - Cause Unknown | 2024-11-03 10:25 | 2024-11-03 10:22 | 2024-11-03 10:22 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Weather Damaged Service | 70-362 | Transformer | 75 | P166602 | 70 |  | 02766 Mcghen, Ryan | CM O&E SUP | Need service crew to replace OH ser | 32.7017 | -117.1358 | 2024 | Conductor
OMD0001145669-01 | Dmg/Wlite-Flash or Sparks | 2024-11-03 10:22 | 2024-11-03 09:44 | 2024-11-03 10:03 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Weather Damaged Conductor | 70-362 | Transformer | 75 | P166602 | 70 | Need service crew to replace cu stranded service. | 02766 Mcghen, Ryan | CM O&E SUP | Need service crew to replace cu str | 32.7017 | -117.1358 | 2024 | Conductor
OMD0001150961-01 | Transformer Outage | 2024-11-24 04:00 | 2024-11-24 02:59 | 2024-11-24 03:20 | Y | N | N | N | N | Arching/Charring |  | 240 V | Other/Undetermined | Bad service | Weather Damaged Service | 365-136 | Transformer | 50 | P206869 | 365 | Bad sec. sertvice burned open. 65' stranded ssc cu | 02819 Patrick, Damion | CM O&E SUP | Bad sec. sertvice burned open. | 32.7414 | -117.1363 | 2024 | Conductor
OMD0001157834-01 | Transformer Outage | 2024-12-21 08:20 | 2024-12-21 06:41 | 2024-12-21 07:00 | N | N | N | N | N | Arching/Charring |  | 120 V | Vegetation Contact |  | Weather Damaged Conductor | 1438-154 | Transformer | 50 | P7292255 | 1438 | SERVICE C/O. INSTALL #4 SOL CU SERVICE. POLE: 1928 33RD ST ( | 10056 Gomez, Miguel | CM O&E SUP | CREW TO CHANGE OUT OLD SERVICE. DAF | 32.7265 | -117.1247 | 2024 | Veg
OMD0001158041-01 | Dmg/Wlite-Pole Burning | 2024-12-22 19:47 | 2024-12-22 18:35 | 2024-12-22 18:50 | N | N | N | N | N | Arching/Charring |  | 120 V | Other/Undetermined | SECODNARY SERVICE WIRE DOWN WHEN ARRIVED. COULD NOT DETERMINE WHAT CAUSED IT TO COME DOWN | Service Down | 255-506 | Transformer | 25 | P189865 | 255 | CREW TO REPLACE SERVICE TO: 262 CORALWOOD CT. CHULA VISTA S | 10056 Gomez, Miguel | CM O&E SUP | SECONDARY SERVICE WIRE CAME DOWN. S | 32.6462 | -117.067 | 2024 | Undetermined
OMD0001158891-05 | Circuit Outage | 2024-12-28 16:20 | 2024-12-28 13:43 | 2024-12-28 14:03 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Connector Damaged | VN-12KV-1481 | Circuit |  | M100417 | 1481 | Bad 600a Tee's in M100417...(Full Set). | 02819 Patrick, Damion | CM O&E SUP | Bad 600a Tee's in M100417...(Full S | 32.7241 | -117.1695 | 2024 | UG Connector
OMD0001161055-01 | Emer-Specl Req - Fire/Police/Govt | 2025-01-08 08:01 | 2025-01-08 06:25 | 2025-01-08 06:45 | N | N | N | N | N | Arching/Charring | 4 kV |  | Other/Undetermined | c/o burned in half | Weather Damaged Connector | LA1-106 | Transformer | 50 | p178096 | LA1 |  | 00108 Alvarez, Marco | CM O&E SUP |  | 32.6929 | -117.0753 | 2025 | Non Conductor
OMD0001162436-01 | Transformer Outage | 2025-01-12 13:51 | 2025-01-12 12:15 | 2025-01-12 12:31 | N | N | N | N | N | Arching/Charring |  | 240 V | Other/Undetermined | SEC CONNECTIONS ON POLE | Weather Damaged Connector | MF1-52 | Transformer | 75 | P738124 | MF1 | BAD SEC CONNECTIONS ALUM TO COPPER ON P738124 AND C/O SEC SE | 00108 Alvarez, Marco | CM O&E SUP | CREW TO C/O SEC CONNECTIONS ON P738 | 32.7638 | -117.116 | 2025 | Non Conductor
OMD0001164253-03 | Circuit Outage | 2025-01-19 10:37 | 2025-01-19 06:48 | 2025-01-19 06:48 | Y | Y | N | N | N |  | 12 kV |  | Electric Facility |  | Connector Damaged | PD-12KV-323 | Circuit |  | H1968874986 | 323 | Damaged 600a Tee's (1000KCMIL) in H1968874986. | 02819 Patrick, Damion | CM O&E SUP | Damaged 600a Tee's (1000KCMIL) in H | 32.7051 | -117.0639 | 2025 | UG Connector
OMD0001166911-01 | Transformer Outage | 2025-01-26 13:14 | 2025-01-26 13:08 | 2025-01-26 13:08 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Weather Damaged Service | BRM1-27 | Transformer | 25 | P733944J | BRM1 | Need service crew to replace bad copper stranded service. | 02766 Mcghen, Ryan | CM O&E SUP | Need OH service crew to replace bad | 32.7526 | -117.1199 | 2025 | Conductor
OMD0001167022-01 | Emer-Specl Req - Fire/Police/Govt | 2025-01-26 12:55 | 2025-01-26 12:27 | 2025-01-26 12:40 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Weather Damaged Service | BRM1-31 | Transformer | 37.5 | P736728 | BRM1 |  | 02766 Mcghen, Ryan | CM O&E SUP | Neighbors service burned down. Sen | 32.7507 | -117.1187 | 2025 | Other All
OMD0001167025-01 | Dmg Dim/Nolite-WireDown Pole to H | 2025-01-26 14:15 | 2025-01-26 14:10 | 2025-01-26 14:10 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Service Down | 168-313 | Transformer | 50 | P670620 | 168 | Bad OH copper stranded service | 02766 Mcghen, Ryan | CM O&E SUP | Need service crew to replace servic | 32.7677 | -117.0757 | 2025 | Conductor
OMD0001167295-01 | Dmg Dim/Nolite-WireDown Pole to H | 2025-01-27 10:29 | 2025-01-27 08:43 | 2025-01-27 08:57 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Weather Damaged Service | MNR3-61 | Transformer | 25 | house | MNR3 | #6 sscc burnt up and came down to ground | 00108 Alvarez, Marco | CM O&E SUP |  | 32.7668 | -117.1096 | 2025 | Conductor
OMD0001171490-01 | Dmg Dim/Nolite-Pole Burning | 2025-02-08 21:04 | 2025-02-08 20:47 | 2025-02-08 20:47 | N | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility |  | Device Damaged | 591-435 | Transformer | 50 | p282552 | 591 |  | 12558 Simmons, Anthony | CM O&E SUP | customers panel is damaged. damaged | 32.6804 | -117.021 | 2025 | Non Conductor
OMD0000645629-01 | Emer-Specl Req - Fire/Police/Gov | 2019-07-20 04:38 | 2019-07-20 04:12 | 2019-07-20 04:12 | N | N | N | N | Y | Arching/Charring | 12 kV | 240 V | Vegetation Contact |  | Fire Damaged Wire | 94-334 | Transformer | 50 |  | 94 | Need to have RTS from P574064 to P574065 changed due to fire | 01202 Weldy, Kellen | EA O&E SUP |  | 32.7102 | -116.9956 | 2019 | Veg
OMD0000647693-01 | Branch Outage | 2019-07-27 18:26 | 2019-07-27 16:56 | 2019-07-27 17:09 | N | Y | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | weather | Heat Device/Overload | F193584 | Fuse | 150A |  | 242 | bad transformer | 04204 Decresente, Joseph | EA O&E SUP | heat overloaded | 32.8526 | -116.9309 | 2019 | Non Conductor
OMD0000647935-01 | Transformer Outage | 2019-07-29 11:13 | 2019-07-29 09:28 | 2019-07-29 09:38 | N | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility |  | Connector Damaged | 1049-209 | Transformer | 25 | P374172 | 1049 |  | 00460 Stiles, Jake | EA O&E SUP | Cust had low voltage with loadbox. | 32.7255 | -117.0862 | 2019 | Non Conductor
OMD0000649826-01 | Branch Outage | 2019-08-05 09:09 | 2019-08-05 09:02 | 2019-08-05 09:02 | N | N | N | N | N | Arching/Charring | 12 kV |  | Contact by Object | Mylar balloon shorted out transformer | Foreign Object in Transformer | 1434-10AE | Switch |  | P1976073297 | 1434 | Mylar balloons caused sta 1434-160 to flash over. Isolated | 00460 Stiles, Jake | EA O&E SUP | Mylar balloon caused Sta 1434-160 t | 32.7068 | -117.1206 | 2019 | Balloon
OMD0000650070-01 | Emer-Specl Req - Fire/Police/Gov | 2019-08-06 02:13 | 2019-08-06 00:12 | 2019-08-06 00:29 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Device Deenergized for Safety | 74-238 | Three Phase Transformer | 75 | Z371385 | 74 |  | 04204 Decresente, Joseph | EA O&E SUP | cap bank bushing broke/exploded . D | 32.7801 | -116.9573 | 2019 | Non Conductor
OMD0000684936-01 | Branch Outage | 2019-12-10 13:55 | 2019-12-10 11:26 | 2019-12-10 11:26 | N | Y | N | N | N | Arching/Charring | 12 kV |  | Contact by Object | hit by car | Motor Vehicle Contact with Xfmr | F157331 | Fuse | 150A | d2172478165 | 95 | sta 95-602 hit by car | 52851 Mackley, Scott | BC O&E SUP |  | 32.7662 | -116.9598 | 2019 | UG Vehicle
OMD0000651970-01 | Transformer Outage | 2019-08-13 19:59 | 2019-08-13 19:01 | 2019-08-13 19:13 | N | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility | Secondary connection below station | Connector Damaged | 361-113 | Transformer | 50 | P837549 | 361 | Open wire service burnt open @ connection. Being held up by | 00460 Stiles, Jake | EA O&E SUP | Connection from fiber to open wire | 32.7547 | -117.1494 | 2019 | Non Conductor
OMD0000654454-01 | Dmg/Wlite-Other | 2019-08-22 15:34 | 2019-08-22 14:33 | 2019-08-22 14:37 | N | N | N | N | N | Arching/Charring | 4 kV |  | Electric Facility |  | Connector Damaged | 531-58 | Transformer | 150 | Z87342 | 531 | Loadside connection on step down burnt open. Sta 531-SK1. N | 00460 Stiles, Jake | EA O&E SUP | Loadside connection on stepdown 531 | 32.6015 | -117.0926 | 2019 | Non Conductor
OMD0000656413-01 | Substation Outage | 2019-08-30 09:27 | 2019-08-30 09:09 | 2019-08-30 09:09 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Device Damaged | BD-12KV-BK 31 | Substation |  | Cap Bank D fuse disconnect | BORD |  | 00460 Stiles, Jake | EA O&E SUP | Cap bank D fuse disconnect flashed |  |  | 2019 | Non Conductor
OMD0000657125-01 | Emer-Specl Req - Fire/Police/Gov | 2019-09-03 03:18 | 2019-09-03 03:16 | 2019-09-03 03:16 | N | N | N | N | Y | Actual Ignition | 12 kV |  | Other/Undetermined | Homeless started fire at base of pole | Fire Damaged Pole | 135-65M | Primary Meter | 12.0 kV | P2075371575 | 135 |  | 04188 Freymiller, Jeffre | EA O&E SUP | Homeless started fire. Charred pole | 32.7345 | -117.1761 | 2019 | Other All
OMD0000657932-01 | Emer-Specl Req - Fire/Police/Gov | 2019-09-04 18:13 | 2019-09-04 15:53 | 2019-09-04 16:22 | N | N | N | N | N | Arching/Charring | 12 kV | 120 V | Other/Undetermined | lightning storm damaged sta and multiple x-arms | Weather Damaged Transformer | 240-1017 | Transformer | 25 | p139074 and p72693 | 240 | lightning damage x arms at p219333, p139074, p72692 and p139 | 05036 Burrell, Dennis | EA O&E SUP | lightning damage x arms at p219333, | 32.8744 | -116.9069 | 2019 | Non Conductor
OMD0000659991-01 | Emer-Specl Req - Fire/Police/Gov | 2019-09-12 01:14 | 2019-09-11 23:20 | 2019-09-11 23:20 | Y | N | Y | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Device Damaged | 546-131 | Transformer | 167 | P194684 | 546 | Swithc failed causing fire and outage. Switch to be RFS'd an | 04188 Freymiller, Jeffre | EA O&E SUP | Switch burnt up. Crew to jumper out | 32.7896 | -117.2354 | 2019 | Non Conductor
OMD0000661349-01 | Dmg/Wlite-Xfmr/Grn Box Flash/Spr | 2019-09-17 11:43 | 2019-09-17 11:04 | 2019-09-17 11:21 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Open Neutral | 364-543 | Transformer | 50 | P934200 | 364 | Service burnt open in the middle. | 00460 Stiles, Jake | EA O&E SUP | Service is burnt open in the middle | 32.7402 | -117.0939 | 2019 | Non Conductor
OMD0000666065-02 | Branch Outage | 2019-10-06 20:04 | 2019-10-06 15:48 | 2019-10-06 15:48 | N | N | N | N | N | Arching/Charring | 12 kV |  | Vegetation Contact |  | Palm Frond On Conductor | F2251966 | Fuse | 65A |  | 1166 |  | 01202 Weldy, Kellen | EA O&E SUP | Needed crew with tall bucket to rea | 32.777 | -116.7121 | 2019 | Veg
OMD0000668332-02 | Branch Outage | 2019-10-15 17:36 | 2019-10-15 13:33 | 2019-10-15 13:44 | N | N | N | Y | N | Actual Ignition | 4 kV |  | Other/Undetermined | Fire dept thinks it might have been caused by homless in canyon | Fire Damaged Wire | 146-263F | Switch Position |  |  | 146 |  | 00460 Stiles, Jake | EA O&E SUP | De-energized due to fire in area | 32.7636 | -117.0964 | 2019 | Other All
OMD0000670914-01 | Transformer Outage | 2019-10-24 18:39 | 2019-10-24 17:38 | 2019-10-24 17:53 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Fuse Operated in Transformer | 531-58 | Transformer | 150 | P80088 | 531 |  | 00460 Stiles, Jake | EA O&E SUP | Refused sta 531-58. 1 fuse burnt o | 32.6015 | -117.0926 | 2019 | Non Conductor
OMD0000671165-01 | Emer-Specl Req - Fire/Police/Gov | 2019-10-25 14:54 | 2019-10-25 09:52 | 2019-10-25 09:52 | N | N | N | N | Y | Actual Ignition | 12 kV |  | Vegetation Contact |  | Customer Problem | 222-92 | Transformer | 25 |  | 222 |  | 00919 Diaz, Ruben | EA O&E SUP | FIRE | 33.0562 | -116.739 | 2019 | Veg
OMD0000679677-01 | No Lights in Part-Just Started | 2019-11-22 23:02 | 2019-11-22 21:01 | 2019-11-22 21:50 | N | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility |  | Connector Damaged | CMP1-76 | Transformer | 25 | 9245 edgewood dr | CMP1 |  | 07756 Young, Jimmy | EA O&E SUP | bad meter clip need electrician. bo | 32.7601 | -116.9983 | 2019 | Other All
OMD0000680989-01 | Dmg/Wlite-Tree Burning in Wires | 2019-11-27 15:41 | 2019-11-27 14:57 | 2019-11-27 15:18 | N | N | N | N | N | Arching/Charring |  | 120 V | Vegetation Contact | serv running next to palm frayed insilation smoking in rain | Weather Damaged Service | 493-432 | Transformer | 50 | p234876 | 493 | p234876 r/o 1613 fort stockton climber c/o 120' cu serv to 1 | 05036 Burrell, Dennis | EA O&E SUP | p234876 r/o 1613 fort stockton clim | 32.7506 | -117.1785 | 2019 | Veg
OMD0000681085-01 | Transformer Outage | 2019-11-27 21:01 | 2019-11-27 19:59 | 2019-11-27 20:13 | N | N | N | N | N | Arching/Charring | 12 kV | 120 V | Electric Facility | X1 bushing melted | Heat Device/Overload | 83-13 | Transformer | 25 | p678062 | 83 | replace 25 kva he transformer | 07756 Young, Jimmy | EA O&E SUP | 25 kva he transformer X1 bushing me | 32.7927 | -117.0319 | 2019 | Non Conductor
OMD0000682187-01 | Branch Outage | 2019-12-02 06:52 | 2019-12-01 23:42 | 2019-12-02 00:10 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | WIRE DOWN ACROSS HWY 67 | Weather Damaged Conductor | <inline_jumper.12719> |  |  | P771868 | 240 |  | 00919 Diaz, Ruben | EA O&E SUP | WIRE DOWN P771868 TO P771869 & P741 | 32.9068 | -116.9424 | 2019 | Conductor
OMD0000682187-02 | Branch Outage | 2019-12-02 06:41 | 2019-12-02 00:27 | 2019-12-02 00:52 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Conductor Damaged | <inline_jumper.12719> |  |  | P771868 | 240 | wire down 2 spans could change tangent arm at P77868 is roll | 07756 Young, Jimmy | EA O&E SUP | 2 spans 4/3 copper down. one across | 32.9068 | -116.9424 | 2019 | Conductor
OMD0000683479-01 | No Lights - Cause Unknown | 2019-12-05 03:47 | 2019-12-05 02:13 | 2019-12-05 02:24 | N | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility |  | Weather Damaged UG Cable | 412-544 | Transformer | 25 | SH186736 | 412 | Bad molds and servive to 886 terra ln | 07756 Young, Jimmy | EA O&E SUP | Service wire and molds burnt in sec | 32.8061 | -116.9194 | 2019 | UG UG cable
OMD0000689537-01 | No Lights in Part-Just Started | 2019-12-26 15:21 | 2019-12-26 14:18 | 2019-12-26 15:14 | N | N | N | N | N | Arching/Charring |  | 208 V | Electric Facility | Meter base and meter were burnt / melted | Customer Problem | 482-246 | Transformer | 75 | N/A | 482 |  | 03033 Laws, Jeffery | EA O&E SUP | Meter and meter base were damaged / | 32.7235 | -117.2281 | 2019 | Non Conductor
OMD0000693218-01 | Emer-Specl Req - Fire/Police/Gov | 2020-01-10 19:31 | 2020-01-10 17:50 | 2020-01-10 17:50 | N | N | N | N | Y | Actual Ignition |  | 240 V | Contact by Object | car contacted gas meter | Company Shut-Off | 94-653 | Transformer | 25 |  | 94 |  | 07756 Young, Jimmy | EA O&E SUP | cut at pole for saftey | 32.7086 | -116.9873 | 2020 | UG Vehicle
OMD0000694104-01 | Branch Outage | 2020-01-15 10:16 | 2020-01-15 09:01 | 2020-01-15 09:13 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Weather Damaged Device | F2011396 | Fuse | 30A | P170586 | 168 |  | 00460 Stiles, Jake | EA O&E SUP | Fuse holder feeding UG sta burnt op | 32.7586 | -117.0774 | 2020 | Non Conductor
OMD0000695478-01 | Dmg Dim/Nolite-WireDown Pole to | 2020-01-21 13:02 | 2020-01-21 12:16 | 2020-01-21 12:46 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Weather Damaged Service | UP1-51 | Transformer | 15 | P232114 | UP1 | Service down. Its de-energized but still hanging in palm tr | 00460 Stiles, Jake | EA O&E SUP | Service burnt down. Made safe and | 32.7353 | -117.132 | 2020 | Conductor
OMD0000696772-01 | Emer-Specl Req - Fire/Police/Gov | 2020-01-26 18:15 | 2020-01-26 17:29 | 2020-01-26 18:08 | N | N | N | N | N | Arching/Charring |  | 120 V | Other/Undetermined | cigarrette butts stuffed into gap on City of SD street light burned some wiring inside pole. No SDGE equipment affected | Customer Problem | PB1-10 | Transformer | 75 |  | PB1 |  | 03033 Laws, Jeffery | EA O&E SUP | Small fire inside City of SD street | 32.7987 | -117.2433 | 2020 | Other All
OMD0000700458-01 | Dmg Dim/Nolite-WireDown Pole to | 2020-02-10 10:50 | 2020-02-10 10:00 | 2020-02-10 10:45 | N | N | N | N | N | Arching/Charring |  | 120 V | Other/Undetermined | Customer's wires shorted @ weatherhead | Customer Problem | VDN1-67 | Transformer | 50 |  | VDN1 |  | 03033 Laws, Jeffery | EA O&E SUP | Customer's THW @ weatherhead was sh | 32.8154 | -117.2678 | 2020 | Non Conductor
OMD0000705836-01 | Dmg/Wlite-Other | 2020-03-02 10:39 | 2020-03-02 10:30 | 2020-03-02 10:30 | N | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility |  | Weather Damaged Connector | FM3-81 | Transformer | 50 | P931883 | FM3 | Neutral connection burned open and holding up open wire seco | 00460 Stiles, Jake | EA O&E SUP | Burnt open neutral connection @ Sta | 32.7709 | -117.1095 | 2020 | Non Conductor
OMD0000706720-01 | No Lights - Cause Unknown | 2020-03-05 11:58 | 2020-03-05 10:25 | 2020-03-05 10:32 | N | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility |  | Weather Damaged Connector | 431-65 | Transformer | 75 | P930325 | 431 |  | 00460 Stiles, Jake | EA O&E SUP | Replaced bad connection @ pole and | 32.75 | -117.0918 | 2020 | Non Conductor
OMD0000707369-01 | Dmg/Wlite-Flash or Sparks | 2020-03-08 10:08 | 2020-03-08 09:13 | 2020-03-08 09:28 | N | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility |  | Weather Damaged Connector | 152-1000 | Transformer | 37.5 | P189579 | 152 | C/O and upgrade OH Sta 152-1000 and replace station leads. | 00460 Stiles, Jake | EA O&E SUP | Crew to c/o sta 152-1000 and redo s | 32.6081 | -117.0393 | 2020 | Non Conductor
OMD0000717707-01 | Transformer Outage | 2020-04-19 20:04 | 2020-04-19 18:58 | 2020-04-19 19:15 | N | N | N | N | N | Arching/Charring | 4 kV |  | Electric Facility |  | Device Damaged | IB1-91 | Transformer | 25 | P183170 | IB1 | Bad cutout @ Sta IB1-91. Jaw burnt open on cutout | 00460 Stiles, Jake | EA O&E SUP | Bad cutout on sta IB1-91. Need crew | 32.5803 | -117.1132 | 2020 | Non Conductor
OMD0000720361-01 | Dmg Dim/Nolite - Other | 2020-04-29 15:23 | 2020-04-29 14:09 | 2020-04-29 14:25 | N | N | N | N | N | Arching/Charring |  | 120 V | Other/Undetermined | CUSTOMER PANEL | Customer Problem | 723-85 | Transformer | 25 |  | 723 |  | 00460 Stiles, Jake | EA O&E SUP | Cust test block melted and damaged | 32.5841 | -117.0945 | 2020 | Non Conductor
OMD0000685689-01 | Emer-Specl Req - Fire/Police/Gov | 2019-12-12 19:09 | 2019-12-12 15:54 | 2019-12-12 16:24 | Y | N | N | N | N | Actual Ignition | 4 kV |  | Electric Facility | CAR HIT XFMR STA.VS2-128 - PRIMARY CABLE WAS DAMAGED & WAS BURNING - FD HIT IT W/DRY CHEM & WENT OUT - BLEW FUSE AT FUSE CABINET | Motor Vehicle Contact with Xfmr | VS2-90 | Three Phase Transformer | 150 | D3759169922 | VS2 |  | 30566 Garegnani, Dominic | NC O&E SUP | CAR VS STA.VS2-128 - & DAMG PRIMARY | 33.1963 | -117.2344 | 2019 | UG Vehicle
OMD0000685687-01 | Branch Outage | 2019-12-12 19:11 | 2019-12-12 19:09 | 2019-12-12 19:09 | Y | N | N | N | N | Actual Ignition | 4 kV |  | Electric Facility | CAR HIT STA.VS2-128 - CABLE DAMAGED & WAS BURNING - FD PUT IT OUT - DID NOT SPREAD | Motor Vehicle Contact with Xfmr | F588758 | Fuse | 150A | D3759169922 | VS2 |  | 30566 Garegnani, Dominic | NC O&E SUP | CAR VS STA.VS2-128 - & DAMG CABLE - | 33.197 | -117.2339 | 2019 | UG Vehicle
OMD0000728183-01 | Dmg/Wlite-Other | 2020-05-29 11:40 | 2020-05-29 10:37 | 2020-05-29 10:43 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility | Junction box was damaged by unknown 3rd party, connections in box were making contact with metal. | Customer Problem | 56-102 | Transformer | 50 | N/A | 56 | Building / business has multiple addresses and multiple mete | 03033 Laws, Jeffery | EA O&E SUP | Building / business has multiple ad | 32.7981 | -117.2553 | 2020 | Non Conductor
OMD0000733911-01 | Emer-Specl Req - Fire/Police/Gov | 2020-06-21 15:31 | 2020-06-21 12:51 | 2020-06-21 13:50 | Y | N | N | Y | N | Actual Ignition |  | 120 V | Electric Facility | customer owned electrical | Conductor Damaged | PE1-133 | Transformer | 25 | meter#5562790 | PE1 |  | 07756 Young, Jimmy | EA O&E SUP | customer extension cord caused igni | 33.0512 | -116.6319 | 2020 | Other All
OMD0000740525-01 | Emer-Specl Req - Fire/Police/Gov | 2020-07-15 14:12 | 2020-07-15 12:49 | 2020-07-15 12:57 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Service Down | 362-91 | Transformer | 125 | P733289 | 362 | 1/0 4 wire AL service burnt down due to problem in customers | 00460 Stiles, Jake | EA O&E SUP | Service burnt down. Cust needs ele |  |  | 2020 | Other All
OMD0000688400-02 | Branch Outage | 2019-12-21 06:43 | 2019-12-21 03:09 | 2019-12-21 03:49 | Y | Y | N | N | N | Arching/Charring | 12 kV |  | Contact by Object | car contact | Foreign Object Contacted Device | F2301673 | Fuse | 150A | D2630472271 | 762 | car contact hit station | 05351 Henry, Matthew (I) | INACTIVE T | car contact sta 762-253 | 32.8875 | -117.1555 | 2019 | UG Vehicle
OMD0000756878-01 | Branch Outage | 2020-09-05 01:04 | 2020-09-04 23:37 | 2020-09-04 23:37 | Y | N | Y | Y | N | Actual Ignition | 12 kV |  | Contact by Object | Veh hit telco pole, veh started fire, elec wires started 2 other fires. | Moter Vehicle Contact with Pole | 236-10R | Recloser |  | P216155, P713998 | 236 | Vehicle hit telco stub pole causing damage to wire between P | 03033 Laws, Jeffery | EA O&E SUP |  | 33.058 | -116.8714 | 2020 | Vehicle
OMD0000757226-01 | Emer-Specl Req - Fire/Police/Gov | 2020-09-05 17:43 | 2020-09-05 17:22 | 2020-09-05 17:34 | N | N | N | N | Y | Actual Ignition | 12 kV |  | Other/Undetermined | no damge to eqmt fire out on arrival no fire dpt on scene | Undetermined | 244-95 | Three Phase Transformer | 75 | P476199 | 244 |  | 05036 Burrell, Dennis | EA O&E SUP |  | 32.8627 | -116.9217 | 2020 | Other All
OMD0000760415-01 | No Lights - Cause Unknown | 2020-09-12 12:03 | 2020-09-12 11:04 | 2020-09-12 11:21 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Customer Problem | 972-615 | Transformer | 50 | Cust. meter panel | 972 |  | 03033 Laws, Jeffery | EA O&E SUP | Meter base was burned / melted and | 33.0513 | -116.8938 | 2020 | Non Conductor
OMD0000761747-02 | Branch Outage | 2020-09-17 16:43 | 2020-09-17 13:55 | 2020-09-17 14:54 | Y | N | Y | Y | N | Actual Ignition | 12 kV |  | Electric Facility | Contractor's boom contacted and broke 1 wire 1 span, circuit breaker did not trip. | Equipment Contacted Wire | 210-9R | Recloser |  | P215047 | 210 |  | 03033 Laws, Jeffery | EA O&E SUP |  | 33.2787 | -116.6338 | 2020 | Other Contact
OMD0000764238-01 | Emer-Antenna/Metal Object on Wir | 2020-09-27 15:53 | 2020-09-27 14:56 | 2020-09-27 14:56 | N | N | N | N | N | Arching/Charring | 12 kV |  | Contact by Object |  | Foreign Object Contact Conductor | 972-419 | Transformer | 25 |  | 972 |  | 03033 Laws, Jeffery | EA O&E SUP |  | 33.0259 | -116.8828 | 2020 | Other Contact
OMD0000765204-01 | Emer-Specl Req - Fire/Police/Gov | 2020-09-30 13:54 | 2020-09-30 13:07 | 2020-09-30 13:07 | N | Y | Y | Y | N | Actual Ignition |  | 240 V | Other/Undetermined | Fire started underneath service to house. Undetermined is burnt service is cause. | Conductor Damaged | 235-229 | Transformer | 50 | P615292 | 235 | service to 1312 Ramona st burnt up. | 03033 Laws, Jeffery | EA O&E SUP |  | 33.0175 | -116.8796 | 2020 | Other All
OMD0000765360-02 | Branch Outage | 2020-09-30 19:09 | 2020-09-30 17:01 | 2020-09-30 17:01 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | transformer covered in bird droppings, no evidence of actual bird contact | Foreign Object in Transformer | 972-26R | Recloser |  | p718259 | 972 | bad 25kva hj transformer | 07756 Young, Jimmy | EA O&E SUP | replace 25kva HJ transformer | 33.0194 | -116.8578 | 2020 | Other All
OMD0000768888-01 | Emer-Specl Req - Fire/Police/Gov | 2020-10-13 19:02 | 2020-10-13 15:18 | 2020-10-13 15:29 | Y | Y | Y | Y | N | Actual Ignition | 12 kV | 240 V | Electric Facility | XFMR case is energized, and caused the telco cables on pole to become energized, melting insulation and starting fire at base of pole | Transformer Problem | 972-457 | Transformer | 65 | P612927 | 972 | XFMR started small grass fire at base of pole | 03033 Laws, Jeffery | EA O&E SUP |  | 33.0281 | -116.8891 | 2020 | Non Conductor
OMD0000775784-01 | Branch Outage | 2020-11-08 09:10 | 2020-11-08 06:39 | 2020-11-08 08:48 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Weather Damaged Device | F18 | Fuse |  | P478470 | 221 | phase was laying on arm, burnt up x-arms and equipment | 03033 Laws, Jeffery | EA O&E SUP |  | 32.9732 | -116.4138 | 2020 | Non Conductor
OMD0000783434-01 | Emer-Specl Req - Fire/Police/Gov | 2020-12-07 11:19 | 2020-12-07 08:21 | 2020-12-07 09:35 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Device Damaged | 172-137 | Transformer | 25 | P474446 | 172 | Downstream fault caused fuses to operate, but doors did not | 03033 Laws, Jeffery | EA O&E SUP |  | 33.2071 | -116.3315 | 2020 | Non Conductor
OMD0000783454-01 | Emer-Specl Req - Fire/Police/Gov | 2020-12-07 11:30 | 2020-12-07 11:19 | 2020-12-07 11:19 | N | N | N | N | N | Arching/Charring | 12 kV |  | Contact by Object | Crow landed on xfmr & contacted both high voltage leads. | Foreign Object in Transformer | 172-54 | Transformer | 25 |  | 172 | Crow electricuted on xfmr, damaging sta @ burning x-arms, St | 03033 Laws, Jeffery | EA O&E SUP |  | 33.2106 | -116.3393 | 2020 | Animal
OMD0000817734-01 | Emer-Specl Req - Fire/Police/Govt | 2021-04-18 06:42 | 2021-04-18 06:11 | 2021-04-18 06:11 | N | Y | N | N | N | Actual Ignition |  | 240 V | Other/Undetermined | Structure fire melted meter | Customer Problem | 211-18 | Transformer | 25 |  | 211 |  | 03033 Laws, Jeffery | EA O&E SUP | 2 buildings damaged by fire. Remove | 33.2105 | -116.5216 | 2021 | Other All
OMD0000823269-01 | Circuit Outage | 2021-05-12 15:07 | 2021-05-12 14:32 | 2021-05-12 14:42 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | LIGHTNING ARRESTOR FAILED, BURNED UP FIBER GLASS ARM | Device Damaged | LCS-12KV-247 | Circuit |  | P873234 | 247 |  | 00919 Diaz, Ruben | EA O&E SUP | BAD ARRESTOR P873234 |  |  | 2021 | Non Conductor
OMD0000823277-01 | Transformer Outage | 2021-05-12 15:28 | 2021-05-12 15:07 | 2021-05-12 15:07 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | FAILED LIGHTNING ARRESTOR | Device Damaged | 247-457 | Transformer | 25 | P202439 | 247 | FAILED LIGHTNING ARRESTOR BURNED UP FIBERGLASS SWITCH ARM NE | 00919 Diaz, Ruben | EA O&E SUP | BAD ARRESTOR P202439 | 32.8662 | -116.8538 | 2021 | Non Conductor
OMD0000825238-01 | No Lights - Cause Unknown | 2021-05-21 00:18 | 2021-05-20 22:01 | 2021-05-20 23:51 | N | N | N | N | N | Arching/Charring |  | 240 V | Other/Undetermined | burning / melting in customer's meter base | Customer Problem | 972-135 | Transformer | 25 |  | 972 |  | 03033 Laws, Jeffery | EA O&E SUP | Customer's meter base is bad, needs | 33.0456 | -116.9046 | 2021 | Non Conductor
OMD0000830490-01 | Emer-Specl Req - Fire/Police/Govt | 2021-06-13 13:06 | 2021-06-13 12:07 | 2021-06-13 12:07 | Y | Y | Y | Y | N | Actual Ignition | 12 kV |  | Contact by Object | Mylar balloon in primary | Foreign Object Contact Conductor | 236-342 | Transformer | 10 | P107449 | 236 |  | 03033 Laws, Jeffery | EA O&E SUP | Cleared mylar balloons from line, P | 33.0269 | -116.8579 | 2021 | Balloon
OMD0000842101-01 | Emer-Specl Req - Fire/Police/Govt | 2021-07-25 22:00 | 2021-07-25 20:16 | 2021-07-25 20:47 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | insulator tracking caused phase to lay on x-arm and burn only thru arm | Weather Damaged Pole | 161-768 | Transformer | 50 | p572275 | 161 | c/o x-arm p572275 8142 blossom ln 4 P and I sngl arm also c/ | 05036 Burrell, Dennis | EA O&E SUP | c/o x-arm p572275 insulator tracked |  |  | 2021 | Non Conductor
OMD0000842165-01 | Emer-Specl Req - Fire/Police/Govt | 2021-07-26 07:42 | 2021-07-26 05:50 | 2021-07-26 06:02 | Y | Y | N | N | N |  | 12 kV |  | Electric Facility |  | Weather Damaged Pole | 970-865 | Transformer | 25 | P167125 | 970 | Burnt x-arm from brace contacting LA lead | 03033 Laws, Jeffery | EA O&E SUP |  | 33.0216 | -116.8388 | 2021 | Non Conductor
OMD0000842166-01 | Dmg/Wlite-Other | 2021-07-26 08:20 | 2021-07-26 07:44 | 2021-07-26 08:15 | N | N | N | N | N | Arching/Charring |  | 240 V | Vegetation Contact |  | Tree Damaged Service | MOR1-52 | Transformer | 15 |  | MOR1 | Neutral burnt open & PS insulation damaged, please replace s | 03033 Laws, Jeffery | EA O&E SUP |  | 33.0131 | -116.9266 | 2021 | Veg
OMD0000843294-01 | Transformer Outage | 2021-07-29 14:11 | 2021-07-29 13:11 | 2021-07-29 13:12 | Y | N | N | N | N |  | 4 kV |  | Electric Facility |  | Heat Transformer Overload | 355-183 | Transformer | 65 | p677603 | 355 |  | 05036 Burrell, Dennis | EA O&E SUP | refuse sta possible overload fuse d | 32.8368 | -116.7686 | 2021 | Non Conductor
OMD0000693946-01 | Dmg/Wlite-Other | 2020-01-14 11:34 | 2020-01-14 11:29 | 2020-01-14 11:29 | N | N | N | N | Y | Arching/Charring | 12 kV | 120 V | Other/Undetermined | Hot connection in UG xfmr on secondary side | Connector Damaged | 178-396 | Transformer | 50 | D104396 | 178 | C/O hot connections in xfmr | 02704 Martinez, Chris | NC O&E SUP |  | 32.9814 | -117.0575 | 2020 | UG Connector
OMD0000845009-02 | Branch Outage | 2021-08-05 17:58 | 2021-08-05 14:35 | 2021-08-05 15:05 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Connector Damaged | F2251966 | Fuse | 65A | P275730 | 1166 |  | 00460 Stiles, Jake | EA O&E SUP | Wire burnt down from a bad connecti | 32.777 | -116.7121 | 2021 | Non Conductor
OMD0000845357-01 | Emer-Specl Req - Fire/Police/Govt | 2021-08-06 17:33 | 2021-08-06 15:25 | 2021-08-06 16:01 | Y | Y | Y | Y | N |  |  | 240 V | Electric Facility |  | Weather Damaged Service | 524-570 | Transformer | 50 | p278802 | 524 | dmged serv instl 120' 1/0 ssc al | 05036 Burrell, Dennis | EA O&E SUP | dmged serv instl 120' 1/0 ssc al |  |  | 2021 | Conductor
OMD0000849441-01 | Dmg/Wlite-Wire Hanging Low | 2021-08-24 10:44 | 2021-08-24 08:34 | 2021-08-24 08:49 | N | N | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | END OF X-ARM BURNED OFF | Weather Damaged Device | 946-213 | Transformer | 50 |  | 946 | CHG OUT X-ARM, FLOATING PIN & INS. @ P575966 X-ARM TO SOUTH | 00919 Diaz, Ruben | EA O&E SUP | END OF X-ARM BURNED UP @ P575966, & | 32.7946 | -117.0113 | 2021 | Non Conductor
OMD0000850755-01 | Immediate Need - Fire/Police | 2021-08-29 16:50 | 2021-08-29 16:41 | 2021-08-29 16:41 | Y | N | N | N | N |  | 12 kV |  | Other/Undetermined | lightning | Weather Damaged Pole | 972-526 | Transformer | 25 | P615595 | 972 | damaged transformer and pole | 07756 Young, Jimmy | EA O&E SUP | damaged transformer lightning strik | 33.0282 | -116.9006 | 2021 | Non Conductor
OMD0000713891-01 | Branch Outage | 2020-04-05 15:52 | 2020-04-05 13:57 | 2020-04-05 13:57 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | TRUCK & TRAILER HIT XFRM STA. | Motor Vehicle Contact with Xfmr | F588396 | Fuse | 30A | D100516 | 233 | TRAILER HIT STA.233-882 - DMG TO 25HDL & 2W PRIMARY #2AL CAB | 30566 Garegnani, Dominic | NC O&E SUP | TRUCK VS. STA.233-882 - CABLE DAMAG | 33.2532 | -117.2031 | 2020 | UG Vehicle
OMD0000857949-02 | Branch Outage | 2021-09-28 06:47 | 2021-09-28 03:45 | 2021-09-28 04:21 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Weather Damaged UG Cable | F156691 | Fuse | 40A | p572640 | 553 | c/o 250' # 2 cble single wire and 1 cutout and 100a fuse | 05036 Burrell, Dennis | EA O&E SUP | c/o cble | 32.7795 | -116.9533 | 2021 | OH to UG
OMD0000859696-01 | Emer-Specl Req - Fire/Police/Govt | 2021-10-04 23:54 | 2021-10-04 23:16 | 2021-10-04 23:23 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Fire Damaged Pole | 1139-167 | Transformer | 50 | p575629 | 1139 | c/o 8' arm p575629 9429 WHARTON RD | 05036 Burrell, Dennis | EA O&E SUP | c/o 8' arm p575629 | 32.8515 | -116.997 | 2021 | Non Conductor
OMD0000859827-01 | Emer-Specl Req - Fire/Police/Govt | 2021-10-05 05:39 | 2021-10-05 04:58 | 2021-10-05 04:58 | Y | Y | Y | N | N | Arching/Charring | 12 kV |  | Contact by Object | tent brought primary wire down on telco that caught fire | Foreign Object Contacted Wire | 240-948 | Transformer | 25 | P72672 | 240 | c/o 500' 6/3 cu from p74170 to p74171 2 wire 1 span | 05036 Burrell, Dennis | EA O&E SUP | 500' 6/3 cu from p74170 to 74171 | 32.878 | -116.9171 | 2021 | Other Contact
OMD0000862567-01 | Emer-Specl Req - Fire/Police/Govt | 2021-10-15 13:34 | 2021-10-15 12:15 | 2021-10-15 12:15 | N | Y | Y | Y | N |  |  | 240 V | Other/Undetermined | strctr fire burned down serv tripped trfrmr fuse not supspect sdge equip | Weather Damaged Service | DV1-159 | Transformer | 25 | P873258 | DV1 |  | 05036 Burrell, Dennis | EA O&E SUP | strc fire spread to veg burned serv | 32.8049 | -116.8214 | 2021 | Other All
OMD0000864347-01 | Dmg/Wlite-Other | 2021-10-25 04:05 | 2021-10-24 20:15 | 2021-10-24 23:24 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | transformer arrestor andbushing visibly arcing. no ignition of pole or vegitation | Device Damaged | 221-509 | Transformer | 25 | P478334 | 221 | bad transformer | 07756 Young, Jimmy | EA O&E SUP | replace 25 kva hj transformer | 33.0681 | -116.5468 | 2021 | Non Conductor
OMD0000867593-01 | Branch Outage | 2021-11-06 21:11 | 2021-11-06 16:23 | 2021-11-06 16:39 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Foreign Object Contacted Device | 396-699R | Recloser |  | P276777 | 396 | crow got between highside of station 396-69 @ P571554. adres | B0278 Dawson, Garth R | EA O&E SUP | crow got between highside of statio | 32.867 | -116.9405 | 2021 | Non Conductor
OMD0000869191-01 | Emer-Specl Req - Fire/Police/Govt | 2021-11-15 05:36 | 2021-11-15 03:48 | 2021-11-15 04:23 | N | N | N | N | Y |  | 12 kV |  | Other/Undetermined | house fire does not apper to be caused by any sdge equipment, cause currently unknown per cal fire | Company Shut-Off | 237-612 | Transformer | 25 |  | 237 |  | 07756 Young, Jimmy | EA O&E SUP | structure fire disconnected service | 33.0367 | -116.8553 | 2021 | Other All
OMD0000871014-01 | Dmg Dim/Nolite - Flash or Sparks | 2021-11-22 16:09 | 2021-11-22 15:25 | 2021-11-22 15:25 | N | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility |  | Conductor Damaged | 972-54 | Transformer | 25 | p411013 | 972 |  | 07756 Young, Jimmy | EA O&E SUP |  | 33.0407 | -116.8662 | 2021 | Conductor
OMD0000874507-01 | Dmg/Wlite-Wire Down Pole to House | 2021-12-08 17:28 | 2021-12-08 16:58 | 2021-12-08 17:14 | N | N | N | N | N | Arching/Charring |  | 240 V | Contact by Object |  | Foreign Object Contact Services | 524-385 | Transformer | 25 |  | 524 | P873786 c/o 100' #2 serv or splice 20' dmg sect at W.H. 1816 | 05036 Burrell, Dennis | EA O&E SUP | P873786 c/o 100' #2 serv or splice | 32.7538 | -116.7515 | 2021 | Other Contact
OMD0000887843-01 | Dmg/Wlite-Other | 2022-02-01 11:13 | 2022-02-01 09:09 | 2022-02-01 09:09 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Device Damaged | 702-326 | Transformer | 50 | P474051 | 702 | Broken crossarm @ P474051 | 00460 Stiles, Jake | EA O&E SUP | Found broken primary crossarm while | 32.791 | -117.0867 | 2022 | Non Conductor
OMD0000891027-01 | Dmg/Wlite-Other | 2022-02-16 14:43 | 2022-02-16 12:33 | 2022-02-16 12:54 | N | N | N | N | N | Arching/Charring | 12 kV |  | Vegetation Contact |  | Palm Frond On Conductor | 702-292 | Transformer | 25 | Z579032 TO Z579033 | 702 | WILL NEED 2 PALM TREES IN NEAR FUTURE MIDSPAN BETWEEN Z5790 | 00919 Diaz, Ruben | EA O&E SUP | PALM TREE BURNING MIDSPAN Z579032 T | 32.7879 | -117.087 | 2022 | Veg
OMD0000892855-01 | Branch Outage | 2022-02-25 14:45 | 2022-02-25 11:59 | 2022-02-25 11:59 | N | N | N | N | N | Arching/Charring | 12 kV |  | Contact by Object |  | Foreign Object Contacted Wire | F156705 | Fuse | 80A | P274131 | 74 | Mylar balloons got together on top of cutouts and flashed ov | 00460 Stiles, Jake | EA O&E SUP | Mylar balloons got accross cutouts | 32.7878 | -116.9701 | 2022 | Balloon
OMD0000897143-01 | Branch Outage | 2022-03-16 01:48 | 2022-03-15 21:14 | 2022-03-15 21:44 | N | N | N | N | N | Arching/Charring | 12 kV |  | Contact by Object | bird nest on sta pole melted bird guard and damaged cutout | Foreign Object Contacted Device | 212-734R | Recloser |  |  | 212 |  | 03033 Laws, Jeffery | EA O&E SUP |  | 33.2457 | -116.6772 | 2022 | Animal
OMD0000899768-01 | Dmg Dim/Nolite-Xfmr/Grn Bx Fls/Sp | 2022-03-28 23:24 | 2022-03-28 23:14 | 2022-03-28 23:14 | N | N | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | LIGHTNING OR MYLAR BALLOONS | Weather Damaged Device | 551-64 | Transformer | 217 | P171304 | 551 | CAP BANK CUT OUT BODY FAILED 76-2CF, MYLAR BALLOON JUST WEST | 00919 Diaz, Ruben | EA O&E SUP | CAP BANK CUT OUT BODY FAILED 76-2CF | 32.7948 | -116.9553 | 2022 | Undetermined
OMD0000921932-01 | Emer-Specl Req - Fire/Police/Govt | 2022-06-29 01:25 | 2022-06-28 21:51 | 2022-06-28 22:08 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Device Damaged | AM2-40 | Transformer | 25 | P78349 | AM2 |  | B0278 Dawson, Garth R | EA O&E SUP | 160-1 under-arm disconnect was arci | 32.7691 | -117.0528 | 2022 | Non Conductor
OMD0000935718-03 | Branch Outage | 2022-08-26 16:39 | 2022-08-26 16:36 | 2022-08-26 16:36 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Device Damaged | 176-1836R | Recloser |  | P118888 | 176 |  | 03033 Laws, Jeffery | EA O&E SUP |  | 32.9765 | -117.0276 | 2022 | Non Conductor
OMD0000940514-01 | Branch Outage | 2022-09-08 19:03 | 2022-09-08 13:26 | 2022-09-08 14:19 | N | N | Y | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | Pole fire. Customer stated struck by lightning? Unable to verify actual cause | Fire Damaged Transformer | F103134 | Fuse | 150A | P2395168473 | 571 | Transfomer exploded causing pole fire | 04188 Freymiller, Jeffre | EA O&E SUP | Faulted transformer and pole fire | 32.8232 | -117.2761 | 2022 | Other All
OMD0000943364-02 | Branch Outage | 2022-09-18 17:01 | 2022-09-18 14:54 | 2022-09-18 15:29 | Y | N | Y | Y | N |  | 12 kV |  | Contact by Object | mylar balloons | Foreign Object Contact Conductor | F548283 | Fuse | 20A | P137757 | 973 |  | 00460 Stiles, Jake | EA O&E SUP | Mylar balloons caused outage and sm | 32.9777 | -116.7907 | 2022 | Balloon
OMD0000946440-03 | Branch Outage | 2022-09-29 20:23 | 2022-09-29 16:25 | 2022-09-29 16:25 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Moter Vehicle Contact with Pole | 972-1582R | Recloser |  | P615151 | 972 |  | 03033 Laws, Jeffery | EA O&E SUP |  | 33.0476 | -116.9061 | 2022 | Non Conductor
OMD0000977747-01 | Dmg Dim/Nolite-WireDown Pole to H | 2023-01-30 14:14 | 2023-01-30 13:37 | 2023-01-30 14:02 | N | N | N | N | Y | Arching/Charring |  | 240 V | Electric Facility | cu serv on ground energozed | Weather Damaged Service | 162-259 | Transformer | 50 | p171209 | 162 | 2881 WASHINGTON ST 70" #2ssc al p171209 | 05036 Burrell, Dennis | EA O&E SUP | 2881 WASHINGTON ST 70" #2ssc al p17 | 32.7373 | -117.0233 | 2023 | Conductor
OMD0000978771-01 | Dmg/Wlite-Other | 2023-02-03 10:18 | 2023-02-03 09:48 | 2023-02-03 10:01 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Weather Damaged Pole | 87-36 | Transformer | 10 | P577072 | 87 | P577072 Primary down guy rusted off and needs anchor rod ex | 00460 Stiles, Jake | EA O&E SUP | Sent f/u to district. Pole has rus | 32.7816 | -117.0163 | 2023 | Non Conductor
OMD0000979722-01 | Dmg/Wlite-Flash or Sparks | 2023-02-08 13:36 | 2023-02-08 13:01 | 2023-02-08 13:21 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Weather Damaged Service | 74-58 | Transformer | 25 | p168817 | 74 | c/o 40' #2 ssc p168817 to 216 MINNESOTA AVE temp WH. | 05036 Burrell, Dennis | EA O&E SUP | c/o 40' #2 ssc p168817 to 216 MINNE | 32.7849 | -116.9601 | 2023 | Conductor
OMD0000979847-01 | Transformer Outage | 2023-02-08 22:57 | 2023-02-08 20:20 | 2023-02-08 21:04 | N | N | N | N | N | Arching/Charring | 12 kV | 120 V | Other/Undetermined | suitcases were melted at station pole and connections were in bad shape. transformer looked to be overloaded due to blown indicator and oil leaking from station. fuses also blown. | Heat Transformer Overload | 157-1159 | Transformer | 25 | P108505 | 157 | MELTED SUITCASES AND SECONDARY CONNECTIONS AT P108505 CAUSIN | B0278 Dawson, Garth R | EA O&E SUP | MELTED SUITCASES AND SECONDARY CONN | 32.7061 | -116.7884 | 2023 | Non Conductor
OMD0000721225-01 | No Lights - Cause Unknown | 2020-05-02 20:53 | 2020-05-02 13:58 | 2020-05-02 14:47 | N | N | N | N | N | Arching/Charring |  | 480 V | Other/Undetermined | customer's equipment | Customer Problem | 147-238 | Transformer | 2000 | D143873 | 147 |  | 03033 Laws, Jeffery | EA O&E SUP | Costco's switchgear failed, de-ener | 32.7832 | -117.1277 | 2020 | UG Switch
OMD0000982846-03 | Branch Outage | 2023-02-22 03:10 | 2023-02-22 02:04 | 2023-02-22 02:04 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Weather Damaged Pole | 172-615R | Recloser |  | P109800 | 172 | Broken pole, P109800 | 03033 Laws, Jeffery | EA O&E SUP |  | 33.2542 | -116.3481 | 2023 | Non Conductor
OMD0000986065-01 | Dmg Dim/Nolite-WireDown Pole to H | 2023-03-01 08:47 | 2023-03-01 07:55 | 2023-03-01 08:17 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Weather Damaged Service | 731-535 | Transformer | 50 | p70318 | 731 | c/o 50' #2 ssc p70318 at 9279 CAMPO RD tall serv truck (rent | 05036 Burrell, Dennis | EA O&E SUP | c/o 50' #2 ssc p70318 at 9279 CAMPO | 32.7499 | -116.9965 | 2023 | Conductor
OMD0000986453-01 | Branch Outage | 2023-03-01 18:45 | 2023-03-01 17:15 | 2023-03-01 17:49 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | tree slapped wire | Tree Damaged Conductor | 731-11R | Recloser |  | p377745 | 731 | p377745 p477823 300' #6 cu 2 phases dwn tree on wire | 05036 Burrell, Dennis | EA O&E SUP | p377745 p477823 300' #6 cu 2 phases | 32.7494 | -116.9875 | 2023 | Veg
OMD0000986808-01 | Emer-Specl Req - Fire/Police/Govt | 2023-03-02 06:56 | 2023-03-02 05:43 | 2023-03-02 06:10 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility | 3rd party connections failed burned wire dwn | Service Down | 357-1210 | Transformer | 25 | p271396 | 357 | 3rd party connecions failed and overloaded serv c/o 50' #2 s | 05036 Burrell, Dennis | EA O&E SUP | 3rd party connecions failed and ove | 32.8486 | -116.7493 | 2023 | Non Conductor
OMD0000992118-01 | Dmg Dim/Nolite-WireDown Pole to H | 2023-03-21 06:51 | 2023-03-21 06:25 | 2023-03-21 06:25 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Service Down | 702-305 | Transformer | 25 | P573252 | 702 | Service burnt down in rain | 00460 Stiles, Jake | EA O&E SUP | Service burnt down in the rain. Ma | 32.7959 | -117.0834 | 2023 | Conductor
OMD0000721283-01 | Emer-Specl Req - Fire/Police/Gov | 2020-05-03 00:17 | 2020-05-03 00:16 | 2020-05-03 00:16 | Y | N | N | N | N | Actual Ignition | 12 kV |  | Contact by Object | Car hit capacitor & knocked off pad, elbows started 2 very small fires. Police on scene put one out with his feet, 2nd fire went out on its own. | Device Damaged | 746-53 | Transformer | 1500 | D199938 | 746 | Car hit and damaged cap station and cable | 03033 Laws, Jeffery | EA O&E SUP |  | 32.8625 | -117.2058 | 2020 | UG Vehicle
OMD0000996840-01 | Branch Outage | 2023-04-05 06:39 | 2023-04-05 00:40 | 2023-04-05 00:40 | N | N | N | N | N |  | 12 kV |  | Vegetation Contact |  | Connector Damaged | F2474158 | Fuse | 30A |  | 597 | wire down #2 acsr | 04148 Fiamengo, Nicholas | EA O&E SUP | wire down need crew to replace wire | 33.0718 | -117.1921 | 2023 | Veg
OMD0000996844-01 | Emer-Specl Req - Fire/Police/Govt | 2023-04-05 01:25 | 2023-04-05 01:25 | 2023-04-05 01:25 | N | N | N | N | N |  | 12 kV |  | Vegetation Contact |  | Conductor Damaged | 597-236 | Transformer | 25 |  | 597 |  | 04148 Fiamengo, Nicholas | EA O&E SUP | wire down need crew to replace wire | 33.0692 | -117.1904 | 2023 | Veg
OMD0000997058-01 | Emer-Specl Req - Fire/Police/Govt | 2023-04-05 15:17 | 2023-04-05 13:57 | 2023-04-05 13:57 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Device Damaged | 88-444 | Transformer | 50 | P672003 | 88 |  | 00460 Stiles, Jake | EA O&E SUP |  | 32.7864 | -117.0292 | 2023 | Non Conductor
OMD0000998649-01 | Flickering Lights-Just Started | 2023-04-12 12:27 | 2023-04-12 11:08 | 2023-04-12 11:20 | N | N | N | N | N | Arching/Charring | 4 kV |  | Electric Facility |  | Device Damaged | AM2-101 | Transformer | 125 | P78395J | AM2 | 4kv cutout burnt open. Need to c/o all 3 cutouts and doors. | 00460 Stiles, Jake | EA O&E SUP | 4KV cutout feeding sta AM2-101 burn | 32.7683 | -117.0423 | 2023 | Non Conductor
OMD0001005732-01 | Emer-Specl Req - Fire/Police/Govt | 2023-05-11 04:30 | 2023-05-11 03:05 | 2023-05-11 03:19 | N | N | N | N | N | Arching/Charring |  | 240 V | Other/Undetermined | Dumpster fire burnt down service | Service Down | RI1-72 | Transformer | 50 |  | RI1 | Dumpster fire caused service to burn down. Need crew to rep | 00460 Stiles, Jake | EA O&E SUP | Dumpster fire under service caused | 32.7886 | -116.9722 | 2023 | Other All
OMD0001006360-01 | Dmg/Wlite-Flash or Sparks | 2023-05-12 11:06 | 2023-05-12 09:25 | 2023-05-12 09:29 | N | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility |  | Connector Damaged | 397-169 | Transformer | 25 | P870660 | 397 |  | 00460 Stiles, Jake | EA O&E SUP | Replaced bad connection on pole | 32.7671 | -117.0211 | 2023 | Non Conductor
OMD0001009710-01 | Dmg/Wlite-Flash or Sparks | 2023-05-26 22:03 | 2023-05-26 21:27 | 2023-05-26 21:41 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Device Damaged | 972-72 | Transformer | 50 | P136564 | 972 |  | 03033 Laws, Jeffery | EA O&E SUP | Replaced bad cutout door 972-73 | 33.0404 | -116.8703 | 2023 | Non Conductor
OMD0001019501-03 | Branch Outage | 2023-07-09 20:31 | 2023-07-09 17:54 | 2023-07-09 17:54 | Y | N | N | Y | N |  | 12 kV |  | Contact by Object | Car hit pole resulting in wire down | Moter Vehicle Contact with Pole | 524-69R | Recloser |  | P274753 | 524 |  | 04188 Freymiller, Jeffre | EA O&E SUP |  | 32.7373 | -116.822 | 2023 | Vehicle
OMD0001019513-01 | Emer-Specl Req - Fire/Police/Govt | 2023-07-09 20:00 | 2023-07-09 16:45 | 2023-07-09 17:29 | Y | Y | Y | Y | N |  | 12 kV |  | Contact by Object |  | Moter Vehicle Contact with Pole | 524-316 | Transformer | 25 | P274753 | 524 |  | 00460 Stiles, Jake | EA O&E SUP | Car hit P274753 and took it out and | 32.7472 | -116.7968 | 2023 | Vehicle
OMD0001026302-01 | No Lights - Cause Unknown | 2023-08-03 13:20 | 2023-08-03 12:18 | 2023-08-03 12:31 | N | N | N | N | N | Arching/Charring |  | 120 V | Other/Undetermined | cust breaker was overloaded | Heat Device/Overload | AM1-76 | Transformer | 25 |  | AM1 |  | 04768 Gemelli, Chad E | EA O&E SUP | main breaker was overloaded, cust a | 32.7619 | -117.0369 | 2023 | Non Conductor
OMD0001026472-01 | Dmg/Wlite-Other | 2023-08-04 09:47 | 2023-08-04 06:55 | 2023-08-04 07:54 | N | N | N | N | N | Arching/Charring |  | 208 V | Other/Undetermined | bad meter socket | Device Damaged | 392-156 | Transformer | 500 |  | 392 |  | 04768 Gemelli, Chad E | EA O&E SUP | bad meter socket, meter also damage | 32.8382 | -116.9653 | 2023 | Non Conductor
OMD0001030269-01 | Transformer Outage | 2023-08-18 21:18 | 2023-08-18 19:27 | 2023-08-18 20:16 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Weather Damaged Connector | 326-329 | Transformer | 25 | P771018 | 326 | P771018 repair 1/0 vert sec at 8819 Leigh ave 10' 1/0 al ver | 05036 Burrell, Dennis | EA O&E SUP | repair vert se suitcase failed | 32.6975 | -117.0089 | 2023 | Non Conductor
OMD0001030817-01 | Dmg/Wlite-Flash or Sparks | 2023-08-20 20:06 | 2023-08-20 19:44 | 2023-08-20 19:44 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Weather Damaged Service | 163-70 | Transformer | 15 | P78925 | 163 | P78925 c/o 60' ser to 7965 nichals st access pole from neihg | 05036 Burrell, Dennis | EA O&E SUP | c/o serv | 32.7249 | -117.0285 | 2023 | Conductor
OMD0001031159-02 | Branch Outage | 2023-08-21 06:01 | 2023-08-20 20:49 | 2023-08-21 00:39 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Weather Damaged Pole | 221-1249R | Recloser |  | P478426 | 221 | Pole top burnt off below hubbard brace | 03033 Laws, Jeffery | EA O&E SUP |  | 33.0112 | -116.4702 | 2023 | Non Conductor
OMD0001031181-01 | Transformer Outage | 2023-08-20 21:33 | 2023-08-20 21:17 | 2023-08-20 21:17 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Weather Damaged Service | 163-79 | Transformer | 15 | P77338 | 163 | 2331 EL PRADO AVE c/o cu serv back house midspan access from | 05036 Burrell, Dennis | EA O&E SUP | c/o serv | 32.7303 | -117.0376 | 2023 | Conductor
OMD0001035619-01 | Branch Outage | 2023-09-03 12:21 | 2023-09-03 11:13 | 2023-09-03 11:13 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Weather Damaged Device | F129371 | Fuse | 60A | P271324 | 402 |  | 05036 Burrell, Dennis | EA O&E SUP | kearny door burnt on half | 32.7804 | -117.0261 | 2023 | Non Conductor
OMD0001043302-01 | Dmg Dim/Nolite - Flash or Sparks | 2023-10-03 11:46 | 2023-10-03 08:46 | 2023-10-03 08:59 | N | N | N | N | N | Arching/Charring |  | 208 V | Electric Facility | customer upgraded panel. wire is overloaded. | Weather Damaged Service | 71-145 | Transformer | 87.5 | P373710 | 71 |  | B0278 Dawson, Garth R | EA O&E SUP | customer having overload issue. had | 32.8132 | -116.9683 | 2023 | Non Conductor
OMD0001049414-01 | Dmg/Wlite-Pole Burning | 2023-10-28 06:09 | 2023-10-28 04:38 | 2023-10-28 05:17 | Y | Y | Y | Y | N |  | 12 kV |  | Electric Facility |  | Device Damaged | 237-335 | Transformer | 25 | P131129 | 237 | Plastic insulator melted and started a fire | 03033 Laws, Jeffery | EA O&E SUP | Plastic insulator caught on fire an | 33.0726 | -116.7734 | 2023 | Non Conductor
OMD0001053716-01 | Emer-Specl Req - Fire/Police/Govt | 2023-11-15 13:11 | 2023-11-15 11:20 | 2023-11-15 11:40 | Y | Y | Y | Y | N |  | 12 kV |  | Electric Facility |  | Weather Damaged Transformer | 242-825 | Transformer | 25 | P672270 | 242 | 13505 MAPLEVIEW ST P672270 c/o 25kva HE need hazmat 15a cmu | 05036 Burrell, Dennis | EA O&E SUP | lightnig vs sta | 32.8643 | -116.9034 | 2023 | Non Conductor
OMD0001055394-01 | Dmg/Wlite-Flash or Sparks | 2023-11-21 17:40 | 2023-11-21 17:38 | 2023-11-21 17:38 | N | N | N | N | Y | Arching/Charring | 12 kV |  | Electric Facility |  | Weather Damaged Device | 731-121 | Transformer | 50 | P247172 | 731 | P247172 c/o 3 cutouts 150a fuse cble pole property side arci | 05036 Burrell, Dennis | EA O&E SUP | c/o cutouts | 32.7429 | -116.9988 | 2023 | Non Conductor
OMD0001056604-01 | Dmg/Wlite-Other | 2023-11-28 10:01 | 2023-11-28 08:50 | 2023-11-28 09:23 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Weather Damaged Device | 161-789 | Transformer | 300 | P576570 | 161 |  | 05036 Burrell, Dennis | EA O&E SUP | c/o kearny door burnt in half | 32.719 | -117.018 | 2023 | Non Conductor
OMD0001064835-01 | Emer-Specl Req - Fire/Police/Govt | 2024-01-03 16:16 | 2024-01-03 12:55 | 2024-01-03 13:13 | N | N | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | tracking | Weather Damaged Device | 240-81 | Transformer | 50 |  | 240 | BURNED UP INSULATOR CAUSED BY TRACKING | 00919 Diaz, Ruben | EA O&E SUP | BURNED UP INSULATOR FROM TRACKING @ | 32.8747 | -116.9079 | 2024 | Non Conductor
OMD0001074651-01 | Branch Outage | 2024-02-05 23:21 | 2024-02-05 19:36 | 2024-02-05 19:36 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Weather Damaged Device | F87368 | Fuse | 100A | P174495 | 733 | Pole Fire P174495. Need to c/o cutouts and cable. 100amp f | 00460 Stiles, Jake | EA O&E SUP | Pole fire P174495. Crew to c/o cab | 32.7545 | -117.0131 | 2024 | Non Conductor
OMD0001080951-01 | Emer-Antenna/Metal Object on Wire | 2024-02-29 13:49 | 2024-02-29 12:17 | 2024-02-29 13:13 | N | N | N | N | N | Arching/Charring | 12 kV |  | Contact by Object |  | Customer Problem | 170-128 | Transformer | 75 | P239239 | 170 |  | 03033 Laws, Jeffery | EA O&E SUP | Forklift made contact with wires pr | 33.2701 | -116.3705 | 2024 | Other Contact
OMD0001084945-01 | Emer-Specl Req - Fire/Police/Govt | 2024-03-14 20:10 | 2024-03-14 18:22 | 2024-03-14 18:34 | N | N | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | DUMSTER FIRE | Transformer Vandalism | 416-70 | Three Phase Transformer | 150 |  | 416 | DUMSTER FIRE DMGD STA 416-69 | 00919 Diaz, Ruben | EA O&E SUP | DUMSTER FIRE DMGD STA 416-69 | 32.8008 | -116.9327 | 2024 | Other All
OMD0001085639-01 | Branch Outage | 2024-03-17 09:20 | 2024-03-17 09:18 | 2024-03-17 09:18 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Weather Damaged Conductor | F58097 | Fuse | 150A | P181380 | 341 |  | 00919 Diaz, Ruben | EA O&E SUP | 1 SPAN, 1 WIRE 6/3 CU, P181379 TO P | 32.6551 | -117.0577 | 2024 | Conductor
OMD0001085643-01 | Emer-Specl Req - Fire/Police/Govt | 2024-03-17 09:18 | 2024-03-17 07:09 | 2024-03-17 07:21 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Weather Damaged Conductor | 341-1076 | Transformer | 25 | P181380 | 341 |  | 00919 Diaz, Ruben | EA O&E SUP | 1 SPAN, 1 WIRE 6/3 CU, P181379 TO P | 32.6551 | -117.0577 | 2024 | Conductor
OMD0001090650-01 | Emer-Specl Req - Fire/Police/Govt | 2024-04-05 02:35 | 2024-04-05 01:16 | 2024-04-05 01:26 | N | N | N | N | N | Arching/Charring |  | 240 V | Other/Undetermined | Dumpster fire | Transformer Vandalism | 431-204 | Transformer | 50 |  | 431 | POLE FIRE BY DUMPSTER, BURNED UP U.G 3 IN RISER & SERVICE, T | 00919 Diaz, Ruben | EA O&E SUP | POLE FIRE BY DUMPSTER, NEED CREW TO | 32.7517 | -117.0961 | 2024 | Other All
OMD0001108518-01 | Circuit Outage | 2024-06-19 15:44 | 2024-06-19 14:06 | 2024-06-19 14:59 | Y | Y | Y | Y | N |  | 12 kV |  | Contact by Object | Mylars in line caused ignition | Foreign Object Contacted Wire | JM-12KV-91 | Circuit |  | Z170800 | 91 |  | 04188 Freymiller, Jeffre | EA O&E SUP | Mylars removed. Restored | 32.7395 | -116.9529 | 2024 | Balloon
OMD0001109388-01 | Emer-Specl Req - Fire/Police/Govt | 2024-06-23 22:51 | 2024-06-23 21:26 | 2024-06-23 21:26 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Weather Damaged Device | 406-242 | Transformer | 50 | p377832 | 406 | c/o 2 - 15a fuse and cutouts P377832 | 05036 Burrell, Dennis | EA O&E SUP | c/o 2 - 15a fuse and cutouts P37783 | 32.7903 | -117.0189 | 2024 | Non Conductor
OMD0001109968-01 | Momentary Outage | 2024-06-25 23:22 | 2024-06-25 21:08 | 2024-06-25 21:08 | N | N | N | Y | N |  | 12 kV |  | Vegetation Contact | Car brought wire down started weeds and small plants on fire also melted plastic fence | Moter Vehicle Contact with Pole | GR-12KV-412 | Circuit |  |  | 412 | car vs pole | 01202 Weldy, Kellen | EA O&E SUP | Both line and load wires down archi |  |  | 2024 | Vehicle
OMD0001111148-01 | Momentary Outage | 2024-06-30 04:42 | 2024-06-29 23:19 | 2024-06-29 23:31 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Contact by Object |  | Moter Vehicle Contact with Pole | GR-12KV-414 | Circuit |  |  | 414 | Car hit pole | 04188 Freymiller, Jeffre | EA O&E SUP | Car hit pole. Crew to replace |  |  | 2024 | Vehicle
OMD0001113735-02 | Branch Outage | 2024-07-10 20:01 | 2024-07-10 19:53 | 2024-07-10 19:53 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Dig-in Underground Cable | F2281244 | Fuse | 40A | P378619 | 974 |  | 00460 Stiles, Jake | EA O&E SUP | Fuses blew due to dig in off P87164 | 32.9324 | -116.8701 | 2024 | Non Conductor
OMD0001114095-01 | Dmg Dim/Nolite - Other | 2024-07-12 01:15 | 2024-07-12 01:15 | 2024-07-12 01:15 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Connector Damaged | 237-591 | Transformer | 25 | P516424 | 237 | Hot connection on P516424 C237 | 03033 Laws, Jeffery | EA O&E SUP |  | 33.0168 | -116.8527 | 2024 | Non Conductor
OMD0001116043-01 | Emer-Specl Req - Fire/Police/Govt | 2024-07-19 19:33 | 2024-07-19 17:57 | 2024-07-19 18:11 | N | N | N | N | N | Arching/Charring |  | 240 V | Vegetation Contact |  | Foreign Object Contact Services | 246-884 | Transformer | 50 |  | 246 | SSC BURNED DOWN | 00919 Diaz, Ruben | EA O&E SUP | SSC BURNED DWN @ TREE | 32.8553 | -116.8473 | 2024 | Veg
OMD0001120914-01 | Voltage Problem-Low/Just Start | 2024-08-07 13:07 | 2024-08-07 11:45 | 2024-08-07 12:06 | N | N | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | THE SUN, BREAKERS | Customer Problem | 386-224 | Transformer | 50 |  | 386 |  | 00919 Diaz, Ruben | EA O&E SUP | CUST PROB, NEEDS ELECTRICIAN TO REP | 32.832 | -116.8937 | 2024 | Non Conductor
OMD0001121793-01 | No Lights in Part-Just Started | 2024-08-10 14:52 | 2024-08-10 14:05 | 2024-08-10 14:29 | N | N | N | N | N | Arching/Charring |  | 240 V | Other/Undetermined | SUN, BRKR GOT HOT & TRIPPED | Customer Problem | 380-344 | Transformer | 50 |  | 380 |  | 00919 Diaz, Ruben | EA O&E SUP | RESET BRKR | 32.7967 | -117.0737 | 2024 | Non Conductor
OMD0001121942-01 | No Lights - Cause Unknown | 2024-08-11 14:42 | 2024-08-11 14:18 | 2024-08-11 14:28 | N | N | N | N | N | Arching/Charring |  | 240 V | Other/Undetermined | HEAT @ SUB PANEL | Customer Problem | 418-536 | Transformer | 50 |  | 418 |  | 00919 Diaz, Ruben | EA O&E SUP | PROB @ SUB PANEL, NEEDS ELECTRICIAN | 32.8114 | -116.9505 | 2024 | Non Conductor
OMD0001121989-01 | Dmg/Wlite-Flash or Sparks | 2024-08-11 19:14 | 2024-08-11 18:21 | 2024-08-11 18:36 | N | N | N | N | N | Arching/Charring |  | 240 V | Other/Undetermined | PS TO N CONTACT | Weather Damaged Service | 731-429 | Transformer | 50 |  | 731 | INSTALL 60 FT #2 SSC AL RFS 6 SOLID OPN WIRE SEC FROM STA 73 | 00919 Diaz, Ruben | EA O&E SUP | OPN WIRE SEC FROM STA 731-429 TO P5 | 32.752 | -116.9874 | 2024 | Other Contact
OMD0001121995-01 | No Lights - Cause Unknown | 2024-08-11 21:53 | 2024-08-11 20:21 | 2024-08-11 20:40 | N | N | N | N | N | Arching/Charring |  | 240 V | Other/Undetermined | CUST FAULT | Customer Problem | 356-1913 | Transformer | 75 |  | 356 |  | 00919 Diaz, Ruben | EA O&E SUP | 1 PS LEG FAULTING TO GRND, NEEDS EL | 32.8684 | -116.8205 | 2024 | Non Conductor
OMD0001122220-01 | Emer-Specl Req - Fire/Police/Govt | 2024-08-12 19:48 | 2024-08-12 15:32 | 2024-08-12 15:47 | N | N | N | N | N | Arching/Charring | 4 kV |  | Electric Facility |  | Heat Device/Overload | RI1-92 | Transformer | 50 | P176025 | RI1 | REPLACE DEAD END ON PHASE & CHG CUT OUT MAY HAVE TO REPLACE | 00919 Diaz, Ruben | EA O&E SUP | CHOCOLATE BOX FAILED & WENT PHASE T | 32.7944 | -116.9734 | 2024 | Non Conductor
OMD0001122579-01 | No Lights - Cause Unknown | 2024-08-13 20:03 | 2024-08-13 19:13 | 2024-08-13 19:49 | N | N | N | N | N | Arching/Charring |  | 240 V | Other/Undetermined | CUSTOMER BUSS WORK | Customer Problem | 411-159 | Transformer | 25 |  | 411 |  | 00919 Diaz, Ruben | EA O&E SUP | BAD 225 AMP MAIN BRKR, NEEDS ELECTR | 32.8021 | -116.9122 | 2024 | Non Conductor
OMD0001122924-01 | Branch Outage | 2024-08-14 20:08 | 2024-08-14 18:09 | 2024-08-14 18:24 | N | N | N | N | N | Arching/Charring | 12 kV |  | Contact by Object |  | Equipment Contacted Conductor | F2010041 | Fuse | 75A |  | 552 | WIRE DWN 1 WIRE 1 SPAN ABOUT 300 FT | 00919 Diaz, Ruben | EA O&E SUP | WIRE DWN P273256 TO P273255 | 32.8023 | -116.9759 | 2024 | Other Contact
OMD0001125002-01 | No Lights - Cause Unknown | 2024-08-21 21:07 | 2024-08-21 20:16 | 2024-08-21 20:34 | N | N | N | N | N | Arching/Charring |  | 240 V | Other/Undetermined | HEAT IN CUSTOMER BRKR | Customer Problem | 409-1165 | Transformer | 50 |  | 409 |  | 00919 Diaz, Ruben | EA O&E SUP | CUST HAS BAD 15 AMP BRKR, NEEDS ELE | 32.8159 | -116.9578 | 2024 | Non Conductor
OMD0001126262-01 | Emer-Specl Req - Fire/Police/Govt | 2024-08-26 12:48 | 2024-08-26 10:59 | 2024-08-26 11:14 | N | N | N | N | N | Arching/Charring | 12 kV |  | Contact by Object | MYLARS | Foreign Object Contact Conductor | 413-241 | Three Phase Transformer | 75 | P74401 | 413 |  | 00919 Diaz, Ruben | EA O&E SUP | MYLARS @ P74401 2 BLWN FUSES, CAUSE | 32.8004 | -116.9288 | 2024 | Balloon
OMD0001130638-01 | Transformer Outage | 2024-09-08 21:55 | 2024-09-08 21:51 | 2024-09-08 21:52 | N | N | N | N | N | Arching/Charring |  | 240 V | Other/Undetermined | THE SUN...TRIPLE DIGITS | Reset Breaker on Transformer | 551-161 | Transformer | 25 |  | 551 | NEED TO REMOVE LOAD OFF OF STA 551-161, STA HAS TRIPPED TWIC | 00919 Diaz, Ruben | EA O&E SUP | RESET SEC BRKR @ STA | 32.8017 | -116.9568 | 2024 | Non Conductor
OMD0001135160-01 | Emer-Specl Req - Fire/Police/Govt | 2024-09-22 04:25 | 2024-09-22 03:52 | 2024-09-22 03:52 | N | N | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | the house was on fire, pretty sure there was heat involved. | Company Shut-Off | 415-543 | Transformer | 50 |  | 415 |  | 07756 Young, Jimmy | EA O&E SUP | 12060 and 12062 short st de-energiz | 32.8268 | -116.9322 | 2024 | Other All
OMD0001139049-01 | Emer-Specl Req - Fire/Police/Govt | 2024-10-07 22:03 | 2024-10-07 18:45 | 2024-10-07 18:45 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Connector Damaged | 971-447 | Transformer | 50 | P419428 | 971 | Secondary melted & caught fire, need to replace xfmr, sec co | 03033 Laws, Jeffery | EA O&E SUP |  | 33.0197 | -116.8664 | 2024 | Non Conductor
OMD0001139144-01 | Emer-Specl Req - Fire/Police/Govt | 2024-10-08 04:28 | 2024-10-08 03:39 | 2024-10-08 04:20 | N | N | N | N | N |  |  | 240 V | Other/Undetermined | unknown causee no FD on scene pole butt charred fire was about 15x15 | Fire Damaged Pole | 244-587 | Transformer | 50 | P171078 | 244 |  | 05036 Burrell, Dennis | EA O&E SUP | no FD on scene pole butt is charred | 32.8439 | -116.9319 | 2024 | Other All
OMD0001143392-01 | Emer-Specl Req - Fire/Police/Govt | 2024-10-24 20:38 | 2024-10-24 20:38 | 2024-10-24 20:38 | N | N | N | N | Y |  | 12 kV | 240 V | Other/Undetermined | Fire in yard (trash) caught pole | Fire Damaged Pole | 94-419 | Transformer | 25 | P870326 | 94 | Pole caught fire. Pole needs to be replaced. Also need to ch | 04188 Freymiller, Jeffre | EA O&E SUP | POLE FIRE | 32.7142 | -116.9905 | 2024 | Other All
OMD0001145594-01 | Emer-Specl Req - Fire/Police/Govt | 2024-11-03 01:38 | 2024-11-03 00:32 | 2024-11-03 01:03 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Weather Damaged Device | 397-84 | Transformer | 167 | P774238 | 397 | Replace 100 kva HE transformer Transformer left in power. Bu | 07756 Young, Jimmy | EA O&E SUP | replace transformer | 32.7777 | -117.0219 | 2024 | Non Conductor
OMD0001148622-01 | No Lights in Part-Just Started | 2024-11-14 13:29 | 2024-11-14 13:04 | 2024-11-14 13:04 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility | mater base/socket clips burnt up | Customer Problem | 406-498 | Transformer | 100 | meter panel | 406 |  | 03033 Laws, Jeffery | EA O&E SUP | Customer's meter base/socket burnt | 32.7708 | -117.0091 | 2024 | Non Conductor
OMD0001150956-01 | Emer-Specl Req - Fire/Police/Govt | 2024-11-24 05:13 | 2024-11-24 01:28 | 2024-11-24 01:44 | Y | Y | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Weather Damaged Device | 144-115 | Transformer | 25 | P91910 | 144 | burnt crossarm, back yard of 3566 atlas CLIMBER | 07756 Young, Jimmy | EA O&E SUP | damaged cross arm deenergized for s | 32.8095 | -117.1586 | 2024 | Non Conductor
OMD0001152966-02 | Circuit Outage | 2024-12-04 16:54 | 2024-12-04 14:42 | 2024-12-04 14:57 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Device Damaged | MY-12KV-400 | Circuit |  | P576830 | 400 | damaged 600A underarm disconnect | 07756 Young, Jimmy | EA O&E SUP | crew to replace underarm disconnect | 32.8008 | -117.0155 | 2024 | Non Conductor
OMD0001152974-01 | Emer-Specl Req - Fire/Police/Govt | 2024-12-04 16:54 | 2024-12-04 14:20 | 2024-12-04 14:39 | N | Y | Y | Y | N |  | 12 kV |  | Other/Undetermined | no obvious cause found just burning of grass near pole and around telco ug utilities | Undetermined | 401-342 | Transformer | 300 | Z470219 | 401 |  | 05036 Burrell, Dennis | EA O&E SUP | no dmg found fire near pole | 32.7908 | -117.0215 | 2024 | Other All
OMD0001158147-02 | Branch Outage | 2024-12-23 12:20 | 2024-12-23 12:10 | 2024-12-23 12:10 | Y | N | Y | N | N | Arching/Charring | 12 kV |  | Electric Facility | Station faulted and caught fire to pole and small surrounding area | Transformer Vandalism | 357-45R | Recloser |  | P375023 | 357 |  | 04188 Freymiller, Jeffre | EA O&E SUP | Faulted transformer. Crew to replac | 32.8161 | -116.7731 | 2024 | Non Conductor
OMD0001158152-01 | Emer-Specl Req - Fire/Police/Govt | 2024-12-23 12:13 | 2024-12-23 10:36 | 2024-12-23 12:06 | N | N | N | N | N |  | 12 kV |  | Other/Undetermined | transformer caught on fire, small fire started at base of pole | Foreign Object Contacted Device | 357-1279 | Transformer | 15 |  | 357 | replace 25 kva H transformer | B5405 Parks, Michael K | EA O&E SUP | replace 25 kva H transformer | 32.8483 | -116.7486 | 2024 | Other All
OMD0001158792-01 | No Lights in Part-Just Started | 2024-12-27 16:30 | 2024-12-27 14:56 | 2024-12-27 15:19 | N | N | N | N | N | Arching/Charring |  | 120 V | Other/Undetermined | Bad connection | Connector Damaged | 356-396 | Transformer | 50 |  | 356 |  | 04768 Gemelli, Chad E | EA O&E SUP | connection burnt open at weatherhea | 32.8625 | -116.8219 | 2024 | Non Conductor
OMD0000647165-01 | Branch Outage | 2019-07-25 20:55 | 2019-07-25 19:19 | 2019-07-25 20:40 | N | N | N | N | N | Arching/Charring | 4 kV |  | Contact by Object | Balloons | Foreign Object Contact Conductor | F129168 | Fuse | 150A | P270259 | RD4 |  | 03508 Dawson, Trevor (I) | INACTIVE T | Balloons cleared @ P270259 | 32.7602 | -117.0683 | 2019 | Balloon
OMD0000657135-01 | No Lights in Part-Just Started | 2019-09-03 09:31 | 2019-09-03 07:09 | 2019-09-03 07:49 | N | N | N | N | N | Arching/Charring |  | 208 V | Other/Undetermined | customer equipment burnt. | Device Damaged | 732-266 | Transformer | 150 |  | 732 |  | 04204 Decresente, Joseph(I) | INACTIVE T | test block burnt in panel . | 32.7466 | -116.9873 | 2019 | Non Conductor
OMD0000657851-01 | Branch Outage | 2019-09-04 16:30 | 2019-09-04 15:41 | 2019-09-04 15:56 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | cutout burned at connection point, no damage to facility/property | Device Damaged | F2089845 | Fuse | 75A | P175122 | 417 | bad cutout | 03508 Dawson, Trevor (I) | INACTIVE T | Cutout failed, need crew to replace | 32.7876 | -116.9337 | 2019 | Non Conductor
OMD0000657892-01 | Branch Outage | 2019-09-04 18:28 | 2019-09-04 16:30 | 2019-09-04 17:28 | N | N | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | Lightning hit X-FMR, minor burn marks on case | Transformer Problem | F192745 | Fuse | 100A | P577747 | 396 |  | 03508 Dawson, Trevor (I) | INACTIVE T | Lightning hit X-FMR | 32.8844 | -116.9462 | 2019 | Non Conductor
OMD0000658801-01 | Transformer Outage | 2019-09-06 23:53 | 2019-09-06 22:31 | 2019-09-06 22:43 | N | N | N | N | N | Arching/Charring | 12 kV | 120 V | Electric Facility | Secondary connection failed, burnt open. Minor charring/melting on pole...no damg to pole/property | Connector Damaged | 374-53 | Transformer | 75 | P132546 | 374 |  | 03508 Dawson, Trevor (I) | INACTIVE T | Bad conn's @pole, made repairs, rst | 32.6965 | -117.1744 | 2019 | Non Conductor
OMD0000659103-01 | Emer-Specl Req - Fire/Police/Gov | 2019-09-08 11:59 | 2019-09-08 09:04 | 2019-09-08 09:35 | N | N | N | N | Y | Actual Ignition | 12 kV |  | Other/Undetermined | Structure fire- apartment bldg- NON SDGE RELATED | Customer Problem | 92-648 | Transformer | 75 |  | 92 |  | 03508 Dawson, Trevor (I) | INACTIVE T | STRUC FIRE- Left apartment unit off | 32.734 | -116.9582 | 2019 | Other All
OMD0000659642-01 | Circuit Outage | 2019-09-10 14:39 | 2019-09-10 13:07 | 2019-09-10 13:25 | N | N | N | Y | N | Actual Ignition | 12 kV |  | Electric Facility | 600 amp disconnect failed p194970 | Heat Device/Overload | SYO-12KV-461 | Circuit |  | p194970 | 461 | bad 900 amp disconnect | 05449 Bauers, Danny (I) | INACTIVE T | 600 amp disconnect failed p194970 | 32.5639 | -117.0333 | 2019 | Non Conductor
OMD0000659642-02 | Circuit Outage | 2019-09-10 14:31 | 2019-09-10 13:28 | 2019-09-10 13:42 | N | N | N | Y | N | Arching/Charring | 12 kV |  | Other/Undetermined | BURNT DISCONNECT | Connector Damaged | SYO-12KV-461 | Circuit |  | p194970 | 461 |  | 28180 Fitch, Arnold (I) | INACTIVE T | BURNT 12KV DISCONNECT AT P194970 | 32.5639 | -117.0333 | 2019 | Non Conductor
OMD0000663072-01 | Emer-Specl Req - Fire/Police/Gov | 2019-09-24 13:59 | 2019-09-24 13:38 | 2019-09-24 13:42 | N | N | N | N | Y | Actual Ignition | 12 kV |  | Other/Undetermined | Transient fire on hillside near SDGE facilities, no damage to SDGE facilities | Weather Damaged Pole | 549-173 | Transformer | 50 |  | 549 |  | 03508 Dawson, Trevor (I) | INACTIVE T | BRUSH FIRE-250 W MAIN ST- SFTY CHK/ | 32.7955 | -116.9796 | 2019 | Other All
OMD0000667278-01 | Voltage Problem-Low/Just Start | 2019-10-10 17:46 | 2019-10-10 16:45 | 2019-10-10 17:14 | N | N | N | N | N | Arching/Charring |  | 240 V | Other/Undetermined | secondary service burned open at pole, no damage to any property | Conductor Damaged | 163-165 | Transformer | 50 | P276548 | 163 | SVC damaged (cut open for SFTY) @ P276548, feeding 1610 ELRO | 03508 Dawson, Trevor (I) | INACTIVE T | SVC wire damaged (NO WIRE DOWN) Cal | 32.7217 | -117.0297 | 2019 | Conductor
OMD0000667698-02 | Branch Outage | 2019-10-12 11:28 | 2019-10-12 09:11 | 2019-10-12 10:14 | N | N | N | N | Y | Arching/Charring | 4 kV |  | Other/Undetermined | SALT AIR CORROSION | Device Damaged | F264711 | Fuse | 40A | P62005 | SEA1 |  | 00638 Olson, Robert (I) | INACTIVE T | CREW TO REPLACE CUT OUT P62005 | 32.9578 | -117.2583 | 2019 | Non Conductor
OMD0000668148-01 | Dmg/Wlite-Xfmr/Grn Box Flash/Spr | 2019-10-15 11:33 | 2019-10-15 05:56 | 2019-10-15 06:40 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Connector Damaged | 77-202 | Transformer | 1500 | P970864 | 77 |  | 04204 Decresente, Joseph(I) | INACTIVE T | joint met with on duty to set up ou | 32.7988 | -116.9752 | 2019 | Non Conductor
OMD0000671547-01 | Emer-Specl Req - Fire/Police/Gov | 2019-10-26 17:46 | 2019-10-26 16:18 | 2019-10-26 16:40 | N | N | N | N | N | Arching/Charring |  | 240 V | Vegetation Contact |  | Connector Damaged | 306-186 | Transformer | 45 | CUSTOMERS METER POLE | 306 |  | 00638 Olson, Robert (I) | INACTIVE T |  | 33.0102 | -117.2005 | 2019 | Veg
OMD0000673455-01 | Branch Outage | 2019-11-01 11:19 | 2019-11-01 09:58 | 2019-11-01 10:11 | N | N | N | N | N | Arching/Charring | 4 kV |  | Electric Facility | blown 15amp fuse | Undetermined | F102741 | Fuse | 15A | p167303 | GN1 |  | 05351 Henry, Matthew (I) | INACTIVE T | one blown fuse on p167303 refused a | 32.8076 | -117.2294 | 2019 | Non Conductor
OMD0000674202-01 | Emer-Specl Req - Fire/Police/Gov | 2019-11-04 20:55 | 2019-11-04 17:29 | 2019-11-04 18:04 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Heat Device/Overload | 191-129 | Three Phase Transformer | 300 | P24434 | 191 | REPLACE DAMAGED UNDERARM DISCONNECTS P24434 SWI 191-413 | 00638 Olson, Robert (I) | INACTIVE T | CREW TO REPLACE DAMAGED 600amp DISC | 33.2016 | -117.3388 | 2019 | Non Conductor
OMD0000674224-01 | Transformer Outage | 2019-11-04 23:02 | 2019-11-04 20:55 | 2019-11-04 21:30 | N | N | N | N | N | Arching/Charring |  | 120 V | Other/Undetermined | Overloaded secondary connections. No DAMG to SDGE/public property | Connector Damaged | 416-238 | Transformer | 100 | P771961 | 416 | Burned up secondary connections @P771961, feeding several ap | 03508 Dawson, Trevor (I) | INACTIVE T | Burned up CONN's @ pole. Need crew | 32.7994 | -116.939 | 2019 | Non Conductor
OMD0000674225-01 | Dmg/Wlite-Flash or Sparks | 2019-11-04 22:33 | 2019-11-04 21:12 | 2019-11-04 21:47 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Service Down | 859-71 | Transformer | 25 | P222614 | 859 | DAMAGED MID SPAN SERVICE | 00638 Olson, Robert (I) | INACTIVE T | NEED CREW TO REPAIR SERVICES TO 933 | 33.1945 | -117.1979 | 2019 | Conductor
OMD0000674571-01 | Non Outage | 2019-11-05 18:45 | 2019-11-05 18:06 | 2019-11-05 18:06 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Conductor Damaged | EOS1-14 | Transformer | 37.5 | P124868 | EOS1 | DAMAGED OH SECODARY #2 COPPER TRIPLEX NEUTRAL BURNED OPEN 40 | 00638 Olson, Robert (I) | INACTIVE T | SENT DAF FOR CREW | 33.1853 | -117.353 | 2019 | Conductor
OMD0000676801-01 | Branch Outage | 2019-11-13 19:11 | 2019-11-13 17:37 | 2019-11-13 17:37 | N | N | N | N | N | Arching/Charring | 12 kV |  | Vegetation Contact |  | Tree Damaged Conductor | F264615 | Fuse | 150A | P416554 | 66 | ROTTEN TREE FELL ON CONDUCTOR HALF WAY BETWEEN P416554 AND | 00638 Olson, Robert (I) | INACTIVE T | ROTTEN TREE FELL CONTACTING CONDUCT | 32.9914 | -117.2239 | 2019 | Veg
OMD0000677451-01 | Emer-Specl Req - Fire/Police/Gov | 2019-11-16 01:00 | 2019-11-15 22:06 | 2019-11-15 22:20 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | CUTOUT & DOOR | Weather Damaged Device | 759-234 | Transformer | 25 | P371792 | 759 | DAMAGED CUTOUT & DOOR | 05449 Bauers, Danny (I) | INACTIVE T | DAMAGED CUTOUT & DOOR CALLED FOR CR | 32.7476 | -117.0217 | 2019 | Non Conductor
OMD0000681103-01 | Emer-Specl Req - Fire/Police/Gov | 2019-11-28 01:52 | 2019-11-28 | 2019-11-28 00:23 | N | N | N | N | Y | Actual Ignition |  | 120 V | Other/Undetermined | STRUCTURE FIRE- Non SDGE related... pulled meters for SFTY per FD request | Company Shut-Off | 1138-720 | Transformer | 25 |  | 1138 |  | 03508 Dawson, Trevor (I) | INACTIVE T | Pulled meters on BLDG, per FD reque | 32.8748 | -116.9391 | 2019 | Other All
OMD0000686264-01 | Dmg/Wlite-Wire Down Pole to Pole | 2019-12-14 10:37 | 2019-12-14 08:02 | 2019-12-14 08:25 | N | N | N | N | N | Arching/Charring | 12 kV |  | Contact by Object | WIRE BURNED IN DIRT ONLY | Equipment Contacted Conductor | 718-60 | Three Phase Transformer | 150 | P81867 | 718 | wire down | 05449 Bauers, Danny (I) | INACTIVE T | DAF COMPLETED WIRE DOWN P81867 & P8 | 32.6405 | -117.1103 | 2019 | Other Contact
OMD0000686480-01 | Branch Outage | 2019-12-15 13:52 | 2019-12-15 12:39 | 2019-12-15 12:57 | N | N | N | N | N | Arching/Charring | 12 kV |  | Vegetation Contact |  | Foreign Object Contact Conductor | F4889 | Fuse | 75A |  | 159 |  | 05449 Bauers, Danny (I) | INACTIVE T | palm frond between p188026 & p18802 | 32.5725 | -117.1187 | 2019 | Veg
OMD0000688307-01 | Emer-Specl Req - Fire/Police/Gov | 2019-12-20 14:26 | 2019-12-20 13:27 | 2019-12-20 13:43 | N | N | N | N | Y | Actual Ignition |  | 120 V | Other/Undetermined | Structure fire in apartment BLDG...NON SDGE RELATED | Customer Problem | 403-382 | Transformer | 50 |  | 403 |  | 03508 Dawson, Trevor (I) | INACTIVE T | Power restored to non damaged units | 32.8024 | -117.0505 | 2019 | Other All
OMD0000721735-01 | Transformer Outage | 2020-05-05 09:43 | 2020-05-05 07:47 | 2020-05-05 08:19 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility | 1-HOLE LUGS BURNING UP AT XFMR FLAGS (AT BUSHING) | Connector Damaged | 751-1605 | Transformer | 50 | D3385269165 | 751 | BAD 1-HOLE LUG SECONDARY CONNECTIONS AT XFMR FLAG AT BUSHING | 30566 Garegnani, Dominic | NC O&E SUP | BAD SECONDARY 1HOLE LUGS AT XFMR BU | 33.0924 | -117.2576 | 2020 | UG Connector
OMD0000690499-01 | Voltage Problem-Low/Just Start | 2019-12-30 13:02 | 2019-12-30 12:26 | 2019-12-30 12:36 | Y | N | N | N | N | Arching/Charring |  | 240 V | Other/Undetermined | city meter pedestile flashed over | Device Damaged | 482-285 | Transformer | 75 |  | 482 |  | 05351 Henry, Matthew (I) | INACTIVE T | need new meter 120/240 and reconnec | 32.7262 | -117.225 | 2019 | Non Conductor
OMD0000700678-01 | Emer-Specl Req - Fire/Police/Gov | 2020-02-11 04:23 | 2020-02-11 01:45 | 2020-02-11 01:59 | Y | N | N | N | N | Actual Ignition | 12 kV |  | Electric Facility | wire down caused small fire | Connector Damaged | 412-88 | Transformer | 50 | P477433 | 412 |  | 50433 Lester, James(I) | INACTIVE T | wire down from p775473 to p477433 | 32.79 | -116.9184 | 2020 | Non Conductor
OMD0000705541-01 | Dmg/Wlite-Flash or Sparks | 2020-02-29 21:09 | 2020-02-29 20:14 | 2020-02-29 20:26 | N | N | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | arcing from weather foggy, moisture in the air | Weather Damaged Device | 52-205 | Transformer | 50 | P2132369374 | 52 | cutouts on P2132369374 arcing on top of door probably needs | 05351 Henry, Matthew (I) | INACTIVE T | cutout proprty side sparking, needs | 32.7481 | -117.2457 | 2020 | Non Conductor
OMD0000710032-01 | Transformer Outage | 2020-03-18 18:29 | 2020-03-18 17:20 | 2020-03-18 17:42 | N | N | N | N | N | Arching/Charring | 4 kV |  | Other/Undetermined | looks like the door slowly melted into the cutout then came open | Heat Device/Overload | PB1-105 | Transformer | 85 | p837159 | PB1 | bad cutouts | 05351 Henry, Matthew (I) | INACTIVE T | bad cutouts on sta PB1-105 | 32.7984 | -117.2495 | 2020 | Non Conductor
OMD0000710047-01 | Transformer Outage | 2020-03-18 21:44 | 2020-03-18 20:39 | 2020-03-18 20:57 | N | N | N | N | N | Arching/Charring | 4 kV |  | Other/Undetermined | wire looks like it melted infront of bushing | Device Deenergized for Safety | PL2-57 | Transformer | 37.5 | P835727 | PL2 | bad 37.5 kva sta | 05351 Henry, Matthew (I) | INACTIVE T | bad sta PL2-57 | 32.7439 | -117.241 | 2020 | Non Conductor
OMD0000710842-01 | Emer-Specl Req - Fire/Police/Gov | 2020-03-23 15:40 | 2020-03-23 14:09 | 2020-03-23 14:30 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Conductor Damaged | 524-1179 | Transformer | 25 | P177990 | 524 | wire down pole to pole | 04204 Decresente, Joseph(I) | INACTIVE T | wire down pole to pole | 32.7517 | -116.7723 | 2020 | Conductor
OMD0000715391-01 | Transformer Outage | 2020-04-11 11:17 | 2020-04-11 09:59 | 2020-04-11 10:24 | N | N | N | N | N | Arching/Charring |  | 240 V | Other/Undetermined | DAMAGE IS INSIDE OF TREE GUARD, TREE WAS REMOVED MAYBE YEARS AGO? NO TREE PRESENT | Weather Damaged Conductor | WA6-98 | Transformer | 25 |  | WA6 | REPLACE SECONDARY #4 SSC COPPER FROM P729251 TO P 729271 | 05449 Bauers, Danny (I) | INACTIVE T | REPLACE SECONDARY #4 SSC COPPER FRO | 32.7302 | -117.1059 | 2020 | Conductor
OMD0000721708-01 | Emer-Specl Req - Fire/Police/Gov | 2020-05-04 20:42 | 2020-05-04 19:59 | 2020-05-04 20:17 | N | N | N | Y | N | Actual Ignition |  | 120 V | Other/Undetermined | HOUSE FIRE LOCKED MTR CABINET IN OFF POSITION BOLT ON MTR HERE | Off at Main Breaker | LF1-84 | Transformer | 50 |  | LF1 |  | 84962 Swanson, Robert (I) | INACTIVE T | FIRE AT THIS HOUSE LOCKED MTR CABIN | 32.8796 | -117.2453 | 2020 | Other All
OMD0000722121-01 | Branch Outage | 2020-05-06 12:31 | 2020-05-06 10:29 | 2020-05-06 10:46 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | SWITCH FAILED NO BURNING ON GROUND AT BASE OF POLE | Heat Device/Overload | 1202-76 | Switch |  | P280173 | 1202 | BAD 600A DISCONNECT | 05449 Bauers, Danny (I) | INACTIVE T | 600 AMP DISCONNECT FAILED | 32.5537 | -116.9884 | 2020 | Non Conductor
OMD0000723888-01 | No Lights in Part-Just Started | 2020-05-12 19:40 | 2020-05-12 18:28 | 2020-05-12 19:27 | N | N | N | N | N | Arching/Charring |  | 120 V | Other/Undetermined | Customer owned equipment (breaker bad) NO SDGE EQUIP | Customer Problem | 163-47 | Transformer | 25 |  | 163 |  | 03508 Dawson, Trevor (I) | INACTIVE T | Cust equipment- BAD BREAKER- Burnt | 32.7308 | -117.0463 | 2020 | Non Conductor
OMD0000724183-01 | Emer-Specl Req - Fire/Police/Gov | 2020-05-14 06:08 | 2020-05-14 01:41 | 2020-05-14 02:22 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Weather Damaged Service | RD4-16 | Transformer | 25 | p732091 | RD4 | replace service | 05449 Bauers, Danny (I) | INACTIVE T | replace service 100' #4 ssc aluminu | 32.7546 | -117.0644 | 2020 | Conductor
OMD0000724441-01 | Dmg/Wlite-Xfmr/Grn Box Flash/Spr | 2020-05-14 22:16 | 2020-05-14 21:01 | 2020-05-14 21:15 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | Bad connection | Connector Damaged | 731-385 | Transformer | 25 | P473973 | 731 | Bad Primary connection . Jumper and change solid blades and | 04204 Decresente, Joseph(I) | INACTIVE T | Bad primary connections for solid b | 32.7533 | -116.9813 | 2020 | Non Conductor
OMD0000727598-01 | Emer-Specl Req - Fire/Police/Gov | 2020-05-27 16:41 | 2020-05-27 14:15 | 2020-05-27 14:23 | N | N | N | N | Y | Actual Ignition |  | 120 V | Other/Undetermined | house fire melted wires at meter panel cause unknown | Heat Device/Overload | 229-60 | Transformer | 75 |  | 229 | house fire at 10155 embassy way mira mesa cross st is JADE | 84962 Swanson, Robert (I) | INACTIVE T | FIRE TOTALLY DESTROYED MTR HAVING C | 32.9029 | -117.1481 | 2020 | Other All
OMD0000729590-01 | Transformer Outage | 2020-06-04 08:21 | 2020-06-04 06:43 | 2020-06-04 07:09 | N | N | N | N | Y | Arching/Charring | 12 kV | 208 V | Other/Undetermined | BLOWN 12a BAY-O-NET FUSE | Heat Device/Overload | 765-331 | Three Phase Transformer | 150 | D112090 | 765 |  | 51977 Lopez, Oscar (I) | INACTIVE T | REQUESTED ETS ASSIST WHEN HELP ARIV | 33.5534 | -117.6861 | 2020 | UG Fuse
OMD0000729660-01 | Dmg Dim/Nolite - Other | 2020-06-04 12:16 | 2020-06-04 09:54 | 2020-06-04 10:05 | N | N | N | N | Y | Arching/Charring | 12 kV | 480 V | Other/Undetermined | BLOWN BAYONET FUSE | Heat Device/Overload | 1242-111 | Transformer | 1000 | D128506 | 1242 |  | 51977 Lopez, Oscar (I) | INACTIVE T | REQUESTED ETS ASSIST ,MR CLOVIS NOT | 33.5011 | -117.6178 | 2020 | UG Fuse
OMD0000730020-01 | Branch Outage | 2020-06-05 14:53 | 2020-06-05 10:53 | 2020-06-05 11:06 | N | N | N | N | Y | Arching/Charring | 12 kV |  | Other/Undetermined | ELBOW CONN SPLIT | Weather Damaged Connector | F739622 | Fuse | 150A | H5194755683 | 557 |  | 51977 Lopez, Oscar (I) | INACTIVE T | ASSISTED OMARA,CITTEL,F/V & FOUND A | 33.5888 | -117.7011 | 2020 | UG Fuse
OMD0000730221-01 | Dmg/Wlite-Xfmr/Grn Box Flash/Spr | 2020-06-06 10:57 | 2020-06-06 10:09 | 2020-06-06 10:22 | N | N | N | N | N | Arching/Charring | 12 kV | 240 V | Electric Facility |  | Weather Damaged Service | 341-1023 | Transformer | 10 | P188843 | 341 | change service | 05449 Bauers, Danny (I) | INACTIVE T | CauseMA30 - Weather Damaged Service | 32.6518 | -117.0621 | 2020 | Other All
OMD0000730516-01 | Dmg/Wlite-Tree on Wires | 2020-06-08 12:38 | 2020-06-08 10:36 | 2020-06-08 10:53 | N | N | N | N | N | Arching/Charring | 12 kV |  | Vegetation Contact |  | Palm Frond On Conductor | 95-409 | Transformer | 50 | P175484 | 95 | Palm tree contact with 12KV line NEED BIG BUCKET for reach | 03508 Dawson, Trevor (I) | INACTIVE T | Palm contact with 12KV...called for | 32.7489 | -116.9796 | 2020 | Veg
OMD0000731184-01 | Transformer Outage | 2020-06-10 06:31 | 2020-06-10 04:27 | 2020-06-10 05:30 | N | N | N | N | N | Arching/Charring | 4 kV |  | Electric Facility | cutout door burned in half | Fuse Operated in Transformer | WA1-66 | Transformer | 50 | wa1-66 | WA1 |  | 05449 Bauers, Danny (I) | INACTIVE T | CauseMA38 - Fuse Operated in Transf | 32.7236 | -117.1276 | 2020 | Non Conductor
OMD0000732341-02 | Branch Outage | 2020-06-14 14:43 | 2020-06-14 12:56 | 2020-06-14 14:15 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Contact by Object |  | Foreign Object Contacted Device | F614645 | Fuse | 75A | P23092 | SC2 |  | 51977 Lopez, Oscar (I) | INACTIVE T | ASSISTED OMARA MILAR BALLOON GOT | 33.4244 | -117.6127 | 2020 | Balloon
OMD0000733236-01 | No Lights in Part-Just Started | 2020-06-17 23:26 | 2020-06-17 21:56 | 2020-06-17 22:13 | Y | N | N | N | N | Arching/Charring |  | 120 V | Other/Undetermined | WEATHER - OLD CONN | Weather Damaged Connector | 1073-231 | Transformer | 50 | SH729305 | 1073 | CHG OUT ALL 3 MOLD CONN IN 3312 BOX SH729305, REM ALL 3 SPLI | 51977 Lopez, Oscar (I) | INACTIVE T | SUBMITTED DAF CREW TO CHG OUT ALL 3 | 33.4805 | -117.6795 | 2020 | UG Connector
OMD0000738122-01 | Emer-Specl Req - Fire/Police/Gov | 2020-07-07 19:38 | 2020-07-07 17:48 | 2020-07-07 18:07 | Y | N | N | N | N | Actual Ignition |  | 120 V | Electric Facility | Fire started in pedestal, damaged pedestal and SDGE owned SVC wires | Conductor Damaged | 162-533 | Transformer | 25 | Secondary pedestal (customer owned) | 162 |  | 03508 Dawson, Trevor (I) | INACTIVE T | Fire DAMGD UG SVC wire/pedestal.... | 32.7325 | -117.0132 | 2020 | Other All
OMD0000741873-01 | No Lights in Part-Just Started | 2020-07-19 13:49 | 2020-07-19 11:23 | 2020-07-19 11:45 | N | N | N | N | Y | Arching/Charring |  | 120 V | Other/Undetermined | CONECTOR | Weather Damaged Connector | 794-631 | Transformer | 50 |  | 794 |  | 51977 Lopez, Oscar (I) | INACTIVE T | CUST HAD HALF POWER FOUND BAD CONNE | 33.4516 | -117.661 | 2020 | Non Conductor
OMD0000742404-01 | No Lights in Part-Just Started | 2020-07-21 17:52 | 2020-07-21 15:58 | 2020-07-21 17:01 | N | N | N | N | N | Arching/Charring |  | 120 V | Other/Undetermined | Burned test block, cust owned... NO SDGE property DAMG | Customer Problem | 76-216 | Transformer | 100 |  | 76 |  | 03508 Dawson, Trevor (I) | INACTIVE T | Burned test block in Cust panel, JU | 32.7954 | -116.9619 | 2020 | Non Conductor
OMD0000743644-01 | Emer-Specl Req - Fire/Police/Gov | 2020-07-26 13:53 | 2020-07-26 12:50 | 2020-07-26 12:50 | Y | N | Y | Y | N | Actual Ignition | 12 kV |  | Electric Facility | Small 10'X10' "spot fire" in grass below pole. NO DAMG | Undetermined | 409-357 | Three Phase Transformer | 300 | P101639 | 409 |  | 03508 Dawson, Trevor (I) | INACTIVE T | Patrolled OH, no DAMG found, restor | 32.8167 | -116.9564 | 2020 | Non Conductor
OMD0000747471-01 | Emer-Specl Req - Fire/Police/Gov | 2020-08-06 20:18 | 2020-08-06 19:52 | 2020-08-06 19:52 | N | N | N | Y | N | Arching/Charring | 12 kV |  | Other/Undetermined | not sure these are our poles they do not come up on map system | Incomplete | 776-61M | Primary Meter | 12.0 kV |  | 776 |  | 84962 Swanson, Robert (I) | INACTIVE T | fire to the north of biosolids plan | 32.8455 | -117.1636 | 2020 | Other All
OMD0000749380-02 | Branch Outage | 2020-08-13 10:30 | 2020-08-13 09:03 | 2020-08-13 10:24 | Y | N | N | N | N | Actual Ignition | 12 kV |  | Electric Facility | Small fire at base of pole...NO DAMG to public property (pictures taken) | Device Damaged | 386-25R | Recloser |  | P204730 | 386 |  | 03508 Dawson, Trevor (I) | INACTIVE T | Capacitor failed, repairs to be sch | 32.832 | -116.9054 | 2020 | Non Conductor
OMD0000753918-01 | Dmg/Wlite-Flash or Sparks | 2020-08-25 20:20 | 2020-08-25 19:50 | 2020-08-25 19:51 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Weather Damaged Connector | 797-237 | Transformer | 750 | H108614 | 797 | CREW TO REPLACE STACKED 600A TEE ASEMBLY FOR MILLION U/G AL | 51977 Lopez, Oscar (I) | INACTIVE T | CREW TO REPLACE STACKED TEE ASEMBLY | 33.5075 | -117.7091 | 2020 | UG Connector
OMD0000756988-01 | Transformer Outage | 2020-09-05 14:20 | 2020-09-05 12:18 | 2020-09-05 13:13 | Y | N | N | N | N | Actual Ignition | 4 kV |  | Electric Facility |  | Device Damaged | SSC1-34 | Transformer | 50 | P26031 | SSC1 | REPLACE C/OUT TO STA SSC1-34 ,PP26031 | 51977 Lopez, Oscar (I) | INACTIVE T | SUBMITTED DAF CREW TO REPLACE U/OUT | 33.4124 | -117.6075 | 2020 | Non Conductor
OMD0000758908-01 | Emer-Specl Req - Fire/Police/Gov | 2020-09-07 13:09 | 2020-09-07 11:17 | 2020-09-07 11:28 | N | N | N | N | N | Arching/Charring | 12 kV |  | Vegetation Contact | TREE BRANCH FELL TORE DOWN SECONDARY AND SLAPPED PRIMARY ONE SPAN ONE WIRE DOWN P121567 TO P12425. | Tree Damaged Conductor | 781-791 | Three Phase Transformer | 150 | P121567 | 781 | TREE BRANCH BROKE TORE DOWN SECONDARY SLAPPED PRIMARY ONE S | 00638 Olson, Robert (I) | INACTIVE T | TREE BRANCH FELL TORE DOWN SECONDAR | 33.1572 | -117.3497 | 2020 | Veg
OMD0000762393-01 | Dmg/Wlite-Flash or Sparks | 2020-09-19 17:22 | 2020-09-19 17:16 | 2020-09-19 17:16 | N | N | Y | N | N | Arching/Charring | 12 kV |  | Electric Facility | cutout door melted in half | Heat Device/Overload | 529-73 | Three Phase Transformer | 150 | P878719 | 529 |  | 05351 Henry, Matthew (I) | INACTIVE T | cap sta 529-76 CW had a fuse door m | 32.8979 | -117.222 | 2020 | Non Conductor
OMD0000762981-01 | Emer-Specl Req - Fire/Police/Gov | 2020-09-22 12:04 | 2020-09-22 11:33 | 2020-09-22 11:40 | N | N | N | Y | N | Actual Ignition |  | 120 V | Other/Undetermined | GARAGE FIRE | Incomplete | 58-607 | Transformer | 25 |  | 58 |  | 84962 Swanson, Robert (I) | INACTIVE T | FIRE BASICALLY IN THE GARAGE TOLD C | 32.8105 | -117.2104 | 2020 | Other All
OMD0000765361-01 | Emer-Specl Req - Fire/Police/Gov | 2020-09-30 17:46 | 2020-09-30 16:36 | 2020-09-30 16:56 | Y | N | N | N | N | Actual Ignition | 4 kV |  | Electric Facility | connection partally burnt open | Connector Damaged | DR1-114 | Transformer | 25 | p177702 | DR1 | connection burnt open | 02435 Deuel, Jeff (I) | INACTIVE T | need crew to repair jumper | 32.744 | -116.9658 | 2020 | Non Conductor
OMD0000775550-01 | Emer-Specl Req - Fire/Police/Gov | 2020-11-07 08:34 | 2020-11-07 07:00 | 2020-11-07 07:00 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Service Down | 486-135 | Transformer | 50 | P514570 | 486 | OH SERVICE BURNT DOWN P514568 TO 559 ELAIN AVE OC | 00638 Olson, Robert (I) | INACTIVE T | SERVICE BURNT DOWN | 33.2576 | -117.2996 | 2020 | Conductor
OMD0000775790-01 | Dmg Dim/Nolite - Tree on Wire | 2020-11-07 20:23 | 2020-11-07 19:38 | 2020-11-07 20:00 | N | N | N | N | N | Arching/Charring |  | 120 V | Vegetation Contact | at weatherhead the service burn itself in the clear | Tree Damaged Conductor | 279-135 | Transformer | 25 | p834653 | 279 | Bad service | 05351 Henry, Matthew (I) | INACTIVE T | bad service due to tree in front, c | 32.8313 | -117.1904 | 2020 | Veg
OMD0000775907-01 | Branch Outage | 2020-11-08 10:31 | 2020-11-08 08:50 | 2020-11-08 09:12 | N | N | N | N | N | Arching/Charring | 12 kV |  | Vegetation Contact |  | Conductor Damaged | F2267811 | Fuse | 150A | P121329 | 198 | WIRE DOWN P121328 TO P121330 700' #6 CU | 00638 Olson, Robert (I) | INACTIVE T | WIRE DOWN P121328 TO 121330 | 33.2252 | -117.3649 | 2020 | Veg
OMD0000775928-01 | Dmg/Wlite-Other | 2020-11-08 12:31 | 2020-11-08 10:50 | 2020-11-08 10:50 | N | N | N | N | Y | Arching/Charring | 4 kV |  | Vegetation Contact | BAMBOO TOUCHING PRIMARY | Incomplete | EOS1-230 | Switch |  | P23408J | EOS1 | HAD TREE CREW COME OUT ON SUNDAY 11/08 2020 TO CUT BAMBOO OU | 00638 Olson, Robert (I) | INACTIVE T | BAMBOO TOUCHING 4 KV | 33.1862 | -117.3481 | 2020 | Veg
OMD0000775988-01 | Emer-Specl Req - Fire/Police/Gov | 2020-11-08 16:56 | 2020-11-08 16:13 | 2020-11-08 16:34 | N | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility |  | Weather Damaged Service | 255-366 | Transformer | 25 | p183487 | 255 | change service | 05449 Bauers, Danny (I) | INACTIVE T | DAF COMPLETED C/O SERVICE | 32.642 | -117.0741 | 2020 | Other All
OMD0000779560-01 | No Lights - Cause Unknown | 2020-11-21 14:28 | 2020-11-21 12:42 | 2020-11-21 13:19 | N | N | N | N | Y | Arching/Charring |  | 120 V | Electric Facility |  | Weather Damaged Connector | 310-60 | Transformer | 50 | P121672 | 310 |  | 51977 Lopez, Oscar (I) | INACTIVE T | CUST HAS A SPLICE ON O/H SVC & THE | 33.4674 | -117.705 | 2020 | Non Conductor
OMD0000747716-01 | No Lights in Part-Just Started | 2020-08-07 14:51 | 2020-08-07 13:25 | 2020-08-07 14:04 | N | N | N | N | Y | Arching/Charring | 12 kV | 120 V | Other/Undetermined | load caused the melting of the service connections | Open Neutral | 753-1008 | Transformer | 75 | d3399269403 | 753 |  | 04148 Fiamengo, Nicholas | EA O&E SUP | need crew to replace secondary conn | 33.1014 | -117.2467 | 2020 | UG Connector
OMD0000791787-01 | Dmg/Wlite-Xfmr/Green Box Oil Lea | 2021-01-11 19:34 | 2021-01-11 17:39 | 2021-01-11 18:35 | N | N | N | N | Y | Arching/Charring | 12 kV | 120 V | Other/Undetermined | OIL LEAKING TRANS | Weather Damaged Transformer | 1259-92 | Transformer | 50 | 1259-92 | 1259 | CHANGE OUT OIL LEAKING TRANSFORMER,STA 1259-92, D150292, 50 | 51977 Lopez, Oscar (I) | INACTIVE T | SUBMITTED DAF CUST REPORTED OIL LEA | 33.5564 | -117.6349 | 2021 | Non Conductor
OMD0000793924-01 | Emer-Specl Req - Fire/Police/Gov | 2021-01-20 10:47 | 2021-01-20 09:33 | 2021-01-20 09:33 | Y | Y | N | N | N | Actual Ignition | 12 kV |  | Vegetation Contact | tree limb fell on 12kv phase midspan taking the line down | Tree Damaged Conductor | 355-454 | Transformer | 25 | p 75976 | 355 | replace downed 12kv line | 13865 Carroll, Dave (I) | INACTIVE T |  | 32.8315 | -116.7844 | 2021 | Veg
OMD0000808621-01 | Dmg/Wlite-Flash or Sparks | 2021-03-09 10:01 | 2021-03-09 08:57 | 2021-03-09 08:57 | Y | N | N | N | N | Arching/Charring |  | 120 V | Contact by Object | secondary hit catv here | Weather Damaged Conductor | 480-424 | Transformer | 25 | p931064 | 480 |  | 84962 Swanson, Robert (I) | INACTIVE T | this is dupe order from 4443 osprey | 32.7292 | -117.251 | 2021 | Other Contact
OMD0000809821-01 | Emer-Specl Req - Fire/Police/Gov | 2021-03-13 04:01 | 2021-03-13 01:39 | 2021-03-13 02:14 | N | N | N | Y | N | Actual Ignition |  | 240 V | Other/Undetermined | House caught on fire by UG electrical service and electrical panel...SDGE service wire damaged, cause UNKNOWN | Conductor Damaged | 57-745 | Transformer | 25 |  | 57 | Structure fire @ 701 COLIMA ST, originated near UG service a | 03508 Dawson, Trevor (I) | INACTIVE T |  | 32.812 | -117.2629 | 2021 | Other All
OMD0000810829-02 | Branch Outage | 2021-03-17 20:47 | 2021-03-17 18:30 | 2021-03-17 18:30 | N | N | N | N | N | Arching/Charring | 4 kV |  | Other/Undetermined | ug cable was melting | Connector Damaged | RI1-3 | Switch |  | H224917678 | RI1 |  | 05351 Henry, Matthew (I) | INACTIVE T | found bad teesin H224917678 | 32.79 | -116.973 | 2021 | UG Connector
OMD0000811818-01 | Branch Outage | 2021-03-22 05:25 | 2021-03-22 03:51 | 2021-03-22 04:05 | N | N | N | N | N | Arching/Charring | 12 kV |  | Contact by Object | MYLAR BALLONS | Vandalism | F156771 | Fuse | 100A | P166560J | 415 | damaged transformer | 05351 Henry, Matthew (I) | INACTIVE T | found mylar ballons on P166560J and | 32.8241 | -116.9218 | 2021 | Balloon
OMD0000812819-01 | Circuit Outage | 2021-03-25 16:47 | 2021-03-25 15:30 | 2021-03-25 16:02 | N | N | N | N | N | Arching/Charring | 4 kV |  | Contact by Object | mylar ballons phase to phase contact, | Vandalism | RD-4KV-RD1 | Circuit |  | P170330 | RD1 |  | 05351 Henry, Matthew (I) | INACTIVE T | Mylar ballons found in the lines ne | 32.7603 | -117.0703 | 2021 | Balloon
OMD0000814438-01 | Emer-Specl Req - Fire/Police/Gov | 2021-04-01 05:00 | 2021-04-01 04:15 | 2021-04-01 04:30 | N | Y | N | Y | N | Arching/Charring | 12 kV | 240 V | Other/Undetermined | fifth wheel trailer caught fire, damaged there equipment | Customer Problem | 247-467 | Transformer | 25 | p75318 | 247 |  | 05351 Henry, Matthew (I) | INACTIVE T | customer fifth wheel caught fire da | 32.8586 | -116.8573 | 2021 | Other All
OMD0000816766-01 | Branch Outage | 2021-04-13 17:52 | 2021-04-13 16:50 | 2021-04-13 16:50 | N | N | N | N | N | Arching/Charring | 12 kV |  | Contact by Object | BIRD CONTACT STA 209-380 P510073 | Foreign Object in Transformer | 209-660R | Recloser |  | P510073 | 209 | REPLACE DAMAGED 25HE | 00638 Olson, Robert (I) | INACTIVE T | CREW TO REPLACE STA 209-380 P51007 | 33.2212 | -117.2404 | 2021 | Animal
OMD0000756212-01 | Emer-Specl Req - Fire/Police/Gov | 2020-09-02 18:16 | 2020-09-02 18:16 | 2020-09-02 18:16 | Y | N | N | N | N | Arching/Charring |  | 120 V | Contact by Object |  | Equipment Damaged Transformer | 353-842 | Transformer | 25 | D202601 | 353 | DAMAGED 25HDS | 56561 McKeown, John | NE O&E SUP |  | 33.2219 | -117.1253 | 2020 | UG Other Contact
OMD0000824875-01 | Circuit Outage | 2021-05-19 12:03 | 2021-05-19 10:53 | 2021-05-19 11:07 | Y | N | N | Y | N | Actual Ignition | 12 kV |  | Contact by Object | circuit 275 between z92509 and 92508 phase to neutral conductors slapped together contractors working 2 poles north | Device Deenergized for Safety | CM-12KV-275 | Circuit |  |  | 275 |  | 84962 Swanson, Robert (I) | INACTIVE T | ok outage caused by conductors slap |  |  | 2021 | Other Contact
OMD0000833293-01 | Emer-Specl Req - Fire/Police/Govt | 2021-06-23 10:22 | 2021-06-23 10:22 | 2021-06-23 10:22 | N | N | N | N | Y | Actual Ignition |  | 120 V | Vegetation Contact | service vs tree | Foreign Object Contact Services | 492-140 | Transformer | 50 | p836051 | 492 |  | 84962 Swanson, Robert (I) | INACTIVE T | sent daf on other order for 2425 ha | 32.7874 | -117.1993 | 2021 | Veg
OMD0000833307-01 | Dmg Dim/Nolite-WireDown Pole to H | 2021-06-23 10:08 | 2021-06-23 09:56 | 2021-06-23 09:56 | N | N | N | N | Y | Actual Ignition |  | 120 V | Vegetation Contact | tree burned open secondary service pole to house | Tree Damaged Service | 492-140 | Transformer | 50 | p836051 | 492 | blown open service customer out of power | 84962 Swanson, Robert (I) | INACTIVE T | sending daf to c/o service pole to | 32.7874 | -117.1993 | 2021 | Veg
OMD0000848770-01 | Branch Outage | 2021-08-20 13:08 | 2021-08-20 13:08 | 2021-08-20 13:08 | N | N | N | N | N | Arching/Charring | 12 kV |  | Contact by Object | mylar balloons | Foreign Object Contact Conductor | F587467 | Fuse | 100A |  | 206 | REPAIR DAMAGED CODUCTOR. 6/3 AND 4/3 | 00638 Olson, Robert (I) | INACTIVE T | MYLAR BALLOON CONTACT P17385 | 33.2049 | -117.1999 | 2021 | Balloon
OMD0000852874-01 | Dmg/Wlite-Flash or Sparks | 2021-09-07 16:16 | 2021-09-07 14:13 | 2021-09-07 15:22 | N | N | N | N | N | Arching/Charring | 12 kV |  | Vegetation Contact | TRACKING ON DOWN GUY FROM PRIMARY | Customer Restored | 159-130 | Transformer | 25 | P188020J | 159 | PLEASE REMOVE PALM TREE NEXT TO POLE P188020J | 05449 Bauers, Danny (I) | INACTIVE T | DAF COMPLETED C/O X ARMS | 32.5721 | -117.1221 | 2021 | Veg
OMD0000854574-01 | Emer-Specl Req - Fire/Police/Govt | 2021-09-14 03:31 | 2021-09-14 01:03 | 2021-09-14 01:59 | N | Y | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | tracking | Weather Damaged Device | 545-349 | Transformer | 25 | p37463 | 545 | replace 3- poly clamp top pin & insulators with 3- glass ins | 05449 Bauers, Danny (I) | INACTIVE T | DAF COMPLETED CREW WILL replace 3- | 32.7869 | -117.254 | 2021 | Non Conductor
OMD0000859021-01 | Transformer Outage | 2021-10-01 15:28 | 2021-10-01 13:47 | 2021-10-01 13:54 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Weather Damaged Conductor | 260-52 | Transformer | 50 | between p282533 & 282532 | 260 | damaged aerial cable between p282533 & p282532 | 05449 Bauers, Danny (I) | INACTIVE T | DAF COMPLETED BAD AERIAL CABLE P282 | 32.5776 | -116.9969 | 2021 | Conductor
OMD0000869134-01 | No Lights in Part-Just Started | 2021-11-14 16:15 | 2021-11-14 13:28 | 2021-11-14 13:42 | N | N | N | N | Y | Arching/Charring |  | 120 V | Other/Undetermined | SPLICE ON SVC-BAD CONN. | Weather Damaged Service | 310-495 | Transformer | 75 | MIDSPAN | 310 | CHANGE OUT 8FT #6 SSC SVC WIRE FROM MIDSPAN TO WEATHER HEAD, | 51977 Lopez, Oscar (I) | INACTIVE T | SUBMITTED DAF-REQUESTED O/H CREW O/ | 33.4725 | -117.693 | 2021 | Conductor
OMD0000869398-01 | No Lights - Cause Unknown | 2021-11-16 05:34 | 2021-11-16 03:41 | 2021-11-16 04:44 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Weather Damaged Device | 156-1335 | Transformer | 25 | p85410 | 156 | change out cutout & door | 05449 Bauers, Danny (I) | INACTIVE T | DAF COMPLETED bad cutout & door |  |  | 2021 | Non Conductor
OMD0000875835-01 | Dmg Dim/Nolite - Flash or Sparks | 2021-12-14 12:01 | 2021-12-14 09:09 | 2021-12-14 10:19 | N | N | N | N | N | Arching/Charring |  | 120 V | Other/Undetermined | BSD SVC INSULATION | Weather Damaged Service | 1073-172 | Transformer | 50 |  | 1073 | CHANGE OUT SECONDARY FROM P220008J TO MIDSPAN & FROM MIDSPAN | 51977 Lopez, Oscar (I) | INACTIVE T | SUBMITTED DAF - O/H CREW TO CHG OUT | 33.4794 | -117.6887 | 2021 | Conductor
OMD0000901866-01 | Dmg/Wlite-Flash or Sparks | 2022-04-07 20:59 | 2022-04-07 18:33 | 2022-04-07 18:44 | Y | N | Y | N | N |  |  | 120 V | Electric Facility |  | Connector Damaged | 303-669 | Transformer | 25 | P126133J | 303 | HEY KEVIN , I'LL SEND YOU AN EMAIL | 00638 Olson, Robert (I) | INACTIVE T | SENT FOLLOW UP TO DISTRICT | 33.1591 | -117.3237 | 2022 | Non Conductor
OMD0000911753-01 | Dmg Dim/Nolite-Wire Down P to P | 2022-05-20 10:05 | 2022-05-20 07:29 | 2022-05-20 08:01 | Y | N | N | N | N | Arching/Charring |  | 240 V | Other/Undetermined | BAD INSULATION ON OLD SVC | Weather Damaged Service | 792-154 | Transformer | 25 |  | 792 | O/H MIDSPAN SVC CHANGE OUT OR IF POSIBLE SPLICE-MEET WITH FO | 51977 Lopez, Oscar (I) | INACTIVE T | SUBMITTED DAF -CREW FALLOW UP TO RE | 33.4605 | -117.6583 | 2022 | Conductor
OMD0000930260-01 | Emer-Specl Req - Fire/Police/Govt | 2022-08-03 21:12 | 2022-08-03 15:13 | 2022-08-03 15:37 | Y | N | N | Y | N | Arching/Charring | 12 kV |  | Vegetation Contact | TREE BRANCH FELL OVER PRI CONDUCTORS | Foreign Object Contacted Wire | 1073-308 | Transformer | 50 | P129443 | 1073 | GET PRI WIRE UP FROM P129443 TO P220035 AND 2 POLES IN BETWE | 51977 Lopez, Oscar (I) | INACTIVE T | WIRE DOWN FROM P129443 TO P220035,4 | 33.4796 | -117.6665 | 2022 | Veg
OMD0000931714-01 | Emer-Specl Req - Fire/Police/Govt | 2022-08-10 13:55 | 2022-08-10 13:55 | 2022-08-10 13:55 | N | N | N | N | Y | Arching/Charring | 12 kV | 120 V | Other/Undetermined | LEAVES INSIDE VAULT...NOT SDGE EQUIP... | Vandalism | 794-180 | Transformer | 75 |  | 794 | CLEAN DEBRI & AROUND SUB TRASFORMER THAT IN MAN HOLE,STA 794 | 51977 Lopez, Oscar (I) | INACTIVE T | COMPLETED BY MACIAS... SOMEONE HAS | 33.4798 | -117.7001 | 2022 | Other All
OMD0000933647-01 | Emer-Specl Req - Fire/Police/Govt | 2022-08-18 20:25 | 2022-08-18 19:39 | 2022-08-18 19:55 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | Bad connection | Heat Device/Overload | 257-483 | Transformer | 37.5 | p283673 | 257 | C/O DISCONNECT SWITCH NORTH SIDE ( SINGLE SIDE) GLOWING AT L | 05449 Bauers, Danny (I) | INACTIVE T | DAF COMPLETED C/O DISCONNECT SWITCH | 32.6364 | -117.0832 | 2022 | Non Conductor
OMD0000933971-01 | Emer-Specl Req - Fire/Police/Govt | 2022-08-19 18:57 | 2022-08-19 17:32 | 2022-08-19 17:54 | N | N | N | N | N | Arching/Charring |  |  | Contact by Object | mylar balloon contacted guy wire & 69kv | Customer Restored | 723-124 | Transformer | 150 | z281468 | 723 |  | 05449 Bauers, Danny (I) | INACTIVE T | per cv fd- pd officer seen mylar ba | 32.5759 | -117.0799 | 2022 | Balloon
OMD0000939235-01 | Transformer Outage | 2022-09-05 19:57 | 2022-09-05 17:18 | 2022-09-05 17:46 | Y | N | N | N | N | Arching/Charring |  | 120 V | Other/Undetermined | LOAD | Weather Damaged Connector | 796-799 | Transformer | 50 | 3312 SEC BOX | 796 | CHG OUT BURNT MOLDS SH776980 ALSO CHG OUT BURNT SERVICES AS | 51977 Lopez, Oscar (I) | INACTIVE T | CREW TO CHG OUT MOLDS IN SH776980 & | 33.5322 | -117.7056 | 2022 | Non Conductor
OMD0000941990-01 | Branch Outage | 2022-09-12 18:30 | 2022-09-12 13:38 | 2022-09-12 14:10 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Weather Damaged Connector | 314-43F | Switch Position |  | M4955356304 | 314 |  | 51977 Lopez, Oscar (I) | INACTIVE T | ASSISTED MR MACIAS,DOSHIER,F/V & FO | 33.5243 | -117.6854 | 2022 | UG Switch
OMD0000944737-01 | Non Outage Order | 2022-09-22 19:25 | 2022-09-22 18:00 | 2022-09-22 18:00 | N | N | N | N | N |  |  | 240 V | Electric Facility |  | Moter Vehicle Contact with Pole | 325-198 | Transformer | 25 | P187596 | 325 | REPLACE POLE & SERVICE | 05449 Bauers, Danny (I) | INACTIVE T | CauseMA67 - Motor Vehicle Contact w | 32.6697 | -117.0503 | 2022 | Vehicle
OMD0000958466-01 | Flickering Lights-Just Started | 2022-11-17 18:12 | 2022-11-17 15:47 | 2022-11-17 16:05 | N | N | N | N | Y | Arching/Charring |  | 120 V | Other/Undetermined | LOOSE CONN | Weather Damaged Connector | 310-83 | Transformer | 75 | P220425 | 310 | DE-ENERGIZE STA,REPLACE 500 THW SEC LEADS & CHANGE OUT HOT C | 51977 Lopez, Oscar (I) | INACTIVE T | SUBMITTED DAF - FOUND HOT CONN. ON | 33.4639 | -117.6989 | 2022 | Non Conductor
OMD0001012335-01 | Circuit Outage | 2023-06-08 11:34 | 2023-06-08 07:57 | 2023-06-08 08:31 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Weather Damaged Connector | BD-12KV-1160 | Circuit |  | h116651 | 1160 |  | 05449 Bauers, Danny (I) | INACTIVE T |  | 32.5603 | -116.9571 | 2023 | UG Connector
PSTL2US1N7U | Transmission Switching | 2022-06-10 13:46 | 2022-06-10 10:28 | 2022-06-10 11:09 | Y | N | N | N | N |  |  |  | Electric Facility |  |  | SWI680-1 | Switch |  | Z114496 | SWI6 |  | 00638 Olson, Robert (I) | INACTIVE T |  |  |  | 2022 | Undetermined
OMD0000644321-01 | Branch Outage | 2019-07-15 04:05 | 2019-07-15 | 2019-07-15 00:29 | Y | N | N | N | N | Actual Ignition | 12 kV |  | Electric Facility |  | Heat Device/Overload | F13774 | Fuse | 100A | P839697 | 158 | BURNT OPEN CUTOUT | 68054 Piraino, John | ME O&E SUP | BAD CUTOUT DOOR | 32.5832 | -117.1094 | 2019 | Non Conductor
OMD0000647578-01 | Single No Light | 2019-07-27 11:47 | 2019-07-27 09:32 | 2019-07-27 10:16 | N | N | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | heat damage to meter clip ..cust panel | Customer Problem | 179-97 | Transformer | 75 |  | 179 | BURNT METER CLIP CUST PANEL...JUMPPERED OUT 480 PANEL FEEDIN | 68054 Piraino, John | ME O&E SUP | JUMMPERD OUT TEST BLOCKS , PANEL FE | 32.7237 | -117.1734 | 2019 | Non Conductor
OMD0000653579-01 | Emer-Specl Req - Fire/Police/Gov | 2019-08-19 18:27 | 2019-08-19 18:18 | 2019-08-19 18:18 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | INLINE DISCONNECT FLASHED OVER | Heat Device/Overload | 366-109 | Transformer | 50 | P737418 | 366 | FLASHED OVER CON AT INLINE DISCONNECT PROPERTY SIDE..NEED TO | 68054 Piraino, John | ME O&E SUP | SENT DAF XOUT INLINE DISCON C366... | 32.7526 | -117.1076 | 2019 | Non Conductor
OMD0000758219-01 | Branch Outage | 2020-09-06 18:21 | 2020-09-06 16:49 | 2020-09-06 17:24 | N | N | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | heat or overload of step down station | Weather Damaged Transformer | F102728 | Fuse | 75A | d137072 | 59 | overloaded and leaking 12kv station 59-mu1 | 00108 Alvarez, Marco | CM O&E SUP |  | 32.8277 | -117.2568 | 2020 | UG Fuse
OMD0000911143-01 | Emer-Specl Req - Fire/Police/Govt | 2022-05-18 03:39 | 2022-05-18 02:21 | 2022-05-18 02:22 | N | N | N | Y | N |  | 12 kV |  | Electric Facility | MYLARS STARTED 40X40 FIRE..R,O 2266 NATIONAL AVE..SDFD PUT OUT..(BRUSH FIRE ) IN YARD | Foreign Object Contact Conductor | 80-306 | Transformer | 75 | P1940472683 | 80 | BRUSH FIRE STARTED R/O 2266 NATIONAL AVE @ P1940472683 FROM | 68054 Piraino, John | ME O&E SUP | MYLARS CAUSED 40/40 BRUSH FIRE AND | 32.6969 | -117.1386 | 2022 | Balloon
OMD0001138432-01 | Branch Outage | 2024-10-04 16:23 | 2024-10-04 13:07 | 2024-10-04 15:17 | N | N | N | N | N |  | 12 kV | 240 V | Contact by Object | Giant Shade Structure flew into primary. Fire department had the fire out by the time i arrived | Conductor Damaged | 445-39R | Recloser |  |  | 445 |  | C5862 Ginkel, Robert | ME O&E SUP | Large shade structure blew into bot | 32.664 | -116.2733 | 2024 | Other Contact
ADV1000000000006612 | Emer-Specl Req - Fire/Police/Gov | 2020-02-05 14:20 | 2020-02-05 13:36 | 2020-02-05 14:13 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | THE POLE WAS IN A PARKING LOT AND NOTHING HIT THE GROUND | Weather Damaged Connector | UNKNOWN | Switch |  | P235908 |  |  | 01826 Fowley, Jack | NC O&E SUP | CREW TO CHANGE OU 160" OF CABLE FRO | 33.073 | -117.3055 | 2020 | Non Conductor
ADV1000000000096994 | FIRE AT POLE | 2021-08-21 21:52 | 2021-08-21 21:46 | 2021-08-21 21:51 | N | N | N | N | N | Arching/Charring |  | 240 V | Other/Undetermined | WOODEN SHED AT 110 S.CLEMENTINE ST OCEANSIDE WAS INGULFED & FLAMES REACHED & DAMAGED #4SSC CU SVC WIRE ABOVE SHED | Service Down |  |  |  | P20456 | 580 | SHED FIRE DAMAGED #4SSC CU SERVICE TO 110 S.CLEMENTINE ST (B | 30566 Garegnani, Dominic | NC O&E SUP | SERVICE TO 110 S.CLEMENTINE ST. WAS |  |  | 2021 | Other All
OMD0000758246-01 | Branch Outage | 2020-09-06 19:20 | 2020-09-06 18:21 | 2020-09-06 18:33 | N | N | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | hole in the station | Weather Damaged Device | 114-18AE | Switch |  | d2378269730 | 114 | station 114-90 leaked all oil out and blew up | 00108 Alvarez, Marco | CM O&E SUP |  | 32.8179 | -117.232 | 2020 | UG Switch
OMD0000645518-02 | Dmg/Wlite-Tree Burning in Wires | 2019-07-19 16:30 | 2019-07-19 15:46 | 2019-07-19 15:55 | N | N | N | N | N | Arching/Charring | 12 kV |  | Vegetation Contact |  | Tree Damaged Conductor | 65-496 | Transformer | 50 |  | 65 |  | 23123 Domnitz, Jared | NC O&E SUP | ASSISTED MIKE WITH BAMBOO IN THE 12 | 32.8509 | -117.238 | 2019 | Veg
OMD0000760841-01 | No Lights - Cause Unknown | 2020-09-14 16:09 | 2020-09-14 14:40 | 2020-09-14 15:11 | N | N | N | N | N | Arching/Charring |  | 208 V | Electric Facility | melted secondary lugs in ug transformer - sta.284-167 | Connector Damaged | 284-167 | Three Phase Transformer | 225 | D3241569064 | 284 | BURNT SECONDARY LUGS "C"PHASE AT STA. 284-167 - | 30566 Garegnani, Dominic | NC O&E SUP | BURNT SECONDARY LUGS (CPHASE) AT ST | 33.0496 | -117.2592 | 2020 | UG Connector
OMD0000645743-01 | Dmg Dim/Nolite - Flash or Sparks | 2019-07-21 13:37 | 2019-07-21 11:55 | 2019-07-21 12:12 | Y | N | N | N | N | Arching/Charring |  | 120 V | Other/Undetermined | LOOSE METER CLIP | Customer Problem | 755-202 | Transformer | 25 |  | 755 |  | 01826 Fowley, Jack | NC O&E SUP | AN ELECTRICIAN WILL NEED TO FIX A M | 33.0948 | -117.2579 | 2019 | Non Conductor
OMD0000763018-01 | No Lights in Part-Just Started | 2020-09-22 16:41 | 2020-09-22 13:46 | 2020-09-22 13:46 | N | N | N | N | Y | Arching/Charring | 12 kV | 208 V | Other/Undetermined | Melted secondary lug in station... | Connector Damaged | 61-1437 | Three Phase Transformer | 300 | D102523 | 61 | Burnt open PS leg in station 61-1437 @ D102523... | 00832 Arevalo, Greg | NC O&E SUP | Damaged secondary lug inside of sta | 32.9326 | -117.2425 | 2020 | UG Connector
OMD0000646683-01 | Circuit Outage | 2019-07-24 17:18 | 2019-07-24 14:10 | 2019-07-24 17:01 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | QUALCOMM EQUIPMENT | Customer Problem | MTO-12KV-1442 | Circuit |  | U100065 | 1442 |  | 23123 Domnitz, Jared | NC O&E SUP | QUALCOMM SWITCH GEAR BLEW UP , THEI | 32.8947 | -117.196 | 2019 | Non Conductor
OMD0000646903-01 | Emer-Specl Req - Fire/Police/Gov | 2019-07-25 09:39 | 2019-07-25 08:16 | 2019-07-25 08:40 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | CUTOUT DOOR P25273 BURNT OPEN - NO PUBLIC FIRE DAMAGE - ISOLATED TO POLE | Weather Damaged Device | 303-649 | Transformer | 50 | P25273 | 303 |  | 30566 Garegnani, Dominic | NC O&E SUP | CUTOUT DOOR BURNT OPEN - P25273 - | 33.1577 | -117.3277 | 2019 | Non Conductor
OMD0000647572-01 | Flickering Lights-Just Started | 2019-07-27 01:35 | 2019-07-27 00:52 | 2019-07-27 01:08 | Y | N | N | N | N | Arching/Charring |  | 120 V | Other/Undetermined | CUSTOMER BREAKER IN METER PANEL | Customer Problem | 509-350 | Transformer | 25 |  | 509 |  | 30566 Garegnani, Dominic | NC O&E SUP | GOOD VLT AT CUST. MAIN BREAKER - CU | 33.1993 | -117.2622 | 2019 | Non Conductor
OMD0000648188-01 | Branch Outage | 2019-07-29 20:30 | 2019-07-29 20:24 | 2019-07-29 20:24 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | 25 amp smu fuse blew from bird contact 73-555 the fuse did not clear completly and burnt the door in half was arcing when i arrived. | Foreign Object in Transformer | F2191630 | Fuse | 25A | z272913 | 73 |  | 70169 Ransom, Ryan | NC O&E SUP | bird contact 73-555 | 32.7712 | -116.6814 | 2019 | Non Conductor
OMD0000649651-03 | Circuit Outage | 2019-08-04 07:36 | 2019-08-04 01:24 | 2019-08-04 07:35 | N | N | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | FAULTED 600A CONNECTIONS | Connector Damaged | BE-12KV-293 | Circuit |  |  | 293 |  | 07093 Lasua, Keoni | NC O&E SUP | BAD TEES |  |  | 2019 | Non Conductor
OMD0000650764-01 | Emer-Specl Req - Fire/Police/Gov | 2019-08-08 13:45 | 2019-08-08 12:20 | 2019-08-08 12:31 | Y | N | N | N | N | Arching/Charring |  | 240 V | Other/Undetermined | NO OBVIOUS CAUSE, I THINK SOMETHING DAMGED THE WIRE AT ONE TIME AND THE WIRE GOT HOT AND FAILED. | Service Deenergized For Safety | 712-66 | Transformer | 100 |  | 712 | O.H. SERVICE BURNED OPEN. | 23123 Domnitz, Jared | NC O&E SUP | SERVICE CAUGHT ON FIRE. DAMAGED. NE | 32.826 | -117.1468 | 2019 | Other All
OMD0000650806-01 | Emer-Specl Req - Fire/Police/Gov | 2019-08-08 16:04 | 2019-08-08 14:07 | 2019-08-08 15:16 | N | N | N | N | Y | Actual Ignition | 12 kV |  | Other/Undetermined | HOUSE FIRE | Company Shut-Off | 833-113 | Transformer | 75 |  | 833 |  | 07093 Lasua, Keoni | NC O&E SUP | HOUSE FIRE - REMOVED METER #5408486 | 32.959 | -117.2319 | 2019 | Other All
OMD0000651994-01 | Branch Outage | 2019-08-14 01:06 | 2019-08-13 22:05 | 2019-08-13 23:29 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | kearny cutout door burned open | Weather Damaged Device | F265466 | Fuse | 50A | P717239 | 68 |  | 73442 Rodman, Roland | NC O&E SUP | bad cutout door on P717239 , instal | 32.9739 | -117.1719 | 2019 | Non Conductor
OMD0000652181-01 | Flickering Lights-Just Started | 2019-08-14 18:28 | 2019-08-14 16:51 | 2019-08-14 18:21 | N | N | N | N | N | Arching/Charring |  | 120 V | Other/Undetermined | METER WAS SET INCORRECTLY - BURNT METER CLIP & METER STAB | Customer Problem | 305-381 | Transformer | 50 |  | 305 |  | 30566 Garegnani, Dominic | NC O&E SUP | CUST. HAS BAD TOP LEFT (LINE SIDE) | 33.025 | -117.2231 | 2019 | Non Conductor
OMD0000652557-01 | Emer-Specl Req - Fire/Police/Gov | 2019-08-15 20:47 | 2019-08-15 18:21 | 2019-08-15 18:21 | N | N | N | N | Y | Arching/Charring |  | 120 V | Other/Undetermined | house fire turned into brush fire melted the service drop. | Undetermined | 448-549 | Transformer | 15 | p45858 | 448 | need to remove service from pole 45858 sta 448-126. service | 70169 Ransom, Ryan | NC O&E SUP | house fire turned into brush fire m | 32.6466 | -116.423 | 2019 | Other All
OMD0000652734-02 | Branch Outage | 2019-08-16 16:35 | 2019-08-16 13:29 | 2019-08-16 13:29 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | TRUCK HIT DOWNGUY P162249 - SLAPPED WIRE TOGETHER AT P20548 (VERTICLE CONSTRUCTION) BLEW FUSES AT P25135 | Moter Vehicle Contact with Pole | F265074 | Fuse | 150A | P20548 | 289 | DOWN GUY HIT BY TRUCK P162249 - POLE TO SPLIT - NEED TEMP RE | 30566 Garegnani, Dominic | NC O&E SUP | TRUCK HIT DOWNGUY & ANCHOR P162249 | 33.0238 | -117.281 | 2019 | Non Conductor
OMD0000654331-01 | Transformer Outage | 2019-08-22 09:35 | 2019-08-22 09:13 | 2019-08-22 09:13 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility | TRACKHOE HIT ANCHOR ROD & SLAPPED SECONDARY TOGETHER - NO FIRE SPARKS ON CONDUCTOR | Moter Vehicle Contact with Pole | 303-397 | Transformer | 25 | P127313 | 303 |  | 30566 Garegnani, Dominic | NC O&E SUP | CONTRACTOR W/ TRACKHOE HIT ANCHOR A | 33.158 | -117.3311 | 2019 | Non Conductor
OMD0000654337-01 | Emer-Grn Bx Unlock/Open/Xpose Wi | 2019-08-22 09:11 | 2019-08-22 07:33 | 2019-08-22 07:52 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility | TRACKHOE HIT ANCHOR ROD & SLAPPED OPEN WIRE SECONDARY TOGETHER CAUSING SPARKS - NO FIRE CAUSE | Moter Vehicle Contact with Pole | 303-397 | Transformer | 25 | P127313 | 303 |  | 30566 Garegnani, Dominic | NC O&E SUP | CONTRACTOR W/ TRACKHOE HIT ANCHOR A | 33.158 | -117.3311 | 2019 | Non Conductor
OMD0000654339-01 | Emer-Specl Req - Fire/Police/Gov | 2019-08-22 09:13 | 2019-08-22 09:12 | 2019-08-22 09:12 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility | SECONDARY SLAPPED TOGETHER - HIT BY TRACKHOE | Moter Vehicle Contact with Pole | 303-496 | Transformer | 150 | P127312 | 303 |  | 30566 Garegnani, Dominic | NC O&E SUP | CONTRACTOR W/ TRACKHOE HIT ANCHOR A | 33.1589 | -117.3306 | 2019 | Non Conductor
OMD0000654709-01 | Transformer Outage | 2019-08-23 15:04 | 2019-08-23 12:35 | 2019-08-23 12:35 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility | TRUCK HIT OH SERVICE & BROKE IT - NO IGNITION ON GROUND | Motor Vehicle Contact Services | CD4-95 | Transformer | 50 | P22130 | CD4 | TRUCK HIT OVERHEAD SSC SERVICE TO APARTMENT COMPLEX - 100' # | 30566 Garegnani, Dominic | NC O&E SUP | LARGE TRUCK HIT SSC SERVCE TO 965 P | 33.1603 | -117.342 | 2019 | Vehicle
OMD0000654717-01 | Emer-Specl Req - Fire/Police/Gov | 2019-08-23 15:03 | 2019-08-23 15:03 | 2019-08-23 15:03 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility | TRUCK CLIPPED SERVICE WIRE & BROKE IT - NO IGNITION ON GROUND | Motor Vehicle Contact Services | CD4-95 | Transformer | 50 | P22130 | CD4 |  | 30566 Garegnani, Dominic | NC O&E SUP | LARGE TRUCK HIT SSC SERVCE TO 965 P | 33.1603 | -117.342 | 2019 | Vehicle
OMD0000655048-03 | Branch Outage | 2019-08-25 22:15 | 2019-08-25 20:08 | 2019-08-25 20:57 | N | N | N | N | N | Arching/Charring | 4 kV |  | Electric Facility | OVERLOAD | Heat Device/Overload | F103142 | Fuse | 200A | P838256 | VDN1 |  | 23123 Domnitz, Jared | NC O&E SUP | OVERLOAD | 32.8229 | -117.274 | 2019 | Non Conductor
OMD0000656670-01 | Emer-Specl Req - Fire/Police/Gov | 2019-08-30 20:48 | 2019-08-30 18:14 | 2019-08-30 19:02 | Y | N | Y | N | N | Actual Ignition |  |  | Other/Undetermined | SMALL BRUSH FIRES AT TWO DIFFERENT TRANSMISSION TOWERS. | Undetermined | 198-1019 | Transformer | 50 | Z223645 | 198 |  | 07093 Lasua, Keoni | NC O&E SUP | TWO SMALL BRUSH FIRES ON CAMP PENDL | 33.2335 | -117.37 | 2019 | Other All
OMD0000786321-01 | Branch Outage | 2020-12-17 17:28 | 2020-12-17 15:05 | 2020-12-17 15:05 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Contact by Object | dig in on cable from 3rd party | Dig-in Underground Cable | F129184 | Fuse | 150A | D195865 | 714 | Dig in of 3 phase cable | 05351 Henry, Matthew (I) | INACTIVE T | 3rd party dig in | 32.8096 | -117.1366 | 2020 | UG Other Contact
OMD0000657564-02 | Branch Outage | 2019-09-04 12:06 | 2019-09-04 08:38 | 2019-09-04 09:21 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | CLEARANCE PROBLEM P113367 - 2PHASES GETTING TOGETHER | Wire Line Problem | F588055 | Fuse | 60A | P113367 | 209 | 3" CLEARANCE BETWEEN LINE & BUCK ON P113367 CIR 209 | 30566 Garegnani, Dominic | NC O&E SUP | WIRE CLEARANCE PROB AT P113367 - SE | 33.2504 | -117.2307 | 2019 | Non Conductor
OMD0000658400-02 | Branch Outage | 2019-09-05 15:55 | 2019-09-05 15:05 | 2019-09-05 15:21 | N | N | N | N | N | Arching/Charring | 4 kV |  | Electric Facility | FUSE DOOR | Heat Device/Overload | F102571 | Fuse | 30A | P17021 | GN1 |  | 23123 Domnitz, Jared | NC O&E SUP | FUSE DOOR BURNED OPEN, REPLACED AND | 32.807 | -117.2371 | 2019 | Non Conductor
OMD0000659149-01 | No Lights in Part-Just Started | 2019-09-09 | 2019-09-08 21:41 | 2019-09-08 22:03 | N | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility | SLIGHTLY ARCING CU/CU 2BOLT SECONDARY NEUTRAL CONNECTION (LOOSE) | Connector Damaged | 512-133 | Transformer | 25 | P320609 | 512 |  | 30566 Garegnani, Dominic | NC O&E SUP | CUST. SYS WHOLE BUILDING AFFECTED - | 32.9889 | -117.2734 | 2019 | Non Conductor
OMD0000659814-01 | Transformer Outage | 2019-09-11 12:14 | 2019-09-11 10:20 | 2019-09-11 10:41 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | CORRODED KEARNY CUTOUT BURNT OPEN AT TOP DOOR CONTACT - CHARRED & MELTED CONTACT | Transformer Problem | 1076-198 | Transformer | 100 | P28705 | 1076 | BURNT OPEN CUTOUT ON 3PHASE BANK STA.1076-198 P28705 - BANK | 30566 Garegnani, Dominic | NC O&E SUP | FUSED CUTOUT BURNT OPEN AT CORRODED | 33.172 | -117.3588 | 2019 | Non Conductor
OMD0000660936-01 | No Lights - Cause Unknown | 2019-09-15 19:04 | 2019-09-15 18:28 | 2019-09-15 18:37 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility | HEAT DETECTED AT CUSTOMER MAIN BREAKER - SLIGHTLY HIGER THAN NOMAL | Customer Problem | 505-294 | Transformer | 25 | CUSTOMER PANEL | 505 |  | 30566 Garegnani, Dominic | NC O&E SUP | GOOD VOLTAGE AT CUSOTMER MAIN BREAK | 33.1762 | -117.2428 | 2019 | Non Conductor
OMD0000662388-01 | Emer-Specl Req - Fire/Police/Gov | 2019-09-21 13:33 | 2019-09-21 11:17 | 2019-09-21 12:23 | N | N | N | Y | N | Actual Ignition | 12 kV |  | Other/Undetermined | FIRE WAS AROUND OUR XFRMR, BUT WAS NOT CAUSED BY ANY SDGE EQUIPMENT. | Undetermined | 523-177 | Transformer | 150 |  | 523 |  | 07093 Lasua, Keoni | NC O&E SUP | FIRE WAS AROUND STATION 523-177, BU | 33.3729 | -117.2509 | 2019 | Other All
OMD0000667164-02 | Branch Outage | 2019-10-10 12:55 | 2019-10-10 12:52 | 2019-10-10 12:52 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | wire down to ground | Conductor Damaged | 448-33R | Recloser |  | p43500 | 448 |  | 70169 Ransom, Ryan | NC O&E SUP | wire broke outside of old splice | 32.6238 | -116.4766 | 2019 | Conductor
OMD0000667452-01 | Transformer Outage | 2019-10-11 12:27 | 2019-10-11 11:16 | 2019-10-11 11:30 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Connector Damaged | 288-968 | Transformer | 25 | Z24533 | 288 |  | 30566 Garegnani, Dominic | NC O&E SUP | BAD OVERARM JUMPER CONNECTION AT Z2 | 33.0381 | -117.2728 | 2019 | Non Conductor
OMD0000668141-01 | Emer-Specl Req - Fire/Police/Gov | 2019-10-15 05:27 | 2019-10-15 02:28 | 2019-10-15 02:56 | N | N | N | Y | N | Actual Ignition | 12 kV |  | Other/Undetermined | VEGEATION FIRE REQUESTED FOR STANDBY PER VISTA FIRE DEPARTMENT | Customer Restored | 205-476 | Transformer | 25 |  | 205 |  | 07093 Lasua, Keoni | NC O&E SUP | STAND BY FOR VISTA FIRE DEPARTMENT | 33.2094 | -117.2169 | 2019 | Veg
OMD0000669544-01 | Single No Light | 2019-10-19 17:17 | 2019-10-19 17:13 | 2019-10-19 17:13 | Y | Y | Y | Y | N | Actual Ignition |  | 240 V | Contact by Object | CUST. HIT CUST.METER POLE BROUGHT DOWN POLE & SVC WIRE - 2ACRE FIRE NO MAJOR DMG - TRIPPED SEC.BREAKER ON STA.901-1460 | Service Down | 901-1460 | Transformer | 15 | P219560 | 901 |  | 30566 Garegnani, Dominic | NC O&E SUP | RESIDENT HIT CUST. OWNED METER POLE | 33.2319 | -117.2594 | 2019 | Other Contact
OMD0000670720-01 | Branch Outage | 2019-10-24 14:25 | 2019-10-24 11:37 | 2019-10-24 11:37 | Y | N | N | N | N | Actual Ignition | 12 kV |  | Electric Facility |  | Device Damaged | F223 | Fuse | 30A | p377113 | 1458 | relpace fuses and bodys | 70169 Ransom, Ryan | NC O&E SUP | fuse door burnt in half causing 3x3 | 32.8356 | -116.7251 | 2019 | Non Conductor
OMD0000670734-01 | Emer-Specl Req - Fire/Police/Gov | 2019-10-24 14:27 | 2019-10-24 14:25 | 2019-10-24 14:25 | Y | N | N | N | N | Actual Ignition | 12 kV |  | Electric Facility |  | Device Damaged | 1458-398 | Transformer | 150 | p377113 | 1458 |  | 70169 Ransom, Ryan | NC O&E SUP | fuse holder burnt in half causing 3 | 32.8357 | -116.7258 | 2019 | Non Conductor
OMD0000672845-01 | Momentary Outage | 2019-10-30 16:06 | 2019-10-30 16:06 | 2019-10-30 16:06 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | POTHEAD CONNECTOR BURNT UP AT P222369 ARCED AND FLASHED | Connector Damaged | OS-12KV-1077 | Circuit |  | P222369 | 1077 |  | 30566 Garegnani, Dominic | NC O&E SUP | CABLE POT HEAD TERMINAL CONNECTION | 33.2189 | -117.3554 | 2019 | Non Conductor
OMD0000672852-01 | Branch Outage | 2019-10-30 15:56 | 2019-10-30 15:35 | 2019-10-30 15:35 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | CONNECTION ON CABLE TERMINAL (POT HEAD) POSSIBLY LOOSE & MELTED & FLASHED | Connector Damaged | 1077-15 | Switch |  | P222369 | 1077 | BURNT UP POT HEAD CONNECTION - CREW TO REPLACE CABLE TO PRIM | 30566 Garegnani, Dominic | NC O&E SUP | POT HEAD CONNECTION BURNT & FLASHED | 33.2184 | -117.3563 | 2019 | Non Conductor
OMD0000674880-01 | Emer-Specl Req - Fire/Police/Gov | 2019-11-06 22:50 | 2019-11-06 20:03 | 2019-11-06 20:15 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | NON-PORCELAIN 56 1/2 INSULATOR FAILED ON P23682 - IT BURNED,MELTED THEN CONDUCTOR FELL ON CROSSARM BURNING UP CROSSARM - NO OTHER FIRE WAS CAUSED (ONLY ON POLE) | Device Damaged | 512-214 | Transformer | 25 | P23682 | 512 | BURNT UP POLYMERE INSULATOR AND CROSSARM AT P23682 | 30566 Garegnani, Dominic | NC O&E SUP | POLYMERE - NON POCELAIN 56 1/2 INSU | 32.9951 | -117.275 | 2019 | Non Conductor
OMD0000676161-01 | Transformer Outage | 2019-11-12 13:57 | 2019-11-12 08:14 | 2019-11-12 09:16 | Y | N | Y | Y | N | Actual Ignition |  | 120 V | Electric Facility | OPEN WIRE SECONDARY(POSS CAUSED BY CORRODED & BROKEN TELCO GUY STRAND) WIRE CAME DOWN ON TELCO & MELTED AT&T WIRES CAUSING FIRE & BUNRED FENCE AT 1002 ALBERTA AVE | Wire Down | EOS2-248 | Transformer | 50 | P22213 | EOS2 | OPEN WIRE SECONDARY DOWN IN BACK YARDS - P22213 TO P22214 | 30566 Garegnani, Dominic | NC O&E SUP | SECONDARY OPEN WIRE DOWN BTWN P2221 | 33.1903 | -117.3698 | 2019 | Non Conductor
OMD0000676184-01 | Emer-Specl Req - Fire/Police/Gov | 2019-11-12 13:59 | 2019-11-12 13:57 | 2019-11-12 13:57 | Y | N | Y | N | N | Actual Ignition |  | 120 V | Electric Facility | OPEN WIRE SECONDARY BROKE P22213 TO P22214 - POSS. CAUSE WAS AT&T BROKE GUY STRAND | Wire Down | EOS2-248 | Transformer | 50 | P22213 | EOS2 |  | 30566 Garegnani, Dominic | NC O&E SUP |  | 33.1903 | -117.3698 | 2019 | Non Conductor
OMD0000677653-01 | Single No Light | 2019-11-17 06:31 | 2019-11-17 06:31 | 2019-11-17 06:31 | N | N | N | N | N | Arching/Charring |  | 480 V | Contact by Object | MOUSE GOT INTO CUSTOMER 480V METER PEDESTAL & FLASHED ACROSS BUS-WORK | Customer Problem | 312-669 | Three Phase Transformer | 150 | METER PEDESTAL | 312 |  | 30566 Garegnani, Dominic | NC O&E SUP | MOUSE GOT INTO 277/480V METER PEDES | 33.4958 | -117.7356 | 2019 | Animal
OMD0000678285-01 | Branch Outage | 2019-11-20 00:51 | 2019-11-19 17:31 | 2019-11-19 19:40 | Y | N | N | N | N | Actual Ignition | 12 kV |  | Other/Undetermined | Flat brace came unbolted and hit 12kv jumper. Rain caused it to track and catch on fire. Fire was on cross arm only. | Weather Damaged Device | F2181615 | Fuse | 75A | P774149 | 171 | C/O damaged x-arm | 02704 Martinez, Chris | NC O&E SUP |  | 33.2594 | -116.3762 | 2019 | Non Conductor
OMD0000678388-01 | Branch Outage | 2019-11-20 00:56 | 2019-11-19 21:37 | 2019-11-19 21:37 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | pole fire , most likely caused by rain and tracking insulators | Weather Damaged Pole | F469159 | Fuse | 150A | P20942 | 781 | pole fire, P20942 | 73442 Rodman, Roland | NC O&E SUP | pole fire P20942 , opened 3-150a f | 33.1502 | -117.3455 | 2019 | Non Conductor
OMD0000678592-01 | Branch Outage | 2019-11-20 11:32 | 2019-11-20 08:57 | 2019-11-20 09:21 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | POLETOP CAUGHT FIRE BETWEEN LINE/CUTOUT ARMS & TRANSFORMER BANK - POLE BURNT IN HALF - NO FIRE ON GROUND | Fire Damaged Pole | F614741 | Fuse | 60A | P167732 | 582 | POLE FIRE - POLE BURNT IN HALF - P167732- W/ STEP DOWN BANK | 30566 Garegnani, Dominic | NC O&E SUP |  | 33.201 | -117.3832 | 2019 | Non Conductor
OMD0000679030-01 | No Lights - Cause Unknown | 2019-11-21 10:27 | 2019-11-21 08:54 | 2019-11-21 09:07 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | Weather caused cut out body to track and burn up. | Weather Damaged Device | 521-499 | Transformer | 25 | P311445 | 521 |  | 02704 Martinez, Chris | NC O&E SUP |  | 33.3813 | -117.2328 | 2019 | Non Conductor
OMD0000679853-01 | Dmg Dim/Nolite - Tree on Wire | 2019-11-23 19:42 | 2019-11-23 18:57 | 2019-11-23 19:19 | N | N | N | N | N | Arching/Charring |  | 240 V | Vegetation Contact | NEOPRENE INSULATED SSC SERVICE IN PALM TREE ARCED & BURNT PS LEG & NEUTRAL OPEN- NO OTHER DMG | Open Neutral | 194-127 | Transformer | 25 | P129555 | 194 | #6 SSC SERVICE BURNT OPEN IN PALM TREE - 1PS & NEUTRAL OPEN | 30566 Garegnani, Dominic | NC O&E SUP | OH SSC SERVICE BURNT OPEN IN QUEEN | 33.2188 | -117.3392 | 2019 | Veg
OMD0000680349-01 | Flickering Lights-Just Started | 2019-11-25 19:58 | 2019-11-25 18:28 | 2019-11-25 18:40 | N | N | N | N | Y | Arching/Charring | 12 kV | 120 V | Electric Facility | Meter clip overheated causing meter & meter base to melt... | Heat Device/Overload | 205-874 | Transformer | 100 | #5427603 | 205 |  | 00832 Arevalo, Greg | NC O&E SUP | Flickering lights caused by overhea | 33.2085 | -117.2359 | 2019 | Non Conductor
OMD0000680394-01 | Branch Outage | 2019-11-25 23:40 | 2019-11-25 22:10 | 2019-11-25 22:10 | N | N | N | N | Y | Arching/Charring | 4 kV |  | Electric Facility |  | Heat Device/Overload | F614741 | Fuse | 60A | P167732 | 582 | Faulted OH stepdown @ P167732 & damaged cable ground @ P2088 | 00832 Arevalo, Greg | NC O&E SUP | Faulted 12 to 4 stepdown @ P167732 | 33.201 | -117.3832 | 2019 | Non Conductor
OMD0000680845-01 | Emer-Specl Req - Fire/Police/Gov | 2019-11-27 14:17 | 2019-11-27 11:42 | 2019-11-27 11:58 | N | N | N | Y | N | Actual Ignition | 12 kV | 480 V | Other/Undetermined | KITCHEN FIRE INSIDE RESTRUANT. STARTED BY CUSTOMER. | Customer Problem | 512-76 | Transformer | 500 |  | 512 |  | 07093 Lasua, Keoni | NC O&E SUP | KITCHEN FIRE INSIDE PAPPLEMOUSE GRI | 32.9811 | -117.2602 | 2019 | Other All
OMD0000680960-01 | Emer-Specl Req - Fire/Police/Gov | 2019-11-27 16:01 | 2019-11-27 13:40 | 2019-11-27 14:11 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | Customer stated arcing at transformer before fuse tripped burning and charring at bushings. | Weather Damaged Device | 289-351 | Three Phase Transformer | 150 | p122702 | 289 | 3 Phase bank failure 289-154 @ P122702. Center fuse blown. | 02734 Willis, Brian | NC O&E SUP | 3 phase bank failure 289-154 @ P122 | 33.0392 | -117.2932 | 2019 | Non Conductor
OMD0000680961-01 | Emer-Specl Req - Fire/Police/Gov | 2019-11-27 14:19 | 2019-11-27 14:17 | 2019-11-27 14:17 | N | N | N | Y | N | Actual Ignition | 12 kV | 480 V | Other/Undetermined | KITCHEN FIRE CAUSED BY CUSTOMER | Customer Restored | 512-76 | Transformer | 500 |  | 512 |  | 07093 Lasua, Keoni | NC O&E SUP | KITCHEN FIRE INSIDE PAPPLEMOUSE GRI | 32.9811 | -117.2602 | 2019 | Other All
OMD0000680964-01 | Emer-Specl Req - Fire/Police/Gov | 2019-11-27 14:20 | 2019-11-27 14:19 | 2019-11-27 14:19 | N | N | N | Y | N | Actual Ignition | 12 kV | 480 V | Other/Undetermined | KITCHEN FIRE CAUSED BY CUSTOMER | Customer Restored | 512-76 | Transformer | 500 |  | 512 |  | 07093 Lasua, Keoni | NC O&E SUP | KITCHEN FIRE INSIDE PAPPLEMOUSE GRI | 32.9811 | -117.2602 | 2019 | Other All
OMD0000680967-01 | Emer-Specl Req - Fire/Police/Gov | 2019-11-27 14:21 | 2019-11-27 14:20 | 2019-11-27 14:20 | N | N | N | Y | N | Actual Ignition | 12 kV | 480 V | Other/Undetermined | KITCHEN FIRE CAUSED BY CUSTOMER | Customer Restored | 512-76 | Transformer | 500 |  | 512 |  | 07093 Lasua, Keoni | NC O&E SUP | KITCHEN FIRE INSIDE PAPPLEMOUSE GRI | 32.9811 | -117.2602 | 2019 | Other All
OMD0000681449-01 | Emer-Specl Req - Fire/Police/Gov | 2019-11-28 22:25 | 2019-11-28 21:37 | 2019-11-28 21:37 | Y | N | Y | N | N | Actual Ignition |  | 240 V | Electric Facility | NEOPRENE INSULATED SSC SERVICE WIRE BURNT DOWN WHEN RAIN CAUSED CRACKED INSULATION TO GO TO GROUND AT MESSENGER & BURN DOWN SEVICE | Service Down | 362-110 | Transformer | 50 | P73815 | 362 | OH #6SSC SERVICE BURNT OPEN & CAME DOWN - P73815 TO HOUSE - | 30566 Garegnani, Dominic | NC O&E SUP | NEOPRENE INSULATED #6SSC SERVICE BU | 32.7664 | -117.1256 | 2019 | Conductor
OMD0000681789-01 | Dmg/Wlite-Flash or Sparks | 2019-11-29 22:06 | 2019-11-29 20:00 | 2019-11-29 20:23 | N | Y | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Heat Device/Overload | 1076-153 | Transformer | 75 | P21173 | 1076 | I jumpered out A phase on cir 1076 @ P21173 solid door. Chan | 00832 Arevalo, Greg | NC O&E SUP | A phase cutout on P21173 was damage | 33.1748 | -117.3662 | 2019 | Non Conductor
OMD0000681902-01 | Dmg/Wlite-Wire Down Pole to Pole | 2019-11-30 15:38 | 2019-11-30 12:46 | 2019-11-30 12:46 | N | N | N | N | N | Arching/Charring | 12 kV |  | Vegetation Contact | ANCHOR ROD RUSTED & PULLED UP AT P13030 CAUSING WIRE TO DIP INTO TREES - NO FIRE BUT BURNING ON CONDUCTORS | Weather Damaged Pole | 305-175 | Transformer | 75 | P13030 | 305 | ANCHOR ROD RUSTED & PULLED UP - POLE GOING OVER PRIMAY IN TR | 30566 Garegnani, Dominic | NC O&E SUP | P13030 ANCHOR ROD PULLED UP & POLE | 33.0251 | -117.2083 | 2019 | Other All
OMD0000685393-01 | No Lights in Part-Just Started | 2019-12-11 15:50 | 2019-12-11 15:01 | 2019-12-11 15:22 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility | NEOPRENE INSULATED SERVICE FAILED MID-SPAN (PS LEG OPEN) & WENT TO GROUND (NEUTRAL WIRE | Weather Damaged Service | 303-841 | Transformer | 25 | P220278 | 303 | DAMAGED OH SSC SERVICE - NEOPRENE INSULATED SERVICE HAS OPEN | 30566 Garegnani, Dominic | NC O&E SUP | OH #6SSC CU NEOPRENE SERVICE HAS OP | 33.1546 | -117.3281 | 2019 | Conductor
OMD0000799651-01 | Emer-Specl Req - Fire/Police/Gov | 2021-02-03 15:32 | 2021-02-03 13:27 | 2021-02-03 13:57 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility | STRUCTURE FIRE - SERVICE & PANEL BURNT- LOOKS LIKE IT WAS STARTED AWAY FROM PANEL BUT THEN ENGULFED - BLEW FUSE AT STA.486-727 D100576 | Fuse Operated in Transformer | 486-727 | Transformer | 25 | D100576 | 486 | FIRE AT 820 ARTHUR AVE DAMAGED UG SERVICE AT PANEL & XFMR FU | 30566 Garegnani, Dominic | NC O&E SUP | STRUCTURE FIRE AT 820 ARTHUR AVE CA | 33.2629 | -117.2908 | 2021 | Other All
OMD0000799934-01 | Emer-Grn Bx Unlock/Open/Xpose Wi | 2021-02-04 13:14 | 2021-02-04 11:22 | 2021-02-04 11:35 | N | Y | N | N | N | Arching/Charring | 12 kV | 208 V | Other/Undetermined | Vehicle hit transformer... | Motor Vehicle Contact with Xfmr | 288-571 | Three Phase Transformer | 300 | D3212169909 | 288 | Car hit station 288-571 @ D3212169909... | 00832 Arevalo, Greg | NC O&E SUP | Car hit station 288-571 @ D32121699 | 33.0452 | -117.2593 | 2021 | UG Vehicle
OMD0000688052-01 | Flickering Lights-Just Started | 2019-12-19 21:06 | 2019-12-19 20:08 | 2019-12-19 20:29 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility | CUST. MAIN BREAKER HOT & ARCING INSIDE PANEL | Customer Problem | 904-134 | Transformer | 75 | house | 904 |  | 30566 Garegnani, Dominic | NC O&E SUP | CUST HAS FLKRING LITES - CUSTOMER M | 33.2193 | -117.3049 | 2019 | Non Conductor
OMD0000688659-01 | Emer-Specl Req - Fire/Police/Gov | 2019-12-23 04:25 | 2019-12-23 00:20 | 2019-12-23 01:47 | N | N | N | Y | N | Actual Ignition | 12 kV |  | Other/Undetermined | HOUSE FIRE CAUSE UNKNOWN | Company Shut-Off | 286-186 | Transformer | 50 |  | 286 |  | 07093 Lasua, Keoni | NC O&E SUP | HOUSE FIRE...CAUSE UNKNOWN, STILL U | 33.0731 | -117.3081 | 2019 | Other All
OMD0000688853-01 | Flickering Lights-Just Started | 2019-12-23 14:15 | 2019-12-23 13:23 | 2019-12-23 13:40 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility | CUSTOMER NEUTRAL BUS CONNECTIONS TOTALLY CORRODED & PANEL NEEDS REPLACEMENT - ARCING HEARD ON NEUTRAL BUS | Customer Problem | 580-630 | Transformer | 50 | Panel | 580 | CUST. NEUTRAL CONNECTION IN TEST BLOCK SECTION & MAIN BREAKE | 30566 Garegnani, Dominic | NC O&E SUP | CUST. LTS FLKRING - GOOD VLTG W/LOA | 33.1927 | -117.3762 | 2019 | Non Conductor
OMD0000691546-01 | Emer-Specl Req - Fire/Police/Gov | 2020-01-03 18:35 | 2020-01-03 17:06 | 2020-01-03 18:30 | Y | N | N | Y | N | Actual Ignition | 12 kV |  | Other/Undetermined | ROOFING CONTRACTORS CAUSED HOUSE FIRE | Company Shut-Off | 757-211 | Transformer | 50 |  | 757 |  | 07093 Lasua, Keoni | NC O&E SUP | CUSTOMER'S ATTIC AND ROOF WAS ON FI | 33.106 | -117.2473 | 2020 | Other All
OMD0000691582-01 | Emer-Specl Req - Fire/Police/Gov | 2020-01-03 22:44 | 2020-01-03 20:51 | 2020-01-03 22:39 | N | N | N | Y | N | Actual Ignition | 4 kV |  | Other/Undetermined | HOUSE FIRE CAUSE UNKNOWN | Service Deenergized For Safety | EN1-117 | Transformer | 25 |  | EN1 |  | 07093 Lasua, Keoni | NC O&E SUP | FIRE AT 470 ARROYO DR, ENCINITAS | 33.0514 | -117.2919 | 2020 | Other All
OMD0000799931-01 | Branch Outage | 2021-02-04 13:16 | 2021-02-04 13:14 | 2021-02-04 13:14 | N | Y | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | Car hit transformer ... | Motor Vehicle Contact with Xfmr | LBE.244597 |  |  | D3212169909 | 288 |  | 00832 Arevalo, Greg | NC O&E SUP | Car hit station 288-571 @ D32121699 | 33.0452 | -117.2593 | 2021 | UG Vehicle
OMD0000697614-01 | No Lights in Part-Just Started | 2020-01-29 14:57 | 2020-01-29 13:51 | 2020-01-29 14:07 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility | BAD CUSTOMER OWNED TEST BLOCK CONNECTON IN PANEL - CUST TO REPLACE PANEL - ETS TIGHTENED CONNECTION & IS OK FOR TEP | Customer Problem | 286-784 | Transformer | 50 | CUST. PANEL | 286 | FYI.... AUTO ZONE AUTO PART STORE - COMMERCIAL 200AMP 240V | 30566 Garegnani, Dominic | NC O&E SUP | CUST. HAD 1/2 PWR - COMMERCIAL 200A | 33.0647 | -117.301 | 2020 | Non Conductor
OMD0000699391-01 | Branch Outage | 2020-02-05 14:55 | 2020-02-05 13:56 | 2020-02-05 13:56 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | OVERHEAD POT-HEAD CABLE TERMINATION & CABLE BURNT JUST BELOW PORCELAIN POTHEAD - FIRE WAS ONLY ON THE CABLE & POTHEAD DID NOT CAUSE ANY OTHER DAMAGE TO POLE/ CROSSARM OR PRIVATE PROP | Conductor Damaged | F402331 | Fuse | 30A | P235908 | 286 | P235908 - BURNT POTHEAD & CABLE - FEEDS STA286-498 - 160' #2 | 30566 Garegnani, Dominic | NC O&E SUP | OVERHEAD PRIMARY TERMINATION POTHEA | 33.073 | -117.3055 | 2020 | OH to UG
OMD0000699394-01 | Emer-Specl Req - Fire/Police/Gov | 2020-02-05 14:57 | 2020-02-05 14:55 | 2020-02-05 14:55 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | 12KV POTHEAD TERMINATION CAUGHT FIRE ON THE CABLE JUST BELOW THE TERMINATOR - NO DAMAGE TO PRIVAT PROPERTY OR POLE | Connector Damaged | UNKNOWN | Switch |  | P235908 |  | BURNT POTHEAD P235908 - DUP DAF | 30566 Garegnani, Dominic | NC O&E SUP | OVERHEAD PRIMARY TERMINATION POTHEA | 33.073 | -117.3055 | 2020 | OH to UG
OMD0000711801-01 | Dmg/Wlite-Explosion | 2020-03-27 14:33 | 2020-03-27 10:08 | 2020-03-27 10:27 | N | N | N | N | N | Arching/Charring | 12 kV |  | Contact by Object | VEHICLE OR EQUIPMENT HIT TELEPHONE CABLE & BROKE P217874 (UNMAPPED) 2W 3SPANS WIRE DOWN - NO FIRE BUT EVEDENCE OF SPARKS ON WIRE | Moter Vehicle Contact with Pole | 783-933 | Three Phase Transformer | 150 | P217874 | 783 | POLE BROKE/ WIRE DOWN 2W 3SPANS - P251002 TO P217875 | 30566 Garegnani, Dominic | NC O&E SUP | VEHICLE OR EQUIPMENT CONTACT WITH T | 33.1513 | -117.3075 | 2020 | Vehicle
OMD0000713777-01 | No Lights in Part-Just Started | 2020-04-04 12:40 | 2020-04-04 09:16 | 2020-04-04 09:35 | N | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility | BAD SECONDARY ALUMINUM TO COPPER CONNECTION AT P31140 - TAPE MELTED ON CONNECTION | Conductor Damaged | 233-68 | Transformer | 25 | P31140 | 233 |  | 30566 Garegnani, Dominic | NC O&E SUP | DEAD LEG AT 400AMP PANEL - BAD AL/ | 33.2655 | -117.222 | 2020 | Conductor
OMD0000799931-02 | Branch Outage | 2021-02-04 13:19 | 2021-02-04 11:29 | 2021-02-04 12:49 | N | N | N | N | Y | Actual Ignition | 12 kV | 208 V | Contact by Object | truck hit transformer 288-571 causing a fire to transformer & truck, fire put out by fire dept | Motor Vehicle Contact with Xfmr | LBE.244597 |  |  | D3212169909 | 288 |  | 23170 Doshier, Richard | OC O&E SUP | crew enroute to replace transformer | 33.0452 | -117.2593 | 2021 | UG Vehicle
OMD0000714076-01 | Branch Outage | 2020-04-06 13:31 | 2020-04-06 13:31 | 2020-04-06 13:31 | N | N | N | N | Y | Actual Ignition | 12 kV |  | Vegetation Contact | PALM FROND BLEW ACROSS PRIMARY NEUTRAL & 12KV PHASE P22035 TO P22009 - WIRE BURNT DOWN 1W - 1SPAN PRI NEUT. - BURNING FROND EXTIGUISHED IN RAIN | Palm Frond On Conductor | F468271 | Fuse | 100A | P22035 | 303 | PRI NEUTRAL WIRE DOWN P22035 TO P22009 - 1W 1SPAN & BAD CUTO | 30566 Garegnani, Dominic | NC O&E SUP | PALM FROND BLEW ACROSS PRIMARY NEUT | 33.1516 | -117.3373 | 2020 | Veg
OMD0000714484-01 | Dmg/Wlite-Flash or Sparks | 2020-04-07 14:33 | 2020-04-07 13:22 | 2020-04-07 14:10 | N | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility | CUSTOMER OWENED EXTERNAL ROMEX OVERHEAD WIRE SMOKING & ARCING - BREAKER IS OFF & OWNER WILL HAVE TO REPLACE & BRING WIRING TO CODE | Customer Problem | 1076-247 | Transformer | 25 | CUSTOMER HOUSE | 1076 |  | 30566 Garegnani, Dominic | NC O&E SUP | CUSTOMER OWNED OVERHEAD ROMEX WIRE | 33.1789 | -117.3617 | 2020 | Non Conductor
OMD0000715071-01 | Emer-Specl Req - Fire/Police/Gov | 2020-04-09 19:41 | 2020-04-09 14:15 | 2020-04-09 15:02 | Y | N | N | N | N | Arching/Charring | 4 kV |  | Electric Facility |  | Weather Damaged Connector | ELS1-75 | Transformer | 50 | M3140770173 | ELS1 | Damaged lineside connection to switch feeding station ELS1-7 | 00832 Arevalo, Greg | NC O&E SUP | Faulted connection in M3140770173 c | 33.0205 | -117.2184 | 2020 | UG Connector
OMD0000715547-01 | Branch Outage | 2020-04-10 20:45 | 2020-04-10 19:46 | 2020-04-10 19:46 | Y | N | N | N | N | Arching/Charring | 4 kV |  | Other/Undetermined | Primary wire down arcing & sparking in customers front yard = 855 Dewitt st... | Weather Damaged Conductor | F401486 | Fuse | 125A | P25790 | EN1 |  | 00832 Arevalo, Greg | NC O&E SUP | Primary wire down from P25790 to P2 | 33.0435 | -117.2909 | 2020 | Conductor
OMD0000715578-01 | Branch Outage | 2020-04-10 20:49 | 2020-04-10 20:45 | 2020-04-10 20:45 | N | N | N | N | Y | Arching/Charring | 4 kV |  | Vegetation Contact | Energized primary phase in front yard of 855 Dewitt st... | Weather Damaged Conductor | <inline_jumper.13558> |  |  | P25790 | EN1 |  | 00832 Arevalo, Greg | NC O&E SUP | Primary wire down from P25790 to P2 | 33.0411 | -117.2905 | 2020 | Veg
OMD0000716549-01 | Transformer Outage | 2020-04-14 17:29 | 2020-04-14 15:40 | 2020-04-14 15:40 | N | N | N | N | N | Arching/Charring | 12 kV | 480 V | Electric Facility | TRANSFORMER FAILED BLOWING FUSE & EJECTING OIL OUT OF PRESSURE RELIEF VALVE | Fuse Operated in Transformer | 486-2071 | Transformer | 150 | P512530 | 486 | BAD 3PHASE BANK 486-2071- 480V OVERHEAD W/CORNER GROUND - 3- | 30566 Garegnani, Dominic | NC O&E SUP | STA.486-2071 FAILED - CREW TO REPLA | 33.2665 | -117.2701 | 2020 | Non Conductor
OMD0000717603-01 | Emer-Specl Req - Fire/Police/Gov | 2020-04-18 20:45 | 2020-04-18 19:11 | 2020-04-18 19:30 | N | N | N | N | Y | Actual Ignition | 12 kV |  | Other/Undetermined | HOUSE FIRE. NO SDGE EQUIPMENT INVOLVED. | Customer Problem | 289-387 | Transformer | 50 |  | 289 |  | 07093 Lasua, Keoni | NC O&E SUP |  | 33.0281 | -117.2858 | 2020 | Other All
OMD0000799935-01 | Emer-Specl Req - Fire/Police/Gov | 2021-02-04 13:23 | 2021-02-04 13:16 | 2021-02-04 13:16 | N | Y | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | Car hit transformer 288-571 | Motor Vehicle Contact with Xfmr | 288-571 | Three Phase Transformer | 300 | D3212169909 | 288 |  | 00832 Arevalo, Greg | NC O&E SUP | Car hit station 288-571 @ D32121699 | 33.0452 | -117.2593 | 2021 | UG Vehicle
OMD0000723438-01 | Branch Outage | 2020-05-11 14:09 | 2020-05-11 14:07 | 2020-05-11 14:07 | N | N | N | N | N | Arching/Charring | 12 kV |  | Contact by Object | MYLAR BALLOONS AT P124380 - FLASH MIDSPAN ON PRIMARY - NO FIRE | Foreign Object Contact Conductor | F468920 | Fuse | 30A | P124380 | 303 |  | 30566 Garegnani, Dominic | NC O&E SUP | MYLAR BALLOONS CONTACTED PRIMARY WI | 33.1534 | -117.3382 | 2020 | Balloon
OMD0000723728-01 | No Lights in Part-Just Started | 2020-05-12 14:45 | 2020-05-12 13:05 | 2020-05-12 13:13 | N | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility | BAD/ CORRODED AL/CU SECONDARY CONNECTION AT P24467 WAS BURNT - NO IGNITION | Connector Damaged | CD4-98 | Transformer | 50 | P24467 | CD4 |  | 30566 Garegnani, Dominic | NC O&E SUP | DEAD LEG AT CUSTOMER PANEL - CORROD | 33.1607 | -117.345 | 2020 | Non Conductor
OMD0000725038-01 | Branch Outage | 2020-05-17 12:57 | 2020-05-17 11:50 | 2020-05-17 12:01 | N | N | N | N | N | Arching/Charring | 4 kV |  | Contact by Object | MYLAR BALLOONS AT P22560 ACROSS 2-4KV PHASES CAUSED PITTING AND ARCING ON COPPER PRIMAY WIRE - NO IGNITION - BLEW FUSES AT P23530 | Foreign Object Contacted Wire | F468479 | Fuse | 150A | P22560 | OS1 | MYLAR BALLOONS ACROSS 4KV PHASES - P120693 TO P22560 - SLEEV | 30566 Garegnani, Dominic | NC O&E SUP | MYLAR BALLOONS ACROSS 4KV PHASES AT | 33.194 | -117.3721 | 2020 | Balloon
OMD0000725040-01 | Emer-Antenna/Metal Object on Wir | 2020-05-17 12:59 | 2020-05-17 12:58 | 2020-05-17 12:58 | N | N | N | N | N | Arching/Charring | 4 kV |  | Contact by Object | DUP REPORT - MYLAR BALLOONS AT P22560 CAUSED ARCING & PITTING ON 4KV PHASE & BLEW FUSE AT P23530 - NO IGNITION | Foreign Object Contacted Wire | OS1-37 | Transformer | 50 | P22560 | OS1 |  | 30566 Garegnani, Dominic | NC O&E SUP | MYLAR BALLOONS ACROSS 4KV PHASES AT | 33.197 | -117.3706 | 2020 | Balloon
OMD0000727627-01 | Branch Outage | 2020-05-27 20:12 | 2020-05-27 18:46 | 2020-05-27 18:58 | N | N | N | N | N | Arching/Charring | 4 kV |  | Electric Facility | CHARRED & PITTED FUSEED CUTOUT DOOR CONTACT AT P15723 - NO IGNITION - (KEARNY HX CUTOUT & DOOR) | Device Damaged | F588944 | Fuse | 30A | P15723 | VS2 |  | 30566 Garegnani, Dominic | NC O&E SUP | P15723 - FUSED CUTOUT DOOR CHARRED | 33.1972 | -117.2388 | 2020 | Non Conductor
OMD0000728717-02 | Branch Outage | 2020-06-01 13:48 | 2020-06-01 12:30 | 2020-06-01 12:43 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | KEARNY CUTOUT CORRODED/ CHARRED & MELTED AT CONTACT TAB - DOOR OPENED | Device Damaged | F468949 | Fuse | 25A | P320415 | 1076 | BAD KEARNY CUTOUTS P320415 - CIR 1076 & 3-12KV ARRESTORS | 30566 Garegnani, Dominic | NC O&E SUP | BAD KEARNY CUTOUT AT P320415 - CREW | 33.1649 | -117.3542 | 2020 | Non Conductor
OMD0000729862-01 | Emer-Specl Req - Fire/Police/Gov | 2020-06-04 22:21 | 2020-06-04 20:55 | 2020-06-04 21:04 | N | N | N | N | N | Arching/Charring | 4 kV |  | Electric Facility | FUSED CUTOUT BLEW & CUSTOMER SAW SPARKS - NO IGNITION | Fuse Operated in Transformer | CD4-70 | Transformer | 25 | P22037 | CD4 |  | 30566 Garegnani, Dominic | NC O&E SUP | FUSED CUTOUT AT STA.CD4-70 BLEW & C | 33.1639 | -117.3383 | 2020 | Non Conductor
OMD0000730980-01 | Branch Outage | 2020-06-09 14:40 | 2020-06-09 14:40 | 2020-06-09 14:40 | N | N | N | N | N | Arching/Charring | 12 kV |  | Contact by Object | large car patio cover flew up into the 12kv lines blowing two 150 amp fuses. wire is ok | Foreign Object Contact Conductor | F128938 | Fuse | 150A | p379137 | 702 |  | 70169 Ransom, Ryan | NC O&E SUP | car patio cover blew up into 12kv | 32.7904 | -117.0806 | 2020 | Other All
OMD0000732962-03 | Branch Outage | 2020-06-16 21:43 | 2020-06-16 19:13 | 2020-06-16 21:35 | N | Y | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Transformer Problem | 522-38R | Recloser |  | P196254 | 522 |  | 02704 Martinez, Chris | NC O&E SUP | Went on site at approxt 1940 forgot | 33.3697 | -117.2278 | 2020 | Non Conductor
OMD0000739740-01 | Dmg Dim/Nolite - Tree on Wire | 2020-07-13 13:10 | 2020-07-13 12:13 | 2020-07-13 12:32 | N | N | N | N | N | Arching/Charring | 4 kV |  | Vegetation Contact |  | Undetermined | EN1-65 | Transformer | 25 | P126819J | EN1 | Customer @ this address has been cutting & trimming vegetati | 00832 Arevalo, Greg | NC O&E SUP | Customers vegetation was touching e | 33.0442 | -117.2897 | 2020 | Veg
OMD0000739833-01 | Branch Outage | 2020-07-13 15:37 | 2020-07-13 14:36 | 2020-07-13 15:08 | N | N | N | N | N | Arching/Charring | 12 kV |  | Contact by Object | BIRD | Transformer Problem | 67-45R | Recloser |  | p474526 | 67 | bad transformer 67-117 | 70169 Ransom, Ryan | NC O&E SUP |  | 32.6731 | -116.7169 | 2020 | Animal
OMD0000743016-03 | Branch Outage | 2020-07-24 08:37 | 2020-07-24 06:55 | 2020-07-24 07:12 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Contact by Object | Bird contact on high side of station 3030-656... | Foreign Object in Transformer | F468729 | Fuse | 100A | P220270 | 303 | Bird contact on primary side of 303-656 @ P220270. Can we f/ | 00832 Arevalo, Greg | NC O&E SUP | Bird contact phase to phase on stat | 33.1606 | -117.3258 | 2020 | Animal
OMD0000745916-01 | Emer-Specl Req - Fire/Police/Gov | 2020-08-02 08:17 | 2020-08-02 06:20 | 2020-08-02 06:46 | Y | Y | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | Stand off pin insulator tracking and melted. Burnt high side lead of transformer in half | Device Damaged | 376-69 | Three Phase Transformer | 2500 | P181326 | 376 | Hi side leads and stirrups need to be replaced on sta 376-17 | 02704 Martinez, Chris | NC O&E SUP |  | 32.6315 | -117.1355 | 2020 | Non Conductor
OMD0000746682-02 | Branch Outage | 2020-08-04 16:54 | 2020-08-04 16:50 | 2020-08-04 16:50 | N | N | N | N | N | Arching/Charring | 12 kV |  | Contact by Object | mylar balloons | Foreign Object Contact Conductor | 445-39R | Recloser |  | 248120 | 445 |  | 70169 Ransom, Ryan | NC O&E SUP | mylar balloons | 32.664 | -116.2733 | 2020 | Balloon
OMD0000749894-01 | Transformer Outage | 2020-08-14 12:10 | 2020-08-14 10:25 | 2020-08-14 11:06 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | blown fuse | Device Deenergized for Safety | 1119-432 | Transformer | 300 | P229478 | 1119 | Damaged cutout due to blown fuse | 02734 Willis, Brian | NC O&E SUP | Blown fuse damaging center cutout u | 33.0674 | -117.2781 | 2020 | Non Conductor
OMD0000749938-01 | Transformer Outage | 2020-08-14 14:32 | 2020-08-14 12:10 | 2020-08-14 13:05 | N | N | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | Blown pothead burnt open | Weather Damaged UG Cable | 1076-242 | Three Phase Transformer | 300 | P23509 | 1076 | Failed pothead connection @ P23509 | 02734 Willis, Brian | NC O&E SUP | Damaged pothead failed. Deenergize | 33.193 | -117.3785 | 2020 | OH to UG
OMD0000755541-03 | Circuit Outage | 2020-08-31 17:17 | 2020-08-31 14:21 | 2020-08-31 14:21 | Y | N | N | Y | N | Actual Ignition | 12 kV |  | Vegetation Contact | Customer hit guy wire with tractor | Equipment Damaged Conductor | FE-12KV-470 | Circuit |  | P310133 | 470 |  | 02704 Martinez, Chris | NC O&E SUP |  |  |  | 2020 | Vehicle
OMD0000757124-02 | No Lights - Cause Unknown | 2020-09-05 17:14 | 2020-09-05 16:51 | 2020-09-05 16:51 | Y | N | N | N | N | Arching/Charring |  | 480 V | Electric Facility |  | Connector Damaged | 209-705 | Transformer | 500 | 209-705 | 209 |  | 00832 Arevalo, Greg | NC O&E SUP | Secondary connections in station 20 | 33.2239 | -117.2277 | 2020 | Non Conductor
OMD0000758428-01 | Transformer Outage | 2020-09-07 03:04 | 2020-09-07 01:51 | 2020-09-07 02:16 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | CHANCE CUTOUT DOOR BURNED IN HALF ON POLE P20402 CAUSING AN OUTAGE - NO FIRE STARTED - CIR 582 | Device Damaged | 582-88 | Three Phase Transformer | 150 | P20402 | 582 |  | 30566 Garegnani, Dominic | NC O&E SUP | CUTOUT DOOR ON P20402 BURNED IN HAL | 33.2007 | -117.3831 | 2020 | Non Conductor
OMD0000760344-01 | Emer-Specl Req - Fire/Police/Gov | 2020-09-12 09:08 | 2020-09-12 08:14 | 2020-09-12 08:14 | Y | N | Y | N | N | Actual Ignition |  | 120 V | Electric Facility | A SERVICE DROP MAY HAVE HAD A NICK IN THE INSULATION AND BURNED DOWN MIDSPAN UNDERNIETH THE TREE GAURD ON THE SRVICE | Service Down | 505-254 | Transformer | 25 | P214882 | 505 | CREW TO REPLACE SERVICE FROM POLE TO HOUSE | 01826 Fowley, Jack | NC O&E SUP | A SERVICE DROP MAY HAVE HAD A NICK | 33.1784 | -117.256 | 2020 | Conductor
OMD0000819298-03 | Circuit Outage | 2021-04-25 11:55 | 2021-04-25 08:47 | 2021-04-25 08:47 | N | Y | N | N | N | Actual Ignition | 12 kV |  | Contact by Object | CAR HIT CAP STATION & SWITCH | Equipment Contacted Device | IB-12KV-158 | Circuit |  | D153203, D153204 | 158 | REPLACE SWITCH & CAP STATION | 05449 Bauers, Danny (I) | INACTIVE T | U15 - DBO - Replace Major Equip |  |  | 2021 | UG Vehicle
OMD0000761655-01 | Circuit Outage | 2020-09-17 15:47 | 2020-09-17 11:29 | 2020-09-17 11:29 | Y | N | Y | Y | N | Actual Ignition | 12 kV |  | Electric Facility | FAILED AL/CU WEDGE-TAP CONNECTION AT P202732 CAUSED SMALL BRUSH FIRE - 40SQUARE FEET - PUT OUT QUICKLY - CIR 750 | Damaged Underground Cable | BQ-12KV-750 | Circuit |  | P202732 | 750 | BAD WEDGETAP CONNECTION 3/0AL TO 400CU P202732 - ALSO POSS B | 30566 Garegnani, Dominic | NC O&E SUP | BAD 1000KCM CABLE TO MAN-HOLE M3448 | 33.1086 | -117.2687 | 2020 | OH to UG
OMD0000821905-01 | Branch Outage | 2021-05-06 14:00 | 2021-05-06 10:59 | 2021-05-06 11:35 | Y | N | N | N | N | Arching/Charring |  | 480 V | Electric Facility |  | Connector Damaged | F587570 | Fuse | 15A | SECONDARY BOX | 353 | DAMAGED 4-WIRE UG SERVICE WIRE 350 | 56561 McKeown, John | NE O&E SUP | DAMAGED SEC WIRE CREW TO REPLACE |  |  | 2021 | Non Conductor
OMD0000769693-01 | Non Outage | 2020-10-16 07:17 | 2020-10-16 06:00 | 2020-10-16 06:38 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility | OVERHEAD SSC SERVICE (NEOPRENE INSULATED) WIRE BURNT OPEN MID-SPAN IN FOGGY CONDITIONS | Open Neutral | 1081-635 | Transformer | 50 | P25146 | 1081 | BAD #6SSC CU OH SERVICE @P25146 - TO 344 LIVERPOOL DR | 30566 Garegnani, Dominic | NC O&E SUP | NEOPRENE INSULATED OH SSC COPPER SE | 33.0221 | -117.2788 | 2020 | Non Conductor
OMD0000770197-01 | Emer-Specl Req - Fire/Police/Gov | 2020-10-18 07:54 | 2020-10-18 07:28 | 2020-10-18 07:44 | Y | Y | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | Heavy fog melted primary insulator @ P120796... | Undetermined | 780-205 | Transformer | 50 | P120796 | 780 |  | 00832 Arevalo, Greg | NC O&E SUP | Primary insulator on buck arm @ P12 | 33.0958 | -117.3161 | 2020 | Other All
OMD0000771983-01 | Emer-Specl Req - Fire/Police/Gov | 2020-10-25 16:41 | 2020-10-25 16:41 | 2020-10-25 16:41 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | THE FUSE AT CAP STA 857-61F MELTED | Heat Device/Overload | 857-146 | Transformer | 150 | P219444 | 857 |  | 01826 Fowley, Jack | NC O&E SUP | THE FUSE AT CAP STA 857-61F MELTED | 33.1684 | -117.2171 | 2020 | Non Conductor
OMD0000772124-01 | Dmg/Wlite-Other | 2020-10-27 10:00 | 2020-10-27 08:50 | 2020-10-27 09:11 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | POLYMER INSULATOR MELTED AND BURNT AT P120796 ALSO CHARRED THE WOOD CROSSARM - NO OTHER IGNITION | Device Damaged | 780-205 | Transformer | 50 | P120796 | 780 |  | 30566 Garegnani, Dominic | NC O&E SUP | P120796 CIR 780 - POLYMER INSULATOR | 33.0958 | -117.3161 | 2020 | Non Conductor
OMD0000773689-01 | Dmg/Wlite-Flash or Sparks | 2020-10-31 01:40 | 2020-10-31 01:08 | 2020-10-31 01:08 | N | N | N | N | N | Arching/Charring | 12 kV |  | Vegetation Contact | LARGE QUEEN PALM FROND GROWING INTO PRIMARY WAS CHARRED - NO IGNITION | Palm Frond On Conductor | 1081-259 | Transformer | 50 | P20760 | 1081 | LARGE QUEEN PALM GROWING INTO PRIMARY CIR 1081 BTWEEN P20760 | 30566 Garegnani, Dominic | NC O&E SUP | LARGE QUEEN PALM HAD FROND ON PRIMA | 33.0183 | -117.2767 | 2020 | Veg
OMD0000773919-01 | Emer-Specl Req - Fire/Police/Gov | 2020-11-01 16:49 | 2020-11-01 10:54 | 2020-11-01 11:21 | N | N | N | N | N | Arching/Charring | 12 kV |  | Vegetation Contact | FAN PALMS SMOLDERING ON PRIMARY WIRE - CIR 68 P14678 TO P14679 | Palm Frond On Conductor | 68-401 | Transformer | 50 | P14678 | 68 |  | 30566 Garegnani, Dominic | NC O&E SUP | PALM TREES WERE SMOLDERING ON PRIMA |  |  | 2020 | Veg
OMD0000784827-01 | Transformer Outage | 2020-12-10 22:47 | 2020-12-10 22:27 | 2020-12-10 22:27 | N | N | N | N | Y | Arching/Charring | 12 kV |  | Other/Undetermined | Hot connection at center phase disconnect. No arcing or sparkingrequesting crew to change out switch | Heat Device/Overload | 780-189M | Primary Meter | 4.16 kV | p123013 | 780 | 900A disconnect overheated on center phase. Hardware also a | 02734 Willis, Brian | NC O&E SUP | Center phase disconnect glowing red | 33.1083 | -117.3197 | 2020 | Non Conductor
OMD0000789610-01 | Emer-Specl Req - Fire/Police/Gov | 2021-01-01 21:12 | 2021-01-01 20:07 | 2021-01-01 20:29 | N | N | N | N | N | Arching/Charring | 4 kV |  | Electric Facility | FIBERGLASS KEARNY CUTOUT DOOR HAD BROKEN FUSE INSIDE BUT DOOR DIDNT FALL OPEN & WAS TRACKING & BURNING ON DOOR TUBE - NO FIRE TO GROUND | Weather Damaged Device | CA1-57 | Transformer | 25 | P124294 | CA1 |  | 30566 Garegnani, Dominic | NC O&E SUP | CUTOUT DOOR FOR STA. CA1-57 HAD BRO | 33.0266 | -117.2841 | 2021 | Non Conductor
OMD0000793136-01 | Emer-Specl Req - Fire/Police/Gov | 2021-01-17 06:17 | 2021-01-17 02:44 | 2021-01-17 02:44 | N | N | N | Y | N | Actual Ignition | 4 kV |  | Other/Undetermined | FIRE HAD ALREADY STARTED UPON ARRIVAL. NO SDGE EQUIPMENT OR FACILITIES WAS DAMAGED. | Undetermined | VS1-156 | Transformer | 50 |  | VS1 |  | 07093 Lasua, Keoni | NC O&E SUP | FIRE AT 414 AND 414 #A N SANTA FE A | 33.2061 | -117.2456 | 2021 | Other All
OMD0000844518-03 | Branch Outage | 2021-08-04 00:58 | 2021-08-03 18:07 | 2021-08-03 18:18 | N | N | N | N | N |  | 12 kV |  | Electric Facility |  | Damaged Underground Cable | F2121998 | Fuse | 150A | D214264 | 282 |  | 00460 Stiles, Jake | EA O&E SUP | Bad cable and fuse cabinet. | 32.8313 | -116.9789 | 2021 | UG UG Cable
OMD0000854610-01 | Dmg Dim/Nolite-Xfmr/Grn Bx Fls/Sp | 2021-09-14 10:16 | 2021-09-14 08:44 | 2021-09-14 09:32 | Y | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Weather Damaged Connector | 169-180 | Transformer | 750 | d147474 | 169 | melted mil. sec. lugs x2 bring flag extension de energize st | 05036 Burrell, Dennis | EA O&E SUP | melted lugs | 32.7543 | -117.0531 | 2021 | UG Connector
OMD0000871182-01 | Voltage Problem-Low/Just Start | 2021-11-23 11:20 | 2021-11-23 09:45 | 2021-11-23 09:56 | Y | N | N | N | N | Arching/Charring |  | 208 V | Electric Facility |  | Connector Damaged | 781-107 | Transformer | 150 | D3669366364 | 781 | OVERLOAD, BURNED OFF SECONDARY LUG. | 23123 Domnitz, Jared | RA O&E SUP | OVERLOADED , SECONDARY LUG MELTED O | 33.1579 | -117.3506 | 2021 | UG Connector
OMD0000897976-01 | Branch Outage | 2022-03-19 23:02 | 2022-03-19 19:24 | 2022-03-19 19:24 | Y | N | N | Y | N | Arching/Charring | 12 kV |  | Electric Facility | car vs transformer...secondary flashed over causing 20'x20' brush fire...fd put out | Motor Vehicle Contact with Xfmr | LBE.56786 |  |  | D216723 | 165 | CAR VS ST 165-601. DAMAGE UG 500 SECONDARY..OIL WENT INTO SE | 68054 Piraino, John | ME O&E SUP | CAR VS STA 165-601 HIT N RUN...DAF | 32.7101 | -117.0877 | 2022 | UG Vehicle
OMD0000802081-01 | Branch Outage | 2021-02-12 14:25 | 2021-02-12 07:14 | 2021-02-12 07:40 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Wire Down | 239-15R | Recloser |  | P215304 | 239 | wire down | 02704 Martinez, Chris | NC O&E SUP |  | 33.3471 | -117.1356 | 2021 | Non Conductor
OMD0000806397-01 | Emer-Specl Req - Fire/Police/Gov | 2021-02-28 09:17 | 2021-02-28 08:46 | 2021-02-28 08:46 | Y | Y | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Damaged Underground Cable | 298-612 | Three Phase Transformer | 225 | P312117 | 298 | Replace damaged cable | 02704 Martinez, Chris | NC O&E SUP |  | 33.1425 | -117.1914 | 2021 | OH to UG
OMD0000817600-01 | Transformer Outage | 2021-04-17 08:44 | 2021-04-17 06:02 | 2021-04-17 07:05 | N | N | N | N | N | Arching/Charring |  | 240 V | Vegetation Contact | Tree between P189344 & 1216 Okinawa Rd rubbed PS legs & neutral together causing station outage & service wire to fall... | Fuse Operated in Transformer | 376-165 | Transformer | 37.5 |  | 376 | Overhead transformer 376-165 faulted after overhead service | 00832 Arevalo, Greg | NC O&E SUP | Overhead service to 1214 & 1216 Oki | 32.6492 | -117.147 | 2021 | Veg
OMD0000817604-01 | Dmg/Wlite-Wire Down Pole to House | 2021-04-17 08:47 | 2021-04-17 08:44 | 2021-04-17 08:44 | N | N | N | N | N | Arching/Charring |  | 240 V | Vegetation Contact |  | Service Down | 376-165 | Transformer | 37.5 |  | 376 |  | 00832 Arevalo, Greg | NC O&E SUP | Overhead service to 1214 & 1216 Oki | 32.6492 | -117.147 | 2021 | Veg
OMD0000819376-01 | Emer-Specl Req - Fire/Police/Govt | 2021-04-25 17:37 | 2021-04-25 17:24 | 2021-04-25 17:24 | Y | N | N | N | N | Actual Ignition |  | 120 V | Other/Undetermined | not sdge customer side started fire in pull box in building A of storage facility | Conductor Damaged | 404-270 | Transformer | 150 | customer wiring | 404 |  | 70169 Ransom, Ryan | NC O&E SUP | fire in customer pull box located a | 32.7737 | -117.0271 | 2021 | Other All
OMD0000822189-01 | Emer-Specl Req - Fire/Police/Govt | 2021-05-07 14:12 | 2021-05-07 13:48 | 2021-05-07 13:48 | N | N | N | N | N | Arching/Charring |  | 120 V | Other/Undetermined | service wire down. riser fell off o house at 1717. houae is under remolded wall wasnt supported.and fell down. | Customer Problem | 386-51 | Transformer | 50 |  | 386 |  | 70169 Ransom, Ryan | NC O&E SUP | customer needs to make repairs to p | 32.8052 | -116.9171 | 2021 | Other All
OMD0000826352-01 | No Lights - Cause Unknown | 2021-05-25 21:42 | 2021-05-25 20:30 | 2021-05-25 21:02 | N | N | N | N | N | Arching/Charring |  | 120 V | Other/Undetermined | main breaker burning on buss bar | Heat Device/Overload | 96-274 | Transformer | 50 |  | 96 |  | 70169 Ransom, Ryan | NC O&E SUP | removed locking ring for electricia | 32.7552 | -116.9358 | 2021 | Other All
OMD0000844125-01 | Dmg/Wlite-Other | 2021-08-02 14:53 | 2021-08-02 14:00 | 2021-08-02 14:00 | N | N | N | N | N |  | 12 kV |  | Electric Facility | TEST - Arrestor still on pole, burnt - TEST | Customer Restored | 1435-144 | Transformer | 225 | P123456789 | 1435 |  | 00832 Arevalo, Greg | NC O&E SUP | TESTING for ETS Safety Meeting | 32.7129 | -117.1224 | 2021 | Non Conductor
OMD0000846711-01 | No Lights in Part-Just Started | 2021-08-12 14:05 | 2021-08-12 13:53 | 2021-08-12 13:53 | N | Y | N | N | N | Arching/Charring |  | 240 V | Other/Undetermined | Either overload or loose connection caused meter clip & meter stabs to melt... | Customer Problem | MT1-96 | Transformer | 75 |  | MT1 |  | 00832 Arevalo, Greg | NC O&E SUP | No light issue caused by burnt mete | 32.7431 | -117.1812 | 2021 | Non Conductor
OMD0000848958-01 | Emer-Specl Req - Fire/Police/Govt | 2021-08-21 10:45 | 2021-08-21 08:05 | 2021-08-21 09:41 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility | CUSTOMER MOVED SDG&E WEATHERPROOF #6 CU SERVICE TO ILLEAGAL TEMP POLE & PS LEGS SHORTED/ SPARKED & CAUSED WIRE DOWN FROM P123482 TO TEMP POLE - NO IGNITION ON GROUND - WAS RAINING | Service Down | 1081-239 | Transformer | 75 | P123482 | 1081 |  | 30566 Garegnani, Dominic | NC O&E SUP | WEATHERPROOF WIRE DOWN FROM P123482 | 33.0206 | -117.2773 | 2021 | Other All
OMD0000851491-01 | Dmg/Wlite-Other | 2021-08-31 18:01 | 2021-08-31 17:48 | 2021-08-31 17:48 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Weather Damaged Conductor | 66-789 | Transformer | 75 | P133183 | 66 |  | 00541 Cabezuela, Javier | NC O&E SUP | REPORTS OF ARCHING AFTER LINGHTING | 32.9907 | -117.2259 | 2021 | Other All
OMD0000851739-01 | Emer-Specl Req - Fire/Police/Govt | 2021-09-01 20:03 | 2021-09-01 18:37 | 2021-09-01 18:49 | Y | Y | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Weather Damaged Connector | 257-1090 | Transformer | 150 | P183416 | 257 | Burnt open pothead @ P183416... | 00832 Arevalo, Greg | NC O&E SUP | Burnt open pothead connection @ P18 | 32.6427 | -117.0812 | 2021 | OH to UG
OMD0000853530-01 | Dmg/Wlite-Flash or Sparks | 2021-09-09 22:08 | 2021-09-09 21:17 | 2021-09-09 21:34 | Y | Y | N | N | N | Arching/Charring |  | 240 V | Other/Undetermined | Old copper stranded service burnt open in multiple spots due to bad insulation... | Weather Damaged Service | 320-152 | Transformer | 50 |  | 320 | Burnt open overhead service @ 311 Sunswept St... | 00832 Arevalo, Greg | NC O&E SUP | Copper stranded service from P67307 | 32.6951 | -117.0387 | 2021 | Conductor
OMD0000854602-02 | Branch Outage | 2021-09-14 07:59 | 2021-09-14 07:03 | 2021-09-14 07:46 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | old cut out door tracked and burnt in half | Device Damaged | F86036 | Fuse | 100A | p871298 | 730 | change cut outs p871298 2- 100amp chance doors currently ne | 70169 Ransom, Ryan | NC O&E SUP | bad c/o door will fill out follwup | 32.7148 | -116.9863 | 2021 | Non Conductor
OMD0000854604-01 | Emer-Specl Req - Fire/Police/Govt | 2021-09-14 08:17 | 2021-09-14 08:00 | 2021-09-14 08:00 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Device Damaged | 730-1184 | Transformer | 25 | p871298 | 730 |  | 70169 Ransom, Ryan | NC O&E SUP | cut out burnt in half do to trackin | 32.7148 | -116.9868 | 2021 | Non Conductor
OMD0000859639-01 | Dmg Dim/Nolite - Flash or Sparks | 2021-10-05 04:11 | 2021-10-05 02:37 | 2021-10-05 03:14 | Y | N | N | N | N | Arching/Charring |  | 240 V | Other/Undetermined | Old copper stranded service, insulation on PS legs failed... | Weather Damaged Service | EO1-110 | Transformer | 25 |  | EO1 | Old copper service faulted @ weatherhead causing outage. Mad | 00832 Arevalo, Greg | NC O&E SUP | Old copper service faulted @ weathe | 32.7125 | -117.0543 | 2021 | Conductor
OMD0000860304-01 | Emer-Specl Req - Fire/Police/Govt | 2021-10-05 16:44 | 2021-10-05 15:48 | 2021-10-05 16:09 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | Lightning hit xfmr causing pole fire | Weather Damaged Transformer | 1435-179 | Transformer | 50 | P202901 | 1435 | C/O Xfmr hit by lightning | 02704 Martinez, Chris | NC O&E SUP | Xfmr hit by Lightning causing lead | 32.719 | -117.1233 | 2021 | Non Conductor
OMD0000862913-01 | Emer-Specl Req - Fire/Police/Govt | 2021-10-18 07:16 | 2021-10-18 07:16 | 2021-10-18 07:16 | N | N | N | N | N |  | 12 kV |  | Electric Facility | A CAP STATION CAUGHT FIRE THERE WAS SOME BURNING OIL ON THE GOUND | Heat Device/Overload | 61-557 | Transformer | 25 | P60898 | 61 | CREW TO REMOVE CAP STATION 61-1577CM IT CAUGHT FIRE | 01826 Fowley, Jack | NC O&E SUP | CREW TO REMOVE CAP STATION 61-1577C | 32.9678 | -117.2646 | 2021 | Non Conductor
OMD0000864537-01 | Dmg/Wlite-Pole Burning | 2021-10-25 19:55 | 2021-10-25 19:38 | 2021-10-25 19:38 | N | Y | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | Tracking @ primary level above station caused xarm to catch fire... | Company Shut-Off | 1434-229 | Transformer | 50 | P76707 | 1434 |  | 00832 Arevalo, Greg | NC O&E SUP | Primary xarm @ P76707 caught fire. | 32.7123 | -117.1071 | 2021 | Non Conductor
OMD0000864542-01 | Emer-Specl Req - Fire/Police/Govt | 2021-10-25 19:38 | 2021-10-25 17:37 | 2021-10-25 17:37 | N | Y | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Company Shut-Off | 1434-229 | Transformer | 50 | P76707 | 1434 | Fire damaged 10ft 4pin primary xarm @ P76707 | 00832 Arevalo, Greg | NC O&E SUP | Primary xarm @ P76707 caught fire. | 32.7123 | -117.1071 | 2021 | Other All
OMD0000865216-01 | Emer-Specl Req - Fire/Police/Govt | 2021-10-28 14:39 | 2021-10-28 10:54 | 2021-10-28 11:31 | N | N | N | N | Y |  |  | 120 V | Other/Undetermined | structure fire burnt down secondary service | Service Deenergized For Safety | 92-477 | Transformer | 50 |  | 92 |  | 70169 Ransom, Ryan | NC O&E SUP | structure fire burnt down service w | 32.7419 | -116.9633 | 2021 | Other All
OMD0000867517-01 | Emer-Specl Req - Fire/Police/Govt | 2021-11-06 03:54 | 2021-11-06 03:38 | 2021-11-06 03:38 | N | N | N | N | Y |  |  | 120 V | Other/Undetermined | structure fire | Customer Problem | 280-319 | Transformer | 25 |  | 280 |  | 70169 Ransom, Ryan | NC O&E SUP | structure fire pulled meter for saf | 32.8321 | -117.0247 | 2021 | Other All
OMD0000868465-01 | Emer-Specl Req - Fire/Police/Govt | 2021-11-11 12:01 | 2021-11-11 10:54 | 2021-11-11 11:17 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | Blown lightning arrestor | Undetermined | 168-414 | Transformer | 25 | P571034 | 168 | Blown lightning arrestor @ P571034. Isolated damaged arresto | 00832 Arevalo, Greg | NC O&E SUP | Blown lighning arrestor @ P571034. | 32.7721 | -117.086 | 2021 | Other All
OMD0000869427-01 | Dmg/Wlite-Flash or Sparks | 2021-11-16 09:38 | 2021-11-16 08:31 | 2021-11-16 08:46 | N | N | N | N | Y | Arching/Charring |  | 240 V | Other/Undetermined | Copper stranded service burnt open & went PS to N... | Service Deenergized For Safety | WA6-51 | Transformer | 25 |  | WA6 | Burnt open copper stranded service... | 00832 Arevalo, Greg | NC O&E SUP | Weather damaged service causing out | 32.7386 | -117.0971 | 2021 | Conductor
OMD0000871898-01 | Emer-Specl Req - Fire/Police/Govt | 2021-11-26 19:03 | 2021-11-26 17:53 | 2021-11-26 18:56 | N | N | N | N | Y |  |  | 120 V | Other/Undetermined | customer owned equipment sub panel to another building had fire at base of panel. customer had generator hooked up to panel durring power shut off. maybe generator caused fire not sure did not look to be electric in nature. | Undetermined | 157-1259 | Transformer | 15 |  | 157 |  | 70169 Ransom, Ryan | NC O&E SUP | power is on and sdge facilities are | 32.7265 | -116.7754 | 2021 | Other All
OMD0000872491-01 | No Lights in Part-Just Started | 2021-11-30 12:26 | 2021-11-30 11:42 | 2021-11-30 11:55 | N | N | N | N | N | Arching/Charring |  | 240 V | Other/Undetermined | Copper stranded service flashed over PS to Neutral... | Weather Damaged Service | 364-331 | Transformer | 50 |  | 364 | Stranded copper service damaged & needs to be changed out... | 00832 Arevalo, Greg | NC O&E SUP | Copper stranded service failed w/we | 32.7448 | -117.0983 | 2021 | Conductor
OMD0000873042-01 | No Lights in Part-Just Started | 2021-12-02 11:44 | 2021-12-02 10:29 | 2021-12-02 10:57 | N | N | N | N | Y | Arching/Charring |  | 240 V | Other/Undetermined | Copper stranded service burnt open PS to Neutral... | Weather Damaged Service | RD4-210 | Transformer | 50 | P176057J | RD4 | Burnt open copper stranded service @ P176057... | 00832 Arevalo, Greg | NC O&E SUP | Burnt open PS & N leg @ P176057J ca | 32.7588 | -117.0671 | 2021 | Conductor
OMD0000877721-01 | Dmg/Wlite-Other | 2021-12-16 15:47 | 2021-12-16 15:39 | 2021-12-16 15:39 | N | N | N | N | Y | Arching/Charring | 12 kV |  | Other/Undetermined | Hole burnt thru primary crossarm & primary pin... | Undetermined | 591-58 | Transformer | 15 | Z85459 | 591 | Primary xarm @ Z85459 is damaged. Hole burnt thru @ primary | 00832 Arevalo, Greg | NC O&E SUP | Primary xarm @ Z85459 is damaged. H | 32.6787 | -117.0012 | 2021 | Non Conductor
OMD0000888263-01 | Emer-Specl Req - Fire/Police/Govt | 2022-02-03 00:26 | 2022-02-02 22:49 | 2022-02-02 23:41 | N | N | N | N | N |  | 12 kV |  | Other/Undetermined |  | Undetermined | 286-741 | Transformer | 25 |  | 286 |  | 07093 Lasua, Keoni | NC O&E SUP | HOUSE FIRE AT 304 ALVISO WAY, ENCIN | 33.0559 | -117.293 | 2022 | Other All
OMD0000893071-01 | Transformer Outage | 2022-02-26 17:02 | 2022-02-26 14:59 | 2022-02-26 15:19 | N | N | N | N | N | Arching/Charring |  | 208 V | Contact by Object | Delivery truck struck service @ weatherhead causing PS to Gnd fault/flash/melted connections & wire... | Motor Vehicle Contact Services | 256-88 | Transformer | 75 |  | 256 |  | 00832 Arevalo, Greg | NC O&E SUP | Truck hit service @ bldg causing PS | 32.6294 | -117.0934 | 2022 | Vehicle
OMD0000895337-01 | Dmg/Wlite-Other | 2022-03-08 21:02 | 2022-03-08 17:15 | 2022-03-08 17:26 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | disconnect failed | Device Damaged | 406-436 | Transformer | 50 | p105185 | 406 | 600amp underarm disconnect burning up | 70169 Ransom, Ryan | NC O&E SUP |  | 32.7908 | -117.0167 | 2022 | Non Conductor
OMD0000895350-01 | Emer-Specl Req - Fire/Police/Govt | 2022-03-08 23:48 | 2022-03-08 22:36 | 2022-03-08 22:36 | Y | Y | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | Possible guy wire contact w/69kv phase @ Z100714... | Fire Damaged Pole | 105-108 | Transformer | 75 | Z100714 | 105 | Z100714 pole change out. 69kv w/12kv ubderbuilt... | 00832 Arevalo, Greg | NC O&E SUP | Z100714 pole top caught fire @ 69kv | 32.7554 | -117.1994 | 2022 | Other Contact
OMD0000895375-01 | Dmg Dim/Nolite-Pole Burning | 2022-03-08 23:51 | 2022-03-08 23:48 | 2022-03-08 23:48 | Y | Y | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | Possible guy wire contact w/69kv phase @ Z100714 | Fire Damaged Pole | UNKNOWN | Switch |  | Z100714 | 124 |  | 00832 Arevalo, Greg | NC O&E SUP | Z100714 pole top caught fire @ 69kv | 32.7541 | -117.1995 | 2022 | Other Contact
OMD0000895386-01 | Dmg/Wlite-Flash or Sparks | 2022-03-08 22:31 | 2022-03-08 22:29 | 2022-03-08 22:29 | Y | Y | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | Possible guy wire failure contacted 69kv phase @ Z100714... | Fire Damaged Pole | 491-117 | Transformer | 75 | Z100714 | 491 |  | 00832 Arevalo, Greg | NC O&E SUP | Z100714 pole top caught fire @ 69kv | 32.7558 | -117.2013 | 2022 | Other Contact
OMD0000897162-01 | Dmg/Wlite-Flash or Sparks | 2022-03-16 01:24 | 2022-03-15 21:55 | 2022-03-15 22:11 | N | N | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | Corrosion on device | Weather Damaged Device | 781-401 | Transformer | 75 | P28840 | 781 | Damaged cutout on east side of pole arcing and sparking. Ne | 02734 Willis, Brian | NC O&E SUP | Corroded cutout at P28840 causing a | 33.1583 | -117.3526 | 2022 | Other All
OMD0000897976-02 | Branch Outage | 2022-03-19 22:21 | 2022-03-19 22:20 | 2022-03-19 22:20 | N | N | N | Y | N |  | 12 kV | 208 V | Contact by Object |  | Motor Vehicle Contact with Xfmr | LBE.56786 |  |  | 165-601 | 165 |  | 00832 Arevalo, Greg | NC O&E SUP | Car hit station 165-601 causing out | 32.7101 | -117.0877 | 2022 | UG Vehicle
OMD0000897980-02 | Emer-Specl Req - Fire/Police/Govt | 2022-03-19 22:20 | 2022-03-19 19:09 | 2022-03-19 19:09 | N | N | N | Y | N |  | 12 kV | 208 V | Electric Facility |  | Motor Vehicle Contact with Xfmr | 165-601 | Three Phase Transformer | 300 | 165-601 | 165 |  | 00832 Arevalo, Greg | NC O&E SUP | Car hit station 165-601 causing out | 32.7101 | -117.0877 | 2022 | UG Vehicle
OMD0000904922-02 | Transformer Outage | 2022-04-21 14:18 | 2022-04-21 12:27 | 2022-04-21 14:12 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility | Faulted secondary molds in SH211277 faulted & melted... | Weather Damaged Connector | 80-514 | Three Phase Transformer | 100 | SH211277 | 80 |  | 00832 Arevalo, Greg | NC O&E SUP | Blown bayonet fuses @ 80-514 caused | 32.6956 | -117.1125 | 2022 | UG Connector
OMD0000909436-01 | Emer-Specl Req - Fire/Police/Govt | 2022-05-11 22:30 | 2022-05-11 20:51 | 2022-05-11 22:21 | Y | N | N | N | N | Arching/Charring |  | 480 V | Electric Facility |  | Device Damaged | 91-668 | Transformer | 150 | customer pedistal meter base | 91 | meter pedistal burnt up feeding parking lot lights. deenger | 70169 Ransom, Ryan | NC O&E SUP | customer meter pedistal burnt up ne | 32.7396 | -116.9361 | 2022 | Other All
OMD0000911636-01 | Dmg/Wlite-Other | 2022-05-19 18:15 | 2022-05-19 17:13 | 2022-05-19 17:42 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility | NEOPRENE INSULATIOIN ON SSC SERVICE CRACKED & PS LEGS TRACKED TO & BURNT NEUTRAL MESSENGER WIRE OPEN | Open Neutral | 303-989 | Transformer | 50 | P128731 TO HOUSE | 303 | OPEN/ BURNT NEUTRAL MESSENGER ON #6SSC CU SERVICE -(NEOPRENE | 30566 Garegnani, Dominic | NC O&E SUP | OPEN NEUTRAL MESSENGER WIRE ON OH # | 33.1555 | -117.3406 | 2022 | Non Conductor
OMD0000911955-01 | Dmg Dim/Nolite-Wire Down P to P | 2022-05-20 15:51 | 2022-05-20 15:37 | 2022-05-20 15:37 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility | NEOPRENE INSULATED OH CU SERVICE WIRES ARCING & BURNT DOWN IN FOG/RAIN | Service Down | EN1-362 | Transformer | 25 | P26272 (MID-SPAN SVC) | EN1 | OH SSC NEOPRENE COPPER SERVICE DOWN - FROM ALLEY MID-SPAN TO | 30566 Garegnani, Dominic | NC O&E SUP | NEOPRENE OH SSC COPPER SERVICE BURN | 33.0564 | -117.3004 | 2022 | Conductor
OMD0000917565-01 | No Lights - Cause Unknown | 2022-06-14 15:02 | 2022-06-14 13:40 | 2022-06-14 14:19 | N | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility | NEOPRENE INSULATED SSC CU SERVICE BURNT OPEN MID-SPAN - WIRE STAYED UP BUT CUST. OUT OF POWER | Weather Damaged Service | 303-1008 | Transformer | 25 | P220662 | 303 | NEOPRENE SSC CU SERVICE WIRES BURNT OPEN AT P220662 | 30566 Garegnani, Dominic | NC O&E SUP | NEOPRENE INSULATED SSC CU SERVICE P | 33.1562 | -117.3329 | 2022 | Conductor
OMD0000922993-01 | Branch Outage | 2022-07-02 17:19 | 2022-07-02 15:29 | 2022-07-02 15:43 | N | N | N | Y | N |  | 12 kV |  | Contact by Object |  | Foreign Object Contacted Device | F2239268 | Fuse | 150A | P2107872488 | 365 |  | 00832 Arevalo, Greg | NC O&E SUP | Animal contact @ P2107872488 caused | 32.7428 | -117.1456 | 2022 | Other Contact
OMD0000923365-01 | Dmg/Wlite-Other | 2022-07-05 13:48 | 2022-07-05 13:37 | 2022-07-05 13:37 | N | N | N | N | N |  | 4 kV |  | Electric Facility |  | Foreign Object Contact Conductor | CG1-103 | Transformer | 10 | p376796 to p675838 | CG1 |  | 70169 Ransom, Ryan | NC O&E SUP | duplicate order | 32.7698 | -116.9674 | 2022 | Conductor
OMD0000923367-01 | Emer-Specl Req - Fire/Police/Govt | 2022-07-05 13:37 | 2022-07-05 10:53 | 2022-07-05 11:17 | Y | N | N | Y | N |  | 4 kV |  | Electric Facility |  | Foreign Object Contact Conductor | CG1-103 | Transformer | 10 | p376796 | CG1 | secondary wire down, open wire. going back with aerial cab | 70169 Ransom, Ryan | NC O&E SUP | tree crew dropped branch and open w | 32.7698 | -116.9674 | 2022 | Veg
OMD0000926152-01 | Emer-Specl Req - Fire/Police/Govt | 2022-07-17 06:17 | 2022-07-17 03:52 | 2022-07-17 04:06 | N | N | N | N | Y |  | 12 kV |  | Other/Undetermined | House fire in attic above garage | Undetermined | 576-95 | Transformer | 75 |  | 576 |  | 11288 Ott, Frank | NC O&E SUP | House fire started in attic above g | 33.0366 | -117.0496 | 2022 | Other All
OMD0000926254-01 | Branch Outage | 2022-07-18 09:03 | 2022-07-18 07:25 | 2022-07-18 07:25 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Contact by Object | car hit station | Motor Vehicle Contact with Xfmr | F157844 | Fuse | 100A |  | 551 | car hit station 551-129 and run of cable | 70169 Ransom, Ryan | NC O&E SUP | car vs transformer hit and run | 32.8068 | -116.9512 | 2022 | UG Vehicle
OMD0000931348-01 | Dmg/Wlite-Flash or Sparks | 2022-08-09 12:14 | 2022-08-09 11:48 | 2022-08-09 11:48 | Y | Y | N | N | N | Arching/Charring |  | 240 V | Vegetation Contact | Palm tree grew into open wire secondary | Tree Damaged Conductor | EO2-45 | Transformer | 37.5 | P244821 | EO2 | Tree trimmers need to trim/top 2 fan palms that are damaging | 02704 Martinez, Chris | NC O&E SUP |  | 32.7034 | -117.0736 | 2022 | Veg
OMD0000936546-03 | Branch Outage | 2022-08-30 15:16 | 2022-08-30 12:42 | 2022-08-30 15:12 | N | N | N | N | N | Arching/Charring | 12 kV |  | Contact by Object | CABLE TV LASHING (OR STRAND SUPPORT WIRE) CONTACTED PRIMARY CONDUCTOR | Foreign Object Contacted Wire | F2283726 | Fuse | 150A | P14628 | 305 |  | 30566 Garegnani, Dominic | NC O&E SUP | CABLE TV WIRE CONTACTED PRIMARY CON | 33.0111 | -117.2115 | 2022 | Other Contact
OMD0000941672-01 | Emer-Specl Req - Fire/Police/Govt | 2022-09-10 22:11 | 2022-09-10 21:18 | 2022-09-10 21:28 | N | N | N | N | N | Arching/Charring | 4 kV |  | Electric Facility | CORRODED CUTOUT CONTACT IS ARCING - ETS MADE TEMP REPAIR & FLW UP TO REPLACE XFMR & CUTOUT | Weather Damaged Device | AG1-62 | Transformer | 25 | P222757 | AG1 | EMAIL SENT FOR STA.AG1-61 P222757 (NOT 62) CUTOUT IS BURNT | 30566 Garegnani, Dominic | NC O&E SUP | STA. AG1-61 P222757 HAS CUTOUT ARCI | 33.1518 | -117.3478 | 2022 | Non Conductor
OMD0000943119-01 | Dmg Dim/Nolite - Flash or Sparks | 2022-09-16 19:39 | 2022-09-16 17:51 | 2022-09-16 18:11 | N | N | N | N | N | Arching/Charring |  | 240 V | Other/Undetermined | Fumigation techs clamped tent to overhead service causing PS to PS fault, arcing, & melting of service... | Foreign Object Contact Services | 366-287 | Transformer | 75 |  | 366 | Damaged burnt open overhead service @ weatherhead. Fumigatio | 00832 Arevalo, Greg | NC O&E SUP | Fumigation co. clamped tent to over | 32.7538 | -117.1046 | 2022 | Other All
OMD0000949688-01 | Dmg/Wlite-Pole Burning | 2022-10-14 09:34 | 2022-10-14 08:21 | 2022-10-14 08:21 | N | Y | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Company Shut-Off | 163-254 | Transformer | 25 | P76646 | 163 | Burning primary xarm @ P76646. Xarm burnt @ pin & insulator. | 00832 Arevalo, Greg | NC O&E SUP | Xarm caught fire @ pin & insulator | 32.7246 | -117.0521 | 2022 | Non Conductor
OMD0000949690-01 | Dmg/Wlite-Pole Burning | 2022-10-14 10:04 | 2022-10-14 09:34 | 2022-10-14 09:34 | N | Y | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | Pin & Insulator burnt thru wooden xarm & caused ignition @ xarm... | Company Shut-Off | 163-359 | Transformer | 50 | P76646 | 163 |  | 00832 Arevalo, Greg | NC O&E SUP | Primary xarm @ P76646 caught fire @ | 32.7242 | -117.0528 | 2022 | Non Conductor
OMD0000950069-01 | Dmg Dim/Nolite-WireDown Pole to H | 2022-10-16 01:26 | 2022-10-15 23:58 | 2022-10-16 00:15 | N | N | N | N | Y | Arching/Charring |  | 240 V | Other/Undetermined | Copper stranded service faulted | Service Down | 168-495 | Transformer | 50 |  | 168 | Copper stranded service failed @ weatherhead... | 00832 Arevalo, Greg | NC O&E SUP | Copper stranded service failed @ we | 32.7686 | -117.0794 | 2022 | Conductor
OMD0000950329-01 | Dmg Dim/Nolite - Flash or Sparks | 2022-10-17 12:03 | 2022-10-17 11:16 | 2022-10-17 11:24 | N | N | N | N | Y | Arching/Charring |  | 240 V | Other/Undetermined | Copper stranded service... | Weather Damaged Service | 368-106 | Transformer | 25 |  | 368 | Failed copper stranded service... | 00832 Arevalo, Greg | NC O&E SUP | Copper stranded service failed caus | 32.7603 | -117.1158 | 2022 | Conductor
OMD0000952325-01 | Voltage Problem-Low/Just Start | 2022-10-25 11:48 | 2022-10-25 11:09 | 2022-10-25 11:19 | N | N | N | N | Y | Arching/Charring |  | 240 V | Other/Undetermined | Copper stranded service faulted @ P930798 | Weather Damaged Service | WA5-150 | Transformer | 25 |  | WA5 | Faulted 65ft copper stranded service... | 00832 Arevalo, Greg | NC O&E SUP | Copper stranded service faulted @ p | 32.7355 | -117.0909 | 2022 | Conductor
OMD0000954257-01 | Non Outage Order | 2022-11-02 15:50 | 2022-11-02 13:14 | 2022-11-02 13:26 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | tracking | Weather Damaged Pole | 342-1015 | Transformer | 15 | P170346 | 342 | Crew to c/o damaged pole | 02704 Martinez, Chris | NC O&E SUP | Crew to c/o damaged pole | 32.7608 | -117.0722 | 2022 | Other All
OMD0000956107-01 | Emer-Specl Req - Fire/Police/Govt | 2022-11-08 23:53 | 2022-11-08 22:12 | 2022-11-08 22:29 | N | Y | N | N | N |  |  | 240 V | Vegetation Contact | secondary failed midspan between P76836 & P930630 catching pine on fire... | Service Deenergized For Safety | EO3-6 | Transformer | 50 |  | EO3 | 100ft of #4al triplex from p76836 to P930630 caught fire mid | 00832 Arevalo, Greg | NC O&E SUP | Secondary wire between poles failed | 32.7116 | -117.0626 | 2022 | Conductor
OMD0000970364-03 | Circuit Outage | 2023-01-07 01:43 | 2023-01-07 01:43 | 2023-01-07 01:43 | Y | N | N | N | N |  | 12 kV |  | Electric Facility |  | Wire Down | EN-12KV-286 | Circuit |  | P27517 | 286 |  | 30566 Garegnani, Dominic | NC O&E SUP | BI-METAL STIRRUP CORRODED 6/3 CU PR | 33.0792 | -117.2884 | 2023 | Non Conductor
OMD0000970746-01 | No Lights in Part-Just Started | 2023-01-08 13:00 | 2023-01-08 11:32 | 2023-01-08 11:34 | N | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility | BAD AL/CU INSULINK CONNECTION WAS CHARRED AT POLE P225825 | Connector Damaged | 900-653 | Transformer | 15 | P225825 | 900 |  | 30566 Garegnani, Dominic | NC O&E SUP | DEAD LEG AT CUST. PANEL & CUST. HAS | 33.2338 | -117.3151 | 2023 | Non Conductor
OMD0000973371-01 | Dmg/Wlite-Wire Down Pole to House | 2023-01-16 14:31 | 2023-01-16 14:05 | 2023-01-16 14:10 | Y | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Weather Damaged Service | 321-92 | Transformer | 25 | P675485 | 321 | Copper stranded service faulted @ weatherhead... | 00832 Arevalo, Greg | NC O&E SUP | Old copper stranded service faulted | 32.6877 | -117.0876 | 2023 | Conductor
OMD0000973482-01 | Dmg Dim/Nolite-WireDown Pole to H | 2023-01-16 15:20 | 2023-01-16 14:36 | 2023-01-16 14:58 | Y | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Service Down | 257-146 | Transformer | 15 | P88258J | 257 | Copper stranded service faulted... | 00832 Arevalo, Greg | NC O&E SUP | Copper stranded service faulted @ w | 32.6362 | -117.084 | 2023 | Conductor
OMD0000928819-01 | Emer-Specl Req - Fire/Police/Govt | 2022-07-28 15:50 | 2022-07-28 15:50 | 2022-07-28 15:50 | Y | N | N | Y | N |  | 12 kV |  | Contact by Object |  | Equipment Contact UG Cable | 437-149 | Three Phase Transformer | 1000 | D161400 | 437 | 25NDS, 300' #2Sol, 700 #2 secondary | 02216 Johns, Mike | BC O&E SUP |  | 32.9117 | -117.1111 | 2022 | UG Other Contact
OMD0000976973-01 | Dmg Dim/Nolite-WireDown Pole to H | 2023-01-26 18:14 | 2023-01-26 17:05 | 2023-01-26 17:05 | N | N | N | N | N | Arching/Charring |  | 120 V | Vegetation Contact | tree fell thru service drop tree on customers property not in sdge easement | Tree Damaged Service | RD2-149 | Transformer | 50 |  | RD2 |  | 70169 Ransom, Ryan | NC O&E SUP | removed service wire that was damag | 32.7702 | -117.0674 | 2023 | Veg
OMD0000982367-01 | Circuit Outage | 2023-02-19 12:52 | 2023-02-19 11:52 | 2023-02-19 11:52 | N | N | N | N | Y | Arching/Charring | 4 kV |  | Electric Facility | Porcelain underarm disconnect failure... | Heat Device/Overload | NC-4KV-NC4 | Circuit |  | P1829773709 | NC4 | Faulted porcelain underarm disconnect = NC4-8 @ P1829773709. | 00832 Arevalo, Greg | NC O&E SUP | Overheating/Damaged porcelain under | 32.6666 | -117.1051 | 2023 | Non Conductor
OMD0000982914-01 | Emer-Specl Req - Fire/Police/Govt | 2023-02-22 03:40 | 2023-02-22 01:31 | 2023-02-22 01:31 | Y | N | N | Y | N |  | 12 kV |  | Vegetation Contact | P320576 BROKE OFF AT GROUD AND WIRE SPARKED A FIRE | Weather Damaged Pole | 902-73 | Transformer | 25 | P320576 | 902 | P320576 BROKE OFF AT GROUND LEVEL AND NEEDS TO BE REPLACED | 01826 Fowley, Jack | NC O&E SUP | P320576 SNAPPED OFF AT THE GROUND | 33.1784 | -117.3403 | 2023 | Non Conductor
OMD0000986175-01 | Branch Outage | 2023-03-01 13:13 | 2023-03-01 12:16 | 2023-03-01 12:16 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Tree Damaged Conductor | F87155 | Fuse | 65A | p972374 | 1090 | tree took down wire and broke one xarm | 70169 Ransom, Ryan | NC O&E SUP | tree took down wire | 32.7059 | -116.8881 | 2023 | Veg
OMD0000998217-01 | Branch Outage | 2023-04-10 19:15 | 2023-04-10 19:15 | 2023-04-10 19:15 | Y | N | N | Y | N |  | 12 kV |  | Electric Facility | WIRE DOWN | Foreign Object Contact Conductor | 66-1213R | Recloser |  | P311774 | 66 | DISREGAURD | 01826 Fowley, Jack | NC O&E SUP | A TREE FELL ACCROSS THE WIRE MID SP | 32.9842 | -117.2264 | 2023 | Veg
OMD0001004123-01 | Dmg/Wlite-Explosion | 2023-05-03 23:46 | 2023-05-03 20:53 | 2023-05-03 21:04 | N | N | N | N | Y | Arching/Charring | 12 kV |  | Electric Facility |  | Heat Device/Overload | 205-950 | Three Phase Transformer | 300 | P138669 | 205 | see remarks , I e-mailed pictures | 73442 Rodman, Roland | NC O&E SUP | bad loadside disc on 205-369R , byp | 33.2099 | -117.2291 | 2023 | Non Conductor
OMD0001011948-01 | Dmg Dim/Nolite-Pole Burning | 2023-06-06 20:55 | 2023-06-06 17:24 | 2023-06-06 18:11 | Y | N | N | Y | N |  |  | 480 V | Other/Undetermined | No fire damage to SDGE facilities. Fire damage at customer panel due to possible theft. Denergized transformer bank feeding panel @ P410922 for safety. Fire department called on scene to extinguish smoldering brush. Oceanside Fire iniden | Vandalism | UNKNOWN | Switch |  |  | 486 | Had to denergize 3 phase bank 486-768 @ P410922 for safety. | 02734 Willis, Brian | NC O&E SUP | No fire damage to SDGE facilities. |  |  | 2023 | Other All
OMD0001016064-01 | Emer-Specl Req - Fire/Police/Govt | 2023-06-23 12:47 | 2023-06-23 12:06 | 2023-06-23 12:06 | N | N | N | N | N |  |  | 208 V | Other/Undetermined | CUSTOMER OWNED SOLAR PANELS | Customer Problem | 506-638 | Three Phase Transformer | 500 |  | 506 |  | 07093 Lasua, Keoni | NC O&E SUP | FIRE AT SMART & FINAL STORE IN VIST | 33.1888 | -117.2813 | 2023 | Other All
OMD0001016357-01 | Circuit Outage | 2023-06-25 10:49 | 2023-06-25 10:46 | 2023-06-25 10:46 | N | N | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | Faulted unjacketed primary cable @ H1624674437... | Damaged Underground Cable | IB-12KV-531 | Circuit |  | H1624674437 | 531 |  | 00832 Arevalo, Greg | NC O&E SUP | Faulted three phase primary cable i | 32.6105 | -117.0809 | 2023 | UG UG Cable
OMD0001016358-01 | Emer-Specl Req - Fire/Police/Govt | 2023-06-25 12:22 | 2023-06-25 10:49 | 2023-06-25 10:49 | N | Y | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Damaged Underground Cable | 531-119 | Transformer | 75 | H1624674437 | 531 | Faulted UG primary three phase cable... | 00832 Arevalo, Greg | NC O&E SUP | Faulted three phase primary cable i | 32.6106 | -117.0805 | 2023 | UG UG Cable
OMD0001016612-01 | Dmg/Wlite-Other | 2023-06-26 11:44 | 2023-06-26 11:39 | 2023-06-26 11:39 | Y | Y | N | N | N | Arching/Charring | 4 kV |  | Contact by Object |  | Foreign Object Contact Conductor | MK1-176 | Transformer | 10 | P574024 | MK1 | Mylar balloons damaged primary pins @ P574024... | 00832 Arevalo, Greg | NC O&E SUP | Crew to replace x arm, pins, & isul | 32.7146 | -117.0889 | 2023 | Balloon
OMD0001018139-01 | Emer-Specl Req - Fire/Police/Govt | 2023-07-03 00:30 | 2023-07-02 20:30 | 2023-07-02 21:29 | N | N | N | N | N |  |  | 120 V | Other/Undetermined | FIRE DEPARTMENT BELIEVES IT MAY BE AN ACT OF ARSON | Company Shut-Off | 66-680 | Transformer | 25 |  | 66 |  | 07093 Lasua, Keoni | NC O&E SUP | HOUSE FIRE. CRIMINAL INVESTIGATION | 32.985 | -117.2324 | 2023 | Other All
OMD0001021110-03 | Branch Outage | 2023-07-14 21:58 | 2023-07-14 17:14 | 2023-07-14 17:35 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Conductor Damaged | F59168 | Fuse | 150A | H1927174234 | 80 | Faulted UG Cable & splice @ H1927174234... | 00832 Arevalo, Greg | NC O&E SUP | Faulted cable in H1927174234 caused | 32.6965 | -117.0895 | 2023 | UG UG Cable
OMD0001021315-01 | Emer-Specl Req - Fire/Police/Govt | 2023-07-16 01:09 | 2023-07-15 21:11 | 2023-07-15 21:28 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Weather Damaged Connector | 532-188 | Transformer | 10 | P18375 | 532 | Heat damaged 900a disconnects @ P18375... | 00832 Arevalo, Greg | NC O&E SUP | Heat damaged 900a disconnect connec | 32.5828 | -117.0938 | 2023 | Non Conductor
OMD0001022046-01 | Dmg/Wlite-Other | 2023-07-18 14:55 | 2023-07-18 14:18 | 2023-07-18 14:18 | N | N | N | N | N |  | 12 kV |  | Other/Undetermined | BRUSH FIRE NEAR GOPHER CANYON @ FAIRVIEW. CAUSE OF FIRE UNKNOWN. NO SDGE EQUIPMENT DAMAGED. | Undetermined | 209-1669 | Transformer | 25 |  | 209 |  | 07093 Lasua, Keoni | NC O&E SUP | BRUSH FIRE NEAR GOPHER CANYON @ FAI | 33.2492 | -117.2201 | 2023 | Other All
OMD0001030539-01 | Dmg/Wlite-Xfmr/Grn Box Flash/Sprk | 2023-08-20 12:32 | 2023-08-20 11:53 | 2023-08-20 12:05 | Y | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Weather Damaged Service | MNR3-91 | Transformer | 25 | P739774 | MNR3 |  | 00832 Arevalo, Greg | NC O&E SUP | BP @ this home noticed smoke & flas | 32.7672 | -117.1052 | 2023 | Other All
OMD0001030595-01 | Dmg Dim/Nolite-WireDown Pole to H | 2023-08-20 11:53 | 2023-08-20 10:06 | 2023-08-20 11:05 | Y | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Service Down | 366-292 | Transformer | 100 | P2149973785 | 366 | Burnt open copper stranded service... | 00832 Arevalo, Greg | NC O&E SUP | Copper stranded service wire burnt | 32.7547 | -117.1035 | 2023 | Conductor
OMD0001030628-01 | Transformer Outage | 2023-08-20 15:25 | 2023-08-20 15:18 | 2023-08-20 15:18 | N | N | N | N | Y | Arching/Charring |  | 240 V | Other/Undetermined | Copper stranded service failure... | Weather Damaged Service | BRM1-41 | Transformer | 50 | P2141573242 | BRM1 | 30ft faulted #4 copper service from P2141573242 in alley... | 00832 Arevalo, Greg | NC O&E SUP | Copper stranded service failed @ ho | 32.7523 | -117.1212 | 2023 | Conductor
OMD0001030645-01 | No Lights - Cause Unknown | 2023-08-20 12:49 | 2023-08-20 12:32 | 2023-08-20 12:32 | N | N | N | N | Y | Arching/Charring |  | 240 V | Electric Facility | Failure of copper stranded service... | Weather Damaged Service | MNR3-91 | Transformer | 25 | P739774 | MNR3 | Copper stranded service failure @ P739774... | 00832 Arevalo, Greg | NC O&E SUP | Copper stranded service failed @ P7 | 32.7672 | -117.1052 | 2023 | Conductor
OMD0001030823-01 | Dmg/Wlite-Other | 2023-08-20 17:05 | 2023-08-20 15:27 | 2023-08-20 15:42 | N | N | N | N | N | Arching/Charring |  | 240 V | Other/Undetermined | Copper stranded service... | Weather Damaged Service | MT1-107 | Transformer | 25 |  | MT1 | Copper stranded service wire bruning in multiple spots... | 00832 Arevalo, Greg | NC O&E SUP | Weather damaged secondary smolderin | 32.7407 | -117.1775 | 2023 | Conductor
OMD0001030829-01 | No Lights in Part-Just Started | 2023-08-20 17:35 | 2023-08-20 17:05 | 2023-08-20 17:05 | N | N | N | N | N | Arching/Charring |  | 240 V | Contact by Object | Copper stranded service... | Weather Damaged Service | MT1-107 | Transformer | 25 |  | MT1 |  | 00832 Arevalo, Greg | NC O&E SUP | Copper stranded service wire faulte | 32.7407 | -117.1775 | 2023 | Conductor
OMD0000966284-01 | Flickering Lights-Just Started | 2022-12-19 16:56 | 2022-12-19 11:47 | 2022-12-19 11:58 | N | N | N | N | N | Arching/Charring |  | 208 V | Other/Undetermined | MAY BE OVERLOAD ON SECONDARY | Connector Damaged | 41-482 | Three Phase Transformer | 500 | D166746 | 41 | REPAIRS TO SECONDARY 2 RUNS OF MILLION FROM STA 41-482 TO CU | 10056 Gomez, Miguel | CM O&E SUP | CREW TO MAKE REPAIRS TO MILLION SEC | 32.6805 | -117.0884 | 2022 | UG Connector
OMD0001038703-01 | Momentary Outage | 2023-09-14 22:23 | 2023-09-14 22:07 | 2023-09-14 22:07 | N | N | N | N | Y | Arching/Charring | 12 kV |  | Electric Facility |  | Moter Vehicle Contact with Pole | SW-12KV-43 | Circuit |  | P835332 | 43 |  | 00832 Arevalo, Greg | NC O&E SUP | Road One towing contacted overhead | 32.6695 | -117.1119 | 2023 | Vehicle
OMD0001054855-01 | Circuit Outage | 2023-11-19 13:01 | 2023-11-19 09:34 | 2023-11-19 10:27 | N | N | N | N | Y | Arching/Charring | 12 kV |  | Electric Facility |  | Damaged Underground Cable | S-12KV-130 | Circuit |  | Cir 130 Getaway cable | 130 |  | 00832 Arevalo, Greg | NC O&E SUP | Primary getaway cable failed inside |  |  | 2023 | UG UG Cable
OMD0000973808-01 | No Lights in Part-Just Started | 2023-01-17 15:41 | 2023-01-17 14:08 | 2023-01-17 14:08 | Y | N | N | N | N | Arching/Charring |  | 480 V | Electric Facility |  | Connector Damaged | 364-215 | Transformer | 500 | D125734 | 364 |  | 00832 Arevalo, Greg | NC O&E SUP | Faulted 2 hole lugs in station caus | 32.7416 | -117.0988 | 2023 | UG Connector
OMD0001057373-01 | Dmg/Wlite-Wire Down Pole to Pole | 2023-11-30 08:25 | 2023-11-30 08:00 | 2023-11-30 08:00 | N | N | N | N | N | Arching/Charring |  | 240 V | Other/Undetermined | WEATHER COMPROMISED THE INSULATION ON A COPPERWELD SERVICE. PS LEGS BURNED TOGETHER AND THE SERVICE CAME DOWN. | Weather Damaged Service | VS1-237 | Transformer | 25 | P417525 | VS1 | BURNED OPEN COPPERWELD SERVICE | 07093 Lasua, Keoni | NC O&E SUP | RAIN CAUSED OLD COPPERWELD SERVICE | 33.218 | -117.2515 | 2023 | Conductor
OMD0001059762-01 | Emer-Specl Req - Fire/Police/Govt | 2023-12-09 10:37 | 2023-12-09 09:23 | 2023-12-09 09:46 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | FUSE CORRODED & BROKE - DOOR DID NOT DROP & WAS TRACKING, CHARED & SMOKING | Device Damaged | 1081-180 | Transformer | 50 | P220087 | 1081 |  | 30566 Garegnani, Dominic | NC O&E SUP | FUSE CORRODED & BROKE AT P22087 - C | 33.0146 | -117.2782 | 2023 | Non Conductor
OMD0001059777-01 | Branch Outage | 2023-12-09 13:34 | 2023-12-09 11:24 | 2023-12-09 11:54 | N | N | N | Y | N |  | 12 kV |  | Contact by Object | Mylar blanket phase to phase contact between P31630 & P31631... | Foreign Object Contact Conductor | 443-218R | Recloser |  |  | 443 |  | 00832 Arevalo, Greg | NC O&E SUP | Outage caused by mylar blanket cont | 32.5428 | -117.0425 | 2023 | Balloon
OMD0001063687-01 | Dmg/Wlite-Flash or Sparks | 2023-12-28 13:18 | 2023-12-28 11:27 | 2023-12-28 12:07 | N | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility | KEARNY ONE BOLT SECONDARY CONNECTION OVER HEATED & CAUSED SEC. WIRE TO BURN DOWN | Wire Down | 289-161 | Transformer | 50 | P25905 | 289 |  | 30566 Garegnani, Dominic | NC O&E SUP |  | 33.0401 | -117.2945 | 2023 | Non Conductor
OMD0001064130-01 | Dmg/Wlite-Other | 2023-12-30 20:44 | 2023-12-30 20:36 | 2023-12-30 20:36 | N | N | N | N | N | Arching/Charring | 4 kV |  | Electric Facility | KEARNY CUTOUT ARCING AND BURNING AT CUTOUT -DOOR CONTACT W/ CUTOUT BODY - DUE TO COSTAL CORROSION - SPARKS FELL BUT GRASS IS WET DUE TO RAIN - NO IGNITION | Device Damaged | OS1-128 | Transformer | 25 | P23530 | OS1 | BURNT/ BROKEN KEARNY CUTOUT (150AMP QA FUSE) P23530 | 30566 Garegnani, Dominic | NC O&E SUP | CRACKED & BURNING CUTOUT W/150AMP Q | 33.1935 | -117.3721 | 2023 | Non Conductor
OMD0001070191-01 | Emer-Specl Req - Fire/Police/Govt | 2024-01-22 14:40 | 2024-01-22 12:00 | 2024-01-22 12:07 | N | N | N | N | Y | Arching/Charring | 12 kV |  | Vegetation Contact | Signs of arcing only on insulators at pole top. No damage to surrounding vegetation | Tree Damaged Conductor | 1081-290 | Transformer | 75 | Z24529 | 1081 | Tree branch on primary @ Z24529. Causing primary neutral wi | 02734 Willis, Brian | NC O&E SUP | Tree down on primary @ Z24529 causi | 33.0355 | -117.2728 | 2024 | Veg
OMD0001078278-01 | Emer-Specl Req - Fire/Police/Govt | 2024-02-18 03:37 | 2024-02-18 02:30 | 2024-02-18 02:30 | N | N | N | N | N |  |  | 240 V | Other/Undetermined | A FIRE WAS STARTED IN ALLEY BEHIND 303 S COAST HWY, O'SIDE. THE CAUSE IS BELIEVED TO BE BY TRANSIENT(S). THE FIRE BURNED DOWN THE 120' #4SSC CU SERVICE FROM P20363 TO WEATHERHEAD OF MTR #5669090. IT ALSO BURNED THE PANELS UP FOR 301 & 305 S | Service Vandalism | 580-624 | Transformer | 50 |  | 580 | DAMAGED SERVICE FROM FIRE | 07093 Lasua, Keoni | NC O&E SUP | SERVICE WAS BURNED TO THE GROUND DU | 33.1926 | -117.3773 | 2024 | Other All
OMD0001078294-01 | No Lights - Cause Unknown | 2024-02-18 08:18 | 2024-02-18 07:44 | 2024-02-18 08:07 | N | N | N | N | N |  | 12 kV |  | Other/Undetermined | Dumpster fire next to building and electrical equipment | Vandalism | 580-624 | Transformer | 50 |  | 580 |  | 11288 Ott, Frank | NC O&E SUP | Dumpster fire next to building and | 33.1926 | -117.3773 | 2024 | Other All
OMD0001088970-01 | Emer-Specl Req - Fire/Police/Govt | 2024-03-29 18:18 | 2024-03-29 15:39 | 2024-03-29 16:08 | N | N | N | N | Y |  |  | 240 V | Other/Undetermined | House fire caused by homeowner. No damage to SDGE deenergized service at transformer for safety. | Customer Problem | 783-253 | Transformer | 25 |  | 783 | Garage fire deenergized service at D3685067906. Crew will n | 02734 Willis, Brian | NC O&E SUP | Homeowner caused fire in garage. Fo | 33.1756 | -117.2995 | 2024 | Other All
OMD0001093647-01 | Emer-Specl Req - Fire/Police/Govt | 2024-04-16 22:00 | 2024-04-16 20:11 | 2024-04-16 20:11 | N | N | N | N | Y |  |  | 120 V | Other/Undetermined | CAR FIRE NEAR THE HOUSE | Service Deenergized For Safety | 286-112 | Transformer | 50 |  | 286 |  | 07093 Lasua, Keoni | NC O&E SUP | BOOTED MTR FOR SAFETY. CUSTOMER IS | 33.076 | -117.289 | 2024 | Other All
OMD0001097598-03 | Circuit Outage | 2024-05-03 13:28 | 2024-05-03 13:26 | 2024-05-03 13:26 | N | N | N | N | N |  | 12 kV |  | Vegetation Contact |  | Equipment Contacted Conductor | MH-12KV-486 | Circuit |  |  | 486 |  | E4369 Broff, Nicholas | NC O&E SUP |  |  |  | 2024 | Veg
OMD0001097601-01 | Emer-Specl Req - Fire/Police/Govt | 2024-05-03 13:25 | 2024-05-03 11:31 | 2024-05-03 12:39 | N | N | N | N | N |  | 12 kV |  | Vegetation Contact |  | Equipment Contacted Conductor | 486-164 | Transformer | 25 | p114087 | 486 | wire down, one span, approx 500' #6 CU. | E4369 Broff, Nicholas | NC O&E SUP | excavator contacted wire, mid span. | 33.2628 | -117.2803 | 2024 | Veg
OMD0001101830-01 | Emer-Specl Req - Fire/Police/Govt | 2024-05-21 15:55 | 2024-05-21 13:31 | 2024-05-21 13:31 | Y | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Connector Damaged | 1049-178 | Transformer | 75 | SH81687 | 1049 | Faulted 4 way secondary molds in SH81687 | 00832 Arevalo, Greg | NC O&E SUP | 3 - 4way molds faulted in SH81687 c | 32.7244 | -117.0797 | 2024 | UG Connector
OMD0001105365-01 | Circuit Outage | 2024-06-06 12:40 | 2024-06-06 07:32 | 2024-06-06 07:55 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Equipment Contacted Conductor | MH-12KV-486 | Circuit |  | p114087 | 486 | trackhoe contact to 12kv oh wire between P114087 & P114088 , | 73442 Rodman, Roland | NC O&E SUP | trackhoe contact to 12kv oh wire be | 33.2627 | -117.2793 | 2024 | Conductor
OMD0000976181-03 | Branch Outage | 2023-01-24 15:46 | 2023-01-24 14:27 | 2023-01-24 14:48 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | INSULATORS IN D3541175776 FLASHED OVER | Device Damaged | F434117 | Fuse | 150A | D3541175776 | 456 | REPLACE FAILED 3PH FUSE CABINET | 21460 Davis, John | NE O&E SUP | FUSE CABINET D3541175776 FAILED, NE | 33.1379 | -117.0418 | 2023 | UG Fuse
OMD0001107696-01 | Dmg/Wlite-Flash or Sparks | 2024-06-16 05:35 | 2024-06-16 02:56 | 2024-06-16 03:16 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Weather Damaged Connector | 103-99 | Transformer | 25 | P2239270726 | 103 | Not sure if this has been turned in but can we have a crew f | 00832 Arevalo, Greg | NC O&E SUP | Faulted primary connection on 12kv | 32.7782 | -117.2036 | 2024 | Non Conductor
OMD0001108292-01 | Emer-Specl Req - Fire/Police/Govt | 2024-06-19 02:27 | 2024-06-18 22:17 | 2024-06-18 23:02 | N | N | N | N | Y |  |  | 120 V | Other/Undetermined | OCEANSIDE FIRE INVESTIGATOR DID NOT DETERMINE THE CAUSE | Service Deenergized For Safety | 190-721 | Transformer | 75 |  | 190 |  | 07093 Lasua, Keoni | NC O&E SUP | STRUCTURE FIRE. FIRE NOT CAUSED BY | 33.2473 | -117.3264 | 2024 | Other All
OMD0001109721-01 | Voltage Problem-Low/Just Start | 2024-06-24 23:55 | 2024-06-24 21:41 | 2024-06-24 22:41 | N | N | N | N | N | Arching/Charring |  | 240 V | Other/Undetermined | LOOKS LIKE AN OVERLOAD ISSUE OR CORRODED CONNECTION ON THE CUSTOMER'S MAIN. | Customer Problem | 904-37 | Transformer | 50 |  | 904 |  | 07093 Lasua, Keoni | NC O&E SUP | CUSTOMER HAS MELTED BUS WORK INSIDE | 33.2227 | -117.3 | 2024 | Non Conductor
OMD0000981960-01 | Emer-Specl Req - Fire/Police/Govt | 2023-02-17 03:58 | 2023-02-17 00:48 | 2023-02-17 01:29 | N | N | N | N | N | Arching/Charring |  | 208 V | Electric Facility | sec UG cble failure heat at cst pnl | Weather Damaged Service | 91-665 | Transformer | 150 | D135814 | 91 | D135814 C/O 2 RUNS 350 UG SEC 4 WIRE 200' EACH TO CIRCLE K. | 05036 Burrell, Dennis | EA O&E SUP | D135814 C/O 2 RUNS 350 UG SEC 4 WIR | 32.7397 | -116.9393 | 2023 | UG Connector
OMD0001120939-01 | Emer-Specl Req - Fire/Police/Govt | 2024-08-07 14:02 | 2024-08-07 12:26 | 2024-08-07 12:39 | Y | N | N | N | N |  |  | 240 V | Other/Undetermined | Electrician changing out Panel and fire broke out in the attic. | Customer Problem | 752-152 | Transformer | 25 |  | 752 |  | 07093 Lasua, Keoni | NC O&E SUP | Electrician was changing out a pane | 33.0844 | -117.2654 | 2024 | Other All
OMD0001124337-01 | Branch Outage | 2024-08-20 17:14 | 2024-08-20 13:59 | 2024-08-20 17:11 | Y | N | N | N | N |  | 12 kV |  | Vegetation Contact | SEMI TRUCK HIT A LOW HANGING TELCO TRUNK LINE CAUSINE THE PRIMARY TO DIP DOWN AND CONTACT A PALM TREE. | Conductor Damaged | F614693 | Fuse | 150A |  | 194 |  | 07093 Lasua, Keoni | NC O&E SUP | Semi Truck hit telco trunk line tha | 33.2191 | -117.3395 | 2024 | Vehicle
OMD0001127291-01 | Dmg Dim/Nolite - Flash or Sparks | 2024-08-29 21:14 | 2024-08-29 20:13 | 2024-08-29 20:34 | N | N | N | N | N | Arching/Charring | 4 kV |  | Electric Facility | 4KV CUTOUT WAS BURNING & SPARKS FALLING INTO TREE & GROUND - NO IGNITION | Device Damaged | EOS2-68 | Transformer | 50 | P120396 | EOS2 | BURNING 4KV CUTOUT AT STA. EOS2-12 P120396 - | 30566 Garegnani, Dominic | NC O&E SUP | BURNT 4KV CUTOUT AT P120396 FOR STA | 33.1802 | -117.3646 | 2024 | Non Conductor
OMD0001129167-02 | Branch Outage | 2024-09-05 22:57 | 2024-09-05 21:14 | 2024-09-05 21:29 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | BLOWN/ BURNING LIGHTNING ARRESTOR AT P121121 | Weather Damaged Device | F2515239 | Fuse | 150A | P121121 | 288 | PLEASE FOLLOW UP TO REPLACE 3- 12KV LIGHTNING ARRESTORS AT P | 30566 Garegnani, Dominic | NC O&E SUP | BLOWN LIGHTNING ARRESTOR AT P121121 | 33.0432 | -117.2814 | 2024 | Non Conductor
OMD0001134656-01 | Circuit Outage | 2024-09-19 18:37 | 2024-09-19 17:09 | 2024-09-19 17:09 | N | N | N | N | N | Arching/Charring | 12 kV |  | Contact by Object |  | Foreign Object Contact Conductor | CAN-12KV-780 | Circuit |  | p20865 and p20866 | 780 | 2-wire one span down | 70169 Ransom, Ryan | NC O&E SUP | excavator hit wire |  |  | 2024 | Other Contact
OMD0001141459-01 | Dmg/Wlite-Wire Down Pole to Pole | 2024-10-16 14:09 | 2024-10-16 13:55 | 2024-10-16 13:55 | N | N | N | N | N | Arching/Charring | 12 kV |  | Contact by Object |  | Conductor Damaged | 303-994 | Transformer | 25 |  | 303 | wire down | 70169 Ransom, Ryan | NC O&E SUP |  | 33.1601 | -117.3364 | 2024 | Other Contact
OMD0000994472-01 | Dmg/Wlite-Xfmr/Grn Box Flash/Sprk | 2023-03-27 20:03 | 2023-03-27 16:59 | 2023-03-27 17:08 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Connector Damaged | 550-323 | Three Phase Transformer | 750 | D117153 | 550 | hot connections melted off and made contact with inside of s | B0278 Dawson, Garth R | EA O&E SUP | hot connections melted off and made | 32.8086 | -116.9779 | 2023 | UG Connector
OMD0001149360-01 | Dmg/Wlite-Other | 2024-11-18 10:13 | 2024-11-18 09:54 | 2024-11-18 09:54 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Weather Damaged Device | 780-205 | Transformer | 50 | P120796 | 780 | P120796 CIR 780 DAMAGED INSULATORS & CROSSARM FROM SEVERE TR | 30566 Garegnani, Dominic | NC O&E SUP | P120796 CIR 780 DAMAGED INSULATORS | 33.0958 | -117.3161 | 2024 | Non Conductor
OMD0001160896-01 | Dmg/Wlite-Flash or Sparks | 2025-01-07 20:59 | 2025-01-07 18:30 | 2025-01-07 18:52 | N | N | N | N | Y | Arching/Charring | 12 kV |  | Electric Facility |  | Heat Device/Overload | 1406-665 | Transformer | 167 | P235831 | 1406 | Heat damaged under arm hookstick switch... | 00832 Arevalo, Greg | NC O&E SUP | Heat damaged underarm hookstick swi | 33.2471 | -117.313 | 2025 | Non Conductor
OMD0001166880-01 | Dmg/Wlite-Wire Down Pole to Pole | 2025-01-26 07:20 | 2025-01-26 07:18 | 2025-01-26 07:18 | N | N | N | N | N | Arching/Charring |  | 240 V | Other/Undetermined | AN OLD SERVICE GOT WET IN THE RAIN AND BURNT DOWN | Weather Damaged Service | 506-397 | Transformer | 50 |  | 506 |  | 01826 Fowley, Jack | NC O&E SUP | THE SERVICE FOR 4029 SCOTT DR BURNT | 33.1912 | -117.2881 | 2025 | Conductor
OMD0000644634-01 | Branch Outage | 2019-07-16 09:46 | 2019-07-16 07:28 | 2019-07-16 08:24 | Y | N | N | Y | N | Actual Ignition | 12 kV |  | Vegetation Contact |  | Conductor Damaged | F515180 | Fuse | 20A | P114648 | 183 |  | 53699 Marshall, Jim | NE O&E SUP | WIRE DOWN P114648 TO P114649. | 33.1665 | -117.146 | 2019 | Veg
OMD0000644634-02 | Branch Outage | 2019-07-16 09:44 | 2019-07-16 07:38 | 2019-07-16 08:27 | Y | Y | N | Y | N | Actual Ignition | 12 kV |  | Electric Facility | 12KV WIRE DOWN, PHASE TO PHASE 12 KV FAULT ON OVERHEAD CONDUCTORS | Wire Down | F515180 | Fuse | 20A | P114649 | 183 | 12KV WIRE DOWN | 21460 Davis, John | NE O&E SUP | WIRE DOWN, NEED CREW TO MAKE REPAIR | 33.1675 | -117.146 | 2019 | Non Conductor
OMD0000644852-01 | Branch Outage | 2019-07-17 00:15 | 2019-07-16 20:03 | 2019-07-16 20:12 | Y | N | Y | Y | N | Actual Ignition | 12 kV |  | Electric Facility | WIRE DOWN, CAUSED BY FALLEN TREE ACROSS TELCO LINES | Tree Damaged Pole | F514527 | Fuse | 150A | P610712 | 1039 |  | 21460 Davis, John | NE O&E SUP |  | 33.182 | -117.1125 | 2019 | Non Conductor
OMD0001027217-01 | Circuit Outage | 2023-08-08 05:45 | 2023-08-08 04:19 | 2023-08-08 04:19 | Y | Y | N | N | N |  | 12 kV |  | Electric Facility | Primary metering 258-63M blew up | Device Damaged | MG-12KV-258 | Circuit |  | D103552 | 258 |  | 02819 Patrick, Damion | CM O&E SUP | Customer’s off of 12KV cir. 258 Pri | 32.6324 | -117.0997 | 2023 | Undetermined
OMD0000646190-01 | Voltage Problem-Low/Just Start | 2019-07-23 07:34 | 2019-07-23 06:45 | 2019-07-23 07:00 | N | N | N | N | Y | Arching/Charring |  | 208 V | Other/Undetermined | BURNT TEST BLOCK AT METER PANEL, CUSTOMER EQUIPMENT. INSTALLED TEST BLOCK JUMPER. HEAT RISK IS NOW ELIMINATED | Customer Problem | 181-234 | Three Phase Transformer | 75 |  | 181 |  | 21460 Davis, John | NE O&E SUP | FOUND FAILED TEST BLOCK, INSATLLED | 33.121 | -117.1105 | 2019 | Non Conductor
OMD0000646973-01 | Dmg/Wlite-Flash or Sparks | 2019-07-25 12:13 | 2019-07-25 11:08 | 2019-07-25 11:20 | N | N | N | N | Y | Arching/Charring | 12 kV |  | Contact by Object |  | Foreign Object Contacted Device | 354-1002 | Transformer | 25 | Z104944 | 354 |  | 56561 McKeown, John | NE O&E SUP |  | 33.2554 | -117.0864 | 2019 | Other Contact
OMD0000647039-01 | Transformer Outage | 2019-07-25 13:43 | 2019-07-25 12:49 | 2019-07-25 12:58 | N | N | N | N | Y | Arching/Charring | 12 kV | 120 V | Electric Facility |  | Transformer Problem | 454-73 | Transformer | 167 | P419929 | 454 | DAMAGED TRANSFORMER & SECONDARY | 53699 Marshall, Jim | NE O&E SUP | CREW TO CHANGE OUT 454-73 & REPAIR | 33.1495 | -117.0687 | 2019 | Non Conductor
OMD0000649047-02 | Branch Outage | 2019-08-01 14:29 | 2019-08-01 13:19 | 2019-08-01 13:44 | N | N | N | N | Y | Arching/Charring | 12 kV |  | Electric Facility |  | Connector Damaged | <inline_jumper.11983> |  |  | P613575 | 474 |  | 56561 McKeown, John | NE O&E SUP |  | 33.2174 | -117.0318 | 2019 | Non Conductor
OMD0000650597-01 | Emer-Subst Unlock/Open/Expos Wir | 2019-08-07 19:39 | 2019-08-07 18:14 | 2019-08-07 19:32 | Y | N | N | N | N | Actual Ignition |  | 120 V | Electric Facility | CUSTOMER PROBLEM | Service Deenergized For Safety | 908-191 | Transformer | 25 | CUSTOMER METER PANEEL | 908 |  | 56561 McKeown, John | NE O&E SUP | SERVICE REMOVED CUSTOMER NEEDS TO R | 33.2458 | -117.0129 | 2019 | Non Conductor
OMD0000651291-01 | Emer-Specl Req - Fire/Police/Gov | 2019-08-10 15:09 | 2019-08-10 13:19 | 2019-08-10 14:05 | N | N | N | N | Y | Actual Ignition | 12 kV |  | Other/Undetermined | VEG FIRE NO DAMAGE TO SDG&E EQUIPMENT | Fire Damaged Wire | 520-555 | Transformer | 25 |  | 520 |  | 56561 McKeown, John | NE O&E SUP |  | 33.4294 | -117.325 | 2019 | Other All
OMD0000651832-01 | No Lights - Cause Unknown | 2019-08-13 11:10 | 2019-08-13 08:54 | 2019-08-13 10:07 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Device Damaged | 214-395 | Transformer | 25 | P133122 | 214 |  | 56561 McKeown, John | NE O&E SUP | REPLACED CUTOUT DOOR P133122 | 33.3417 | -116.856 | 2019 | Non Conductor
OMD0000652053-01 | Branch Outage | 2019-08-14 10:35 | 2019-08-14 07:06 | 2019-08-14 07:37 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Device Damaged | 204-32R | Recloser |  | P227184 | 204 | NEED TO REPLACE LA ON P227184. LA BLOWN IN THE CLEAR. MADE S | 05221 Clovis, Chad | NE O&E SUP | FOUND LA BLOWN IN THE CLEAR. LA LYI | 33.3796 | -117.5632 | 2019 | Non Conductor
OMD0000652250-01 | Dmg/Wlite-Other | 2019-08-14 16:31 | 2019-08-14 15:56 | 2019-08-14 15:56 | Y | N | N | Y | N | Actual Ignition |  | 120 V | Other/Undetermined | SERVICE BURNT OPEN MIDSPAN CAUSING MOLTEN METAL TO IGNITE WEEDS ON GROUND | Service Deenergized For Safety | 517-328 | Transformer | 75 | P313496 | 517 | BURNT OPEN SERVICE | 53699 Marshall, Jim | NE O&E SUP | CREW TO REPLACE BURNT OPEN SERVICE. | 33.1156 | -117.1037 | 2019 | Conductor
OMD0000658984-01 | No Lights - Cause Unknown | 2019-09-07 14:17 | 2019-09-07 12:54 | 2019-09-07 14:09 | N | N | N | N | N | Arching/Charring |  | 480 V | Electric Facility |  | Conductor Damaged | 350-859 | Transformer | 300 | P410137 | 350 |  | 53699 Marshall, Jim | NE O&E SUP | SERVICE BURNT OPEN AT POLE. REPLACE | 33.2811 | -117.108 | 2019 | Conductor
OMD0000659923-01 | Emer-Specl Req - Fire/Police/Gov | 2019-09-11 16:36 | 2019-09-11 14:34 | 2019-09-11 15:05 | N | N | Y | Y | N | Arching/Charring | 12 kV |  | Contact by Object | BIRD CONTACT FLW-UP MADE TO FIRE COORDINATOR BY ON DUTY SUP | Device Damaged | 351-68 | Transformer | 25 | P228412 | 351 | DAMAGED LIGHTNING ARRESTORS | 56561 McKeown, John | NE O&E SUP | DAMAGED LIGHTNING ARRESTORS P22 | 33.2261 | -117.084 | 2019 | Animal
OMD0000661816-01 | Emer-Specl Req - Fire/Police/Gov | 2019-09-19 08:38 | 2019-09-19 07:08 | 2019-09-19 07:36 | Y | N | N | N | N | Actual Ignition | 12 kV |  | Electric Facility | SECONDARY CONNECTION STARTED FIRE ON POLE | Connector Damaged | 249-548 | Transformer | 50 | P815302 | 249 |  | 02479 Fergerson, Mike | NE O&E SUP | REPAIRED OVERHEAD SERVICE | 33.3664 | -117.0841 | 2019 | Non Conductor
OMD0000664192-03 | Circuit Outage | 2019-09-28 12:08 | 2019-09-28 10:55 | 2019-09-28 10:55 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Device Damaged | ES-12KV-180 | Circuit |  | P217429 | 180 | BLOWN LIGHTNING ARRESTORS | 53699 Marshall, Jim | NE O&E SUP | CREW TO REPLACE BLOWN LIGHTNING ARR | 33.1471 | -117.122 | 2019 | Non Conductor
OMD0000668444-01 | Emer-Specl Req - Fire/Police/Gov | 2019-10-15 20:22 | 2019-10-15 18:54 | 2019-10-15 19:05 | N | N | N | Y | Y | Actual Ignition | 12 kV |  | Other/Undetermined | Homeless started fire at base of pole | Vandalism | 519-420 | Transformer | 50 | P17483 | 519 | POLE FIRE REPLACE SECONDARY WIRE | 02479 Fergerson, Mike | NE O&E SUP |  | 33.1281 | -117.0745 | 2019 | Other All
OMD0000671043-01 | Emer-Specl Req - Fire/Police/Gov | 2019-10-25 15:44 | 2019-10-25 03:55 | 2019-10-25 03:59 | Y | N | Y | Y | N | Actual Ignition | 12 kV |  | Electric Facility | FAULTED UG CABLE AT POLE CAUSED 3 ACRE BRUSH FIRE | Damaged Underground Cable | 597-575 | Transformer | 50 | P211697 | 597 | REPLACE DAMAGED POTHEAD | 21460 Davis, John | NE O&E SUP | CABLE FAULT CAUSED BRUSH FIRE AT P2 | 33.1212 | -117.1648 | 2019 | OH to UG
OMD0000677471-01 | Emer-Specl Req - Fire/Police/Gov | 2019-11-16 03:54 | 2019-11-16 02:07 | 2019-11-16 02:50 | N | Y | N | N | N | Actual Ignition |  | 120 V | Other/Undetermined | Structure Fire Elec Panel not Affected by Fire | Undetermined | LA3-13 | Transformer | 47.5 |  | LA3 |  | 06594 Schelhorn, Brian | NE O&E SUP | Structure Fire Home Unsalvageable | 32.6684 | -117.0723 | 2019 | Other All
OMD0000680476-01 | No Lights - Cause Unknown | 2019-11-26 09:53 | 2019-11-26 09:05 | 2019-11-26 09:09 | Y | N | N | N | N | Arching/Charring |  | 240 V | Other/Undetermined | SERVICE WIRE OVERLOAD | Weather Damaged Service | 1030-767 | Transformer | 25 |  | 1030 | DAMAGED 4 SSC AL SERVICE WIRE OVERLOAD | 56561 McKeown, John | NE O&E SUP |  | 33.2131 | -116.9782 | 2019 | Conductor
OMD0000684721-01 | Transformer Outage | 2019-12-09 16:04 | 2019-12-09 15:02 | 2019-12-09 15:33 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | cutout door | Fuse Operated in Transformer | 215-852 | Transformer | 35 | p815839 | 215 |  | 56561 McKeown, John | NE O&E SUP |  | 33.2637 | -116.9971 | 2019 | Non Conductor
OMD0000694652-01 | Emer-Specl Req - Fire/Police/Gov | 2020-01-17 06:56 | 2020-01-17 06:32 | 2020-01-17 06:32 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | ARCING AND FIRE AT POLE TOP ONLY, NO FIRE PRESENT UPON MY ARRIVAL. | Device Deenergized for Safety | 187-1228 | Transformer | 25 | P330233 | 187 |  | 21460 Davis, John | NE O&E SUP | CAP STA 187-123CF FAILED, ISOLATED | 33.1308 | -117.0964 | 2020 | Non Conductor
OMD0000697537-01 | Branch Outage | 2020-01-29 12:09 | 2020-01-29 10:57 | 2020-01-29 11:10 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Contact by Object |  | Transformer Problem | F515662 | Fuse | 100A | 450-530 | 450 | DAMAGED 25 HE | 56561 McKeown, John | NE O&E SUP |  | 33.1829 | -117.088 | 2020 | Other Contact
OMD0000697975-01 | Emer-Specl Req - Fire/Police/Gov | 2020-01-30 23:08 | 2020-01-30 21:04 | 2020-01-30 21:39 | N | N | N | N | N | Arching/Charring |  | 120 V | Other/Undetermined | OH SERVICE BURNED OPEN, INSULATION FAILED | Open Neutral | 351-281 | Transformer | 15 |  | 351 |  | 21460 Davis, John | NE O&E SUP | OH SVC BURNED OPEN AT WEATHERHEAD, | 33.2014 | -117.0909 | 2020 | Non Conductor
OMD0000698544-01 | Dmg Dim/Nolite-WireDown Pole to | 2020-02-03 08:08 | 2020-02-03 07:00 | 2020-02-03 07:43 | Y | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility | INSULATION ON SSC OH SERVICE FAILED, SERVICE WIRE BURNED DOWN | Weather Damaged Service | 454-259 | Transformer | 25 | P417368 | 454 | OH SERVICE DOWN | 21460 Davis, John | NE O&E SUP | OH SERVICE BURNT DOWN, CALLED FOR C | 33.1481 | -117.0606 | 2020 | Conductor
OMD0000713263-01 | Emer-Specl Req - Fire/Police/Gov | 2020-04-02 00:37 | 2020-04-01 23:34 | 2020-04-01 23:54 | Y | N | N | N | N | Arching/Charring |  | 208 V | Electric Facility | CUSTOMER PANEL | Customer Problem | 184-152 | Three Phase Transformer | 225 | 184-152 | 184 |  | 56561 McKeown, John | NE O&E SUP | customer needs to replace meter bas | 33.1139 | -117.1172 | 2020 | Non Conductor
OMD0000722026-01 | Emer-Specl Req - Fire/Police/Gov | 2020-05-06 07:34 | 2020-05-06 07:34 | 2020-05-06 07:34 | Y | N | N | Y | N | Actual Ignition |  | 240 V | Contact by Object | CUSTOMER WIRING SHORTED OUT IN WEATHERTHEAD DUE TO TREE TAKING DOWN OH SVC. ALL FIRE DAMAGE WAS TO STRUCTURE. NO SDGE LINES OR EQUIPMENT DAMAGED BY FIRE, NO VEGETATION FIRE. | Foreign Object Contact Services | 907-89 | Transformer | 25 |  | 907 |  | 21460 Davis, John | NE O&E SUP | TREE FELL OVER AND DAMAGED OH SVC A | 33.21 | -117.0286 | 2020 | Veg
OMD0000725023-03 | Branch Outage | 2020-05-17 11:54 | 2020-05-17 09:08 | 2020-05-17 09:44 | N | N | Y | Y | N | Actual Ignition | 12 kV |  | Contact by Object | mylar balloons contact | Foreign Object Contact Conductor | <inline_jumper.13805> |  |  | p515883 | 908 |  | 53699 Marshall, Jim | NE O&E SUP | MYLAR BALLOONS CONTACT P515883. | 33.2378 | -117.0296 | 2020 | Balloon
OMD0000729417-01 | Emer-Specl Req - Fire/Police/Gov | 2020-06-03 13:00 | 2020-06-03 12:31 | 2020-06-03 12:31 | N | N | Y | N | N | Actual Ignition | 12 kV |  | Contact by Object |  | Foreign Object in Transformer | 788-424 | Transformer | 25 | P714412 | 788 | DAMAGE 25HE TRANSFORMER | 56561 McKeown, John | NE O&E SUP |  | 33.1243 | -117.0241 | 2020 | Other Contact
OMD0000729992-01 | Emer-Specl Req - Fire/Police/Gov | 2020-06-05 11:18 | 2020-06-05 10:28 | 2020-06-05 10:40 | N | Y | N | N | N | Arching/Charring |  | 240 V | Other/Undetermined | INSULATION ON SERVICE CRACKED AND BURNED OPEN SERVICE AT WEATHERHEAD. | Weather Damaged Service | FB1-194 | Transformer | 50 |  | FB1 | REPLACE OH SERVICE | 01324 Serrano, Daniel | NE O&E SUP | Need service crew to replace OH ser | 33.3846 | -117.2487 | 2020 | Conductor
OMD0000730937-01 | Emer-Specl Req - Fire/Police/Gov | 2020-06-09 12:51 | 2020-06-09 11:32 | 2020-06-09 11:39 | N | N | N | Y | N | Actual Ignition |  | 120 V | Other/Undetermined | FIRE NOT CAUSED BY SDGE. | Service Down | 521-687 | Transformer | 30 | P117953 | 521 | REPLACE UG SERVICE AND CONDUIT UP P117953. FIRE MELTED CONDU | 01324 Serrano, Daniel | NE O&E SUP | ROAD SIDE FIRE BURNED SERVICE CONDU | 33.387 | -117.2344 | 2020 | Other All
OMD0000733221-01 | Dmg Dim/Nolite-WireDown Pole to | 2020-06-17 20:34 | 2020-06-17 19:37 | 2020-06-17 20:16 | Y | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility | CUSTOMER PANAL | Service Down | 1094-435 | Transformer | 100 | 1094-435 | 1094 | SECONDARY SERVICE DOWN CUSTOMER WILL CALL WHEN REPAIRS ARE | 56561 McKeown, John | NE O&E SUP |  | 33.1789 | -117.1439 | 2020 | Non Conductor
OMD0000741556-01 | Dmg/Wlite-Pole Burning | 2020-07-18 06:38 | 2020-07-17 21:38 | 2020-07-17 22:56 | N | N | Y | Y | N | Actual Ignition | 12 kV |  | Contact by Object | WOODPECKER CONTACT 221-99 | Foreign Object in Transformer | 221-100 | Transformer | 25 | P218665 | 221 | DAMAGED TRANSFORMER 221-99 | 53699 Marshall, Jim | NE O&E SUP | WOODPECKER CONTACT 221-99. | 33.0683 | -116.5531 | 2020 | Animal
OMD0000744878-02 | Branch Outage | 2020-07-29 19:01 | 2020-07-29 17:25 | 2020-07-29 17:50 | Y | N | N | N | N | Actual Ignition | 12 kV |  | Vegetation Contact |  | Conductor Damaged | <inline_jumper.14367> |  |  | P678395 | 524 |  | 02479 Fergerson, Mike | NE O&E SUP | ASSISTED JEFF D. |  |  | 2020 | Veg
OMD0000749380-03 | Branch Outage | 2020-08-13 10:29 | 2020-08-13 09:06 | 2020-08-13 09:38 | Y | N | N | N | N | Actual Ignition | 12 kV |  | Electric Facility | CAP STA. CAUGHT FIRE | Device Damaged | 386-25R | Recloser |  | P204730 | 386 |  | 02479 Fergerson, Mike | NE O&E SUP |  | 32.832 | -116.9054 | 2020 | Non Conductor
OMD0000750612-01 | Emer-Specl Req - Fire/Police/Gov | 2020-08-16 00:21 | 2020-08-15 23:31 | 2020-08-16 00:02 | Y | N | N | N | N | Arching/Charring |  | 120 V | Other/Undetermined | CUSTOMER PANAL NOT SDG&E PROBLEM | Customer Problem | 523-242 | Transformer | 25 |  | 523 |  | 56561 McKeown, John | NE O&E SUP | OFF AT METER FOR CUSTOMER REPAIR | 33.3819 | -117.2389 | 2020 | Non Conductor
OMD0000755541-02 | Circuit Outage | 2020-08-31 16:25 | 2020-08-31 13:50 | 2020-08-31 14:04 | Y | N | Y | Y | N | Actual Ignition | 12 kV |  | Vegetation Contact |  | Wire Down | FE-12KV-470 | Circuit |  | P310131 | 470 |  | 21460 Davis, John | NE O&E SUP |  | 33.1092 | -117.005 | 2020 | Veg
OMD0001028386-01 | Transformer Outage | 2023-08-11 16:16 | 2023-08-11 15:06 | 2023-08-11 15:35 | N | N | N | N | N | Arching/Charring |  | 120 V | Other/Undetermined | MELTED SEC CONNECTOR IN TRANSFORMER | Connector Damaged | 564-1331 | Transformer | 50 | D5202756764 | 564 | BAD SEC CONNECTIONS IN STA 564-1331... | 00462 Macias, Damian | OC O&E SUP | LOOKS LIKE SECONDARY CONNECTIONS BU | 33.5886 | -117.6704 | 2023 | UG Connector
OMD0000756789-01 | Emer-Specl Req - Fire/Police/Gov | 2020-09-04 15:08 | 2020-09-04 13:19 | 2020-09-04 13:34 | Y | N | N | N | N | Actual Ignition |  | 240 V | Other/Undetermined | STRUCTURE FIRE, METER PANEL, METER AND UG SVC DAMAGED BY FIRE. I THINK THIS AS A CUSTOMER CAUSED ELECTRIC FIRE | Customer Problem | 790-680 | Transformer | 50 |  | 790 |  | 21460 Davis, John | NE O&E SUP | DE-ENERGIZED UG SVC DUE TO STRUCTUR | 33.0662 | -117.0547 | 2020 | Other All
OMD0000760040-01 | Emer-Specl Req - Fire/Police/Gov | 2020-09-11 10:51 | 2020-09-11 07:34 | 2020-09-11 08:04 | Y | Y | N | N | N | Actual Ignition | 12 kV |  | Contact by Object | CAR HIT P217780, WIRE WAS BURNING IN TREE'S | Moter Vehicle Contact with Pole | 521-253 | Transformer | 25 | P217780 | 521 | CAR VS POLE, P217780, CR521 | 01324 Serrano, Daniel | NE O&E SUP | CAR HIT P217780, SENT IN DAF FOR RE | 33.3797 | -117.2088 | 2020 | Vehicle
OMD0000760244-01 | Emer-Specl Req - Fire/Police/Gov | 2020-09-11 18:09 | 2020-09-11 16:25 | 2020-09-11 16:57 | N | N | N | N | Y | Arching/Charring |  | 120 V | Other/Undetermined | HOUSE FIRE | Company Shut-Off | 790-674 | Transformer | 50 |  | 790 |  | 56561 McKeown, John | NE O&E SUP | DE-ENERGIZED SERVICE AT TRANSFORMER | 33.0667 | -117.057 | 2020 | Other All
OMD0000760328-01 | Emer-Specl Req - Fire/Police/Gov | 2020-09-12 07:37 | 2020-09-12 07:32 | 2020-09-12 07:34 | Y | N | Y | N | N | Actual Ignition | 12 kV |  | Vegetation Contact |  | Device Damaged | 470-724 | Transformer | 50 | p614833 | 470 |  | 56561 McKeown, John | NE O&E SUP |  | 33.1036 | -117.0067 | 2020 | Non Conductor
OMD0000773375-01 | Transformer Outage | 2020-10-30 08:19 | 2020-10-30 04:46 | 2020-10-30 05:34 | N | N | N | Y | N | Actual Ignition |  | 240 V | Electric Facility | meter caught fire inside meter room and burned panel and other meters | Customer Problem | 523-231 | Transformer | 80 | meter panel | 523 |  | 01324 Serrano, Daniel | NE O&E SUP | FIRE INSIDE CUSTOMER'S METER ROOM. | 33.3819 | -117.2488 | 2020 | Non Conductor
OMD0000775493-01 | Emer-Specl Req - Fire/Police/Gov | 2020-11-06 21:57 | 2020-11-06 20:32 | 2020-11-06 21:13 | Y | Y | N | N | N | Actual Ignition | 12 kV |  | Electric Facility | CUT OUTS ON POLE CUT ON FIRE | Weather Damaged Device | 733-159 | Transformer | 50 | P75813 | 733 | rREPLACE CUT OUTS | 02479 Fergerson, Mike | NE O&E SUP |  | 32.7617 | -117.0159 | 2020 | Non Conductor
OMD0000775518-01 | Emer-Specl Req - Fire/Police/Gov | 2020-11-07 00:30 | 2020-11-06 22:41 | 2020-11-06 23:56 | Y | Y | N | N | N | Actual Ignition | 12 kV |  | Electric Facility | X-ARM ON FIRE | Weather Damaged Device | 162-134 | Transformer | 25 | P169016 | 162 | CHANGE X-ARM | 02479 Fergerson, Mike | NE O&E SUP |  | 32.7345 | -117.0144 | 2020 | Non Conductor
OMD0000775610-01 | Dmg/Wlite-Flash or Sparks | 2020-11-07 10:49 | 2020-11-07 09:17 | 2020-11-07 10:02 | N | N | N | N | Y | Arching/Charring |  | 240 V | Other/Undetermined | service sparking all between P114127 AND P714534. | Weather Damaged Service | 231-172 | Transformer | 100 | P114127 | 231 | REPLACE OH SERVICE BETWEEN P114127 AND P714354 | 01324 Serrano, Daniel | NE O&E SUP | SERVICE IS BAD BETWEEN P114127 AND | 33.3285 | -117.2445 | 2020 | Conductor
OMD0000775804-01 | Emer-Specl Req - Fire/Police/Gov | 2020-11-08 01:22 | 2020-11-07 21:01 | 2020-11-08 01:20 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Fire Damaged Pole | 170-303 | Transformer | 250 | p573777 | 170 |  | 56561 McKeown, John | NE O&E SUP |  | 33.33 | -116.3852 | 2020 | Non Conductor
OMD0000779487-01 | Circuit Outage | 2020-11-20 22:51 | 2020-11-20 19:28 | 2020-11-20 20:04 | Y | Y | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | WIRE DOWN BURNED BUTT OF POLE, P11205 | Conductor Damaged | ESCO-12KV-519 | Circuit |  | P11205 | 519 | WIRE DOWN, DAMAGED POLE P11205 | 21460 Davis, John | NE O&E SUP |  | 33.1279 | -117.0813 | 2020 | Conductor
OMD0000780870-01 | Branch Outage | 2020-11-30 10:26 | 2020-11-30 09:14 | 2020-11-30 09:31 | N | N | Y | N | N | Actual Ignition | 12 kV |  | Vegetation Contact | damage lightning arrestor | Device Damaged | 233-123R | Recloser |  | P161627 | 233 |  | 56561 McKeown, John | NE O&E SUP |  | 33.2677 | -117.237 | 2020 | Non Conductor
OMD0000780870-02 | Branch Outage | 2020-11-30 10:24 | 2020-11-30 09:15 | 2020-11-30 09:41 | Y | N | N | Y | N | Actual Ignition | 12 kV |  | Electric Facility |  | Device Damaged | 233-123R | Recloser |  | P161627 | 233 | NEED CREW TO REPLACE BLOWN ARRESTOR ON P161627 | 01553 Amavisca, Luis | NE O&E SUP | CREW TO REPLACE BLOWN ARRESTOR -- P | 33.2677 | -117.237 | 2020 | Non Conductor
OMD0000794792-01 | Dmg Dim/Nolite-WireDown Pole to | 2021-01-23 03:01 | 2021-01-23 02:07 | 2021-01-23 02:41 | Y | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility |  | Service Down | 452-353 | Transformer | 25 | P511682 | 452 | SERVICE DOWN | 56561 McKeown, John | NE O&E SUP |  | 33.147 | -117.0497 | 2021 | Conductor
OMD0000797451-01 | Dmg Dim/Nolite-Pole Burning | 2021-01-27 13:46 | 2021-01-27 12:27 | 2021-01-27 12:50 | Y | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility | WIRE OVERLOAD | Service Down | 907-1577 | Transformer | 75 | P116716 | 907 | SERVICE DOWN OVERLOAD | 56561 McKeown, John | NE O&E SUP |  | 33.2165 | -117.0335 | 2021 | Conductor
OMD0000800089-01 | Emer-Specl Req - Fire/Police/Gov | 2021-02-05 02:01 | 2021-02-05 00:13 | 2021-02-05 00:49 | N | N | N | N | Y | Arching/Charring |  | 120 V | Other/Undetermined | HOUSE FIRE NOT SDG&E PROBLEM | Off at Main Breaker | 520-145 | Transformer | 25 |  | 520 |  | 56561 McKeown, John | NE O&E SUP | OFF AT MAIN BREAKER | 33.4246 | -117.2212 | 2021 | Other All
OMD0001033236-01 | Branch Outage | 2023-08-26 10:04 | 2023-08-26 03:42 | 2023-08-26 04:32 | N | Y | N | N | N | Arching/Charring | 12 kV |  | Contact by Object |  | Motor Vehicle Contact with Xfmr | F86987 | Fuse | 150A | D2019674338 & D2019574338 | 165 |  | 00832 Arevalo, Greg | NC O&E SUP | Car Vs two transformers 165-262 & 1 | 32.7205 | -117.085 | 2023 | UG Vehicle
OMD0000825986-01 | Dmg/Wlite-Pole Burning | 2021-05-24 18:42 | 2021-05-24 17:27 | 2021-05-24 18:39 | Y | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility |  | Connector Damaged | 907-1412 | Transformer | 50 | BATHROOM | 907 |  | 56561 McKeown, John | NE O&E SUP | REPLACED SEC CONNECTIONS AT WEATHER | 33.2058 | -116.9998 | 2021 | Non Conductor
OMD0000832062-01 | Emer-Specl Req - Fire/Police/Govt | 2021-06-18 11:35 | 2021-06-18 10:23 | 2021-06-18 11:20 | Y | N | N | N | N | Actual Ignition | 12 kV |  | Electric Facility |  | Device Damaged | 456-112 | Transformer | 25 | Z314050 | 456 |  | 53699 Marshall, Jim | NE O&E SUP | CAPACITOR FAILURE. | 33.1457 | -117.0473 | 2021 | Non Conductor
OMD0000835648-02 | Branch Outage | 2021-07-01 10:08 | 2021-07-01 08:08 | 2021-07-01 10:05 | N | N | Y | N | N | Actual Ignition | 12 kV |  | Vegetation Contact |  | Wire Down | 1023-35 | Switch Position |  | P119249 | 1023 |  | 56561 McKeown, John | NE O&E SUP |  | 33.2551 | -117.1544 | 2021 | Veg
OMD0000838199-01 | Dmg/Wlite-Other | 2021-07-12 18:13 | 2021-07-12 18:12 | 2021-07-12 18:13 | N | N | N | N | N |  | 12 kV |  | Vegetation Contact |  | Customer Problem | 350-810 | Transformer | 150 |  | 350 |  | 56561 McKeown, John | NE O&E SUP |  | 33.3132 | -117.0925 | 2021 | Veg
OMD0000842172-03 | Circuit Outage | 2021-07-26 09:45 | 2021-07-26 06:28 | 2021-07-26 08:37 | Y | N | N | N | N |  | 12 kV |  | Electric Facility |  | Transformer Problem | AV-12KV-522 | Circuit |  | P411299 | 522 | DAMAGED 25HJ TRANSFORTMER | 56561 McKeown, John | NE O&E SUP |  |  |  | 2021 | Non Conductor
OMD0000854589-01 | Emer-Specl Req - Fire/Police/Govt | 2021-09-14 07:06 | 2021-09-14 05:49 | 2021-09-14 06:21 | Y | Y | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | NO FIRE DAMAGE FOUND TO ANYTHING BUT THE CAPACITOR | Device Damaged | 234-925 | Transformer | 25 | Z11975 | 234 |  | 21460 Davis, John | NE O&E SUP | CAP STA 234-695 FAULTED CAUSING OUT | 33.3525 | -117.2311 | 2021 | Non Conductor
OMD0000859787-01 | Emer-Specl Req - Fire/Police/Govt | 2021-10-05 02:31 | 2021-10-05 01:23 | 2021-10-05 01:45 | Y | Y | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | FIRE DAMAGE PRESENT AT SWITCH ONLY, NO OTHER FIRE DAMAGE HERE | Device Damaged | 1250-225 | Transformer | 50 | Z510509 | 1250 | SWI 182-T1-1250 CAUGHT ON FIRE AND NEEDED TO BE ISOLATED FOR | 21460 Davis, John | NE O&E SUP | SWI 182-T1-1250 CAUGHT FIRE AND HAD | 33.0948 | -117.1184 | 2021 | Non Conductor
OMD0000862947-02 | Circuit Outage | 2021-10-18 09:47 | 2021-10-18 09:28 | 2021-10-18 09:32 | Y | N | N | N | N |  | 12 kV |  | Electric Facility |  | Device Damaged | ESCO-12KV-515 | Circuit |  | cir515 | 515 |  | 56561 McKeown, John | NE O&E SUP |  |  |  | 2021 | Undetermined
OMD0000867254-01 | Circuit Outage | 2021-11-05 02:53 | 2021-11-04 23:58 | 2021-11-05 00:11 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | CAP STA 788-72 FAULTED, EVIDENCE OF ARC AT POLE TOP. NO FIRE DAMAGE ON GROUND | Device Deenergized for Safety | FE-12KV-788 | Circuit |  | P314935 | 788 | ISOLATE DAMAGED CUT OUTS @ 788-72CF, P314935 | 21460 Davis, John | NE O&E SUP | CAP STA 788-72CF FAILED CAUSING OUT | 33.1029 | -117.0363 | 2021 | Non Conductor
OMD0000882799-01 | Branch Outage | 2022-01-09 06:36 | 2022-01-09 06:36 | 2022-01-09 06:36 | Y | Y | N | N | N | Arching/Charring | 12 kV | 480 V | Electric Facility | Possible Tracking at XFMR Bracket | Fire Damaged Pole | 170-410R | Recloser |  | P571959 | 170 | Pole C/O | 06594 Schelhorn, Brian | NE O&E SUP | Pole Boke Possibly Due to Tracki | 33.3021 | -116.3671 | 2022 | Non Conductor
OMD0000890768-01 | Emer-Specl Req - Fire/Police/Govt | 2022-02-16 01:15 | 2022-02-15 22:09 | 2022-02-15 23:28 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Conductor Damaged | 170-240 | Transformer | 15 | P670188 | 170 | RETIE IN PHASE | 53699 Marshall, Jim | NE O&E SUP | CONDUCTOR ON CROSSARM. BURNT POLE & | 33.2797 | -116.3909 | 2022 | Non Conductor
OMD0000906225-01 | Emer-Specl Req - Fire/Police/Govt | 2022-04-26 16:06 | 2022-04-26 15:15 | 2022-04-26 15:30 | Y | N | N | N | N |  |  | 120 V | Electric Facility |  | Service Deenergized For Safety | 412-626 | Transformer | 15 | P371663 | 412 |  | 02479 Fergerson, Mike | NE O&E SUP | REMOVED SERVICE FOR SAFETY CUSTOMER | 32.7791 | -116.9256 | 2022 | Undetermined
OMD0000908930-01 | Emer-Specl Req - Fire/Police/Govt | 2022-05-10 10:20 | 2022-05-10 09:14 | 2022-05-10 09:14 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Device Damaged | 247-430 | Transformer | 25 | P106173 | 247 | CAP BANK FIRE | 02479 Fergerson, Mike | NE O&E SUP |  | 32.8482 | -116.886 | 2022 | Non Conductor
OMD0000910294-01 | Emer-Specl Req - Fire/Police/Govt | 2022-05-15 00:17 | 2022-05-14 23:17 | 2022-05-14 23:43 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Transformer Problem | 545-57 | Switch |  | P2234269200 | 545 | DAMAGED TRANSFORMER 545-57 | 02479 Fergerson, Mike | NE O&E SUP |  | 32.7767 | -117.2528 | 2022 | Non Conductor
OMD0000910316-01 | Emer-Specl Req - Fire/Police/Govt | 2022-05-15 02:09 | 2022-05-15 01:29 | 2022-05-15 01:44 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Device Damaged | 545-359 | Transformer | 50 | P732797 | 545 | STAND OFF PIN CAUGHT ON FIRE | 02479 Fergerson, Mike | NE O&E SUP |  | 32.7817 | -117.2531 | 2022 | Non Conductor
OMD0000912524-01 | Dmg Dim/Nolite-Tree Burn in Wire | 2022-05-24 05:32 | 2022-05-24 03:55 | 2022-05-24 04:57 | N | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility | SERVICE WIRE RUBBING ON TREE BRANCH | Service Deenergized For Safety | 733-439 | Transformer | 50 | P77794 | 733 | replace service | 02479 Fergerson, Mike | NE O&E SUP |  | 32.7466 | -117.0036 | 2022 | Veg
OMD0000913891-01 | Transformer Outage | 2022-05-29 | 2022-05-28 20:58 | 2022-05-28 21:59 | N | N | N | N | N |  |  | 240 V | Other/Undetermined | Secondary service was on the ground. Very high winds at structure. structure had tin metal roof that looks like it may have blown off roofing and hit/damaged OH service | Weather Damaged Service | 221-276 | Transformer | 10 |  | 221 |  | 11083 Martinez, Danny Joshua | NE O&E SUP | Structure fire, secondary service w | 33.0823 | -116.4406 | 2022 | Conductor
OMD0000915414-01 | Emer-Specl Req - Fire/Police/Govt | 2022-06-06 04:44 | 2022-06-05 22:40 | 2022-06-05 22:48 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | FAULTED UG CABLE CAUSED ARCING AT TOP OF CONDUIT ON CABLE POLE, P18200 | Damaged Underground Cable | 188-784 | Transformer | 25 | P18200 | 188 | REPLACE FAULTED UG CABLE | 21460 Davis, John | NE O&E SUP |  | 33.144 | -117.1107 | 2022 | OH to UG
OMD0000924671-01 | Branch Outage | 2022-07-11 17:47 | 2022-07-11 14:24 | 2022-07-11 17:19 | Y | N | Y | Y | N |  | 12 kV |  | Contact by Object | Mylar Balloons between phases caught fire and dropped to ground starting fire | Foreign Object Contact Conductor | F659051 | Fuse | 80A | Z710962 | 231 |  | 01324 Serrano, Daniel | NE O&E SUP | Mylar balloons got between phases a | 33.3147 | -117.2392 | 2022 | Balloon
OMD0000941097-01 | Emer-Specl Req - Fire/Police/Govt | 2022-09-09 14:09 | 2022-09-09 12:00 | 2022-09-09 12:39 | N | N | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | POSSIBLE FROM LEAKY XFMR | Weather Damaged Transformer | 971-179 | Transformer | 25 |  | 971 | POLE TOP FIRE | 11083 Martinez, Danny Joshua | NE O&E SUP | LEAKY XFMR CAUGHT FIRE, BURNT POLE | 32.9947 | -116.9338 | 2022 | Non Conductor
OMD0000945284-01 | No Lights - Cause Unknown | 2022-09-25 00:33 | 2022-09-24 23:32 | 2022-09-24 23:53 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Contact by Object |  | Transformer Problem | 176-1014 | Transformer | 25 |  | 176 | DAMAGE TRANSFORMER | 56561 McKeown, John | NE O&E SUP |  | 32.9859 | -116.9958 | 2022 | Other Contact
OMD0000945755-01 | Dmg Dim/Nolite - Flash or Sparks | 2022-09-27 11:42 | 2022-09-27 09:52 | 2022-09-27 11:29 | N | N | N | N | Y | Arching/Charring | 12 kV |  | Electric Facility |  | Heat Device/Overload | 233-1237 | Transformer | 55 | P100572 | 233 | REPLACE OH STA 233-1237 ON P100572. CLIMBER | 01324 Serrano, Daniel | NE O&E SUP | TRANSFORMER LEAKING AND CUTOUT BURN | 33.3102 | -117.2322 | 2022 | Non Conductor
OMD0000956187-01 | No Lights - Cause Unknown | 2022-11-09 12:11 | 2022-11-09 11:23 | 2022-11-09 11:23 | Y | Y | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | MAYBE TRACKING | Fuse Operated in Transformer | 233-2030 | Transformer | 25 | P14309 | 233 | C/O CUTOUTS FOR STA 233-2030. | 01324 Serrano, Daniel | NE O&E SUP | CUTOUT BURNED OPEN, I SENT IN DAF F | 33.2682 | -117.238 | 2022 | Non Conductor
OMD0000967502-01 | Emer-Specl Req - Fire/Police/Govt | 2022-12-24 23:31 | 2022-12-24 21:23 | 2022-12-24 21:57 | N | N | N | N | Y |  | 12 kV |  | Other/Undetermined | Fire capt, said ignition was unknown. Incident #027826 | Customer Problem | 175-288 | Transformer | 75 |  | 175 |  | 11083 Martinez, Danny Joshua | NE O&E SUP | PER FIRE CHIEF, BUD SILLONS, CAUSE | 33.0496 | -116.964 | 2022 | Other All
OMD0000972695-01 | Voltage Problem-Low/Just Start | 2023-01-14 16:15 | 2023-01-14 15:36 | 2023-01-14 16:08 | Y | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility | SSC SHORTED OUT DUE TO RAIN | Weather Damaged Service | 451-716 | Transformer | 50 | P419464 | 451 | CHANGE OUT DAMAGED OH SVC | 21460 Davis, John | NE O&E SUP | NEED SVC CREW TO REPLACE DAMAGED OH | 33.1347 | -117.0681 | 2023 | Conductor
OMD0000972715-01 | Dmg Dim/Nolite - Wire Hanging Low | 2023-01-14 17:23 | 2023-01-14 16:51 | 2023-01-14 17:09 | Y | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility | INSULATION FAILED ON SSC OH SVC, SHORTED OUT IN RAIN | Weather Damaged Service | 519-445 | Transformer | 50 | P419111 | 519 | REPLACE DAMAGED OH SVC | 21460 Davis, John | NE O&E SUP | OH SVC BURNT OPEN, CALLED FOR CREW | 33.1306 | -117.0706 | 2023 | Conductor
OMD0000973305-01 | Dmg/Wlite-Wire Down Pole to House | 2023-01-16 13:09 | 2023-01-16 12:48 | 2023-01-16 12:56 | Y | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility | INSULATION FAILED ON OH SVC, STORM | Weather Damaged Service | 376-73 | Transformer | 100 | P732902 | 376 | REPLACE DAMAGED OH SVC | 21460 Davis, John | NE O&E SUP | OH SVC DOWN, CALLED FOR CREW TO REP | 32.6877 | -117.1766 | 2023 | Conductor
OMD0000973343-01 | Dmg/Wlite-Flash or Sparks | 2023-01-16 13:38 | 2023-01-16 13:09 | 2023-01-16 13:15 | Y | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility | INSULATION ON OH SVC FAILED | Weather Damaged Service | 372-76 | Transformer | 50 | P830689 | 372 | CHANGE OUT DAMAGED OH SVC, DE-ENERGIZED FOR SAFETY | 21460 Davis, John | NE O&E SUP | OH SVC BURNT OPEN, NEED CREW TO REP | 32.6999 | -117.1821 | 2023 | Conductor
OMD0000974091-01 | Emer-Specl Req - Fire/Police/Govt | 2023-01-18 04:36 | 2023-01-18 02:54 | 2023-01-18 03:25 | Y | N | N | N | N |  | 12 kV |  | Electric Facility |  | Customer Problem | 973-338 | Transformer | 50 | SH573388 | 973 | ETS CUT SECONDARY SERVICE OPEN AT SH573388, FOR SAFTEY.CUSTO | 11083 Martinez, Danny Joshua | NE O&E SUP | CUSTOMER HAD ELECTRIC BREAKERS AT P | 32.9939 | -116.8077 | 2023 | Other All
OMD0000975476-01 | Emer-Specl Req - Fire/Police/Govt | 2023-01-22 05:02 | 2023-01-22 02:26 | 2023-01-22 02:41 | N | N | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | WIRE DOWN | Wire Down | 470-1826 | Three Phase Transformer | 500 |  | 470 | WIRE DOWN FROM P11606 TO P11610 | 01553 Amavisca, Luis | NE O&E SUP | CREW TO REPLACE DOWN PRIMARY WIRE F | 33.0915 | -117.0094 | 2023 | Conductor
OMD0001035863-01 | Circuit Outage | 2023-09-05 08:31 | 2023-09-05 08:31 | 2023-09-05 08:31 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | UG SWITCH FAULTED, DAMAGE AND ARCING AT SWITCH. | Device Damaged | RIN-12KV-216 | Circuit |  | D239363 | 216 | REPLACE FAULTED PME 9 SWITCH | 21460 Davis, John | NE O&E SUP | PME 9 SWITCH @ D269363 FAILED AND | 33.2739 | -116.9539 | 2023 | UG Switch
OMD0000979885-01 | Emer-Specl Req - Fire/Police/Govt | 2023-02-09 06:22 | 2023-02-09 05:28 | 2023-02-09 05:52 | N | N | N | N | Y |  | 12 kV |  | Other/Undetermined | FIRE RESTRICITED TO CONTENTS OF HOUSE, NO DAMAGE TO SDGE FACILITIES, SDGE NOT CAUSE OF FIRE | Customer Problem | 540-272 | Transformer | 25 |  | 540 |  | 21460 Davis, John | NE O&E SUP | BOOTED METER DUE TO STRUCTURE FIRE. | 32.9917 | -117.0927 | 2023 | Other All
OMD0000980175-01 | Branch Outage | 2023-02-10 05:47 | 2023-02-09 23:36 | 2023-02-09 23:58 | N | N | N | N | Y | Arching/Charring | 12 kV |  | Vegetation Contact | PINE TREE FELL AND TOOK DOWN PRIMARY WIRE. | Foreign Object Contact Conductor | F2418275 | Fuse | 15A | P18979 | 521 | PRIMARY WIRE DOWN P18979. | 01324 Serrano, Daniel | NE O&E SUP | TREE FELL AND TOOK DOWN PRIMARY BET | 33.3856 | -117.2101 | 2023 | Veg
OMD0000980721-01 | Emer-Specl Req - Fire/Police/Govt | 2023-02-13 02:57 | 2023-02-13 02:18 | 2023-02-13 02:29 | Y | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility | #6 COPPERWELD OH SERVICE BURNT DOWN, INSULATION FAILED AT WEATHERHEAD | Service Down | 453-796 | Transformer | 50 | P417094 | 453 | REPLACE OH SVC'S 709 & 719 CAMELLIA ST, ESC. | 21460 Davis, John | NE O&E SUP | OH SVC DOWN @ 709 CAMELLIA, CALLED | 33.1405 | -117.0582 | 2023 | Conductor
OMD0000985284-01 | Emer-Specl Req - Fire/Police/Govt | 2023-02-26 23:10 | 2023-02-26 21:47 | 2023-02-26 22:39 | N | N | N | N | Y | Arching/Charring |  | 120 V | Vegetation Contact |  | Service Vandalism | 519-358 | Three Phase Transformer | 75 |  | 519 |  | 56561 McKeown, John | NE O&E SUP |  | 33.1279 | -117.078 | 2023 | Other All
OMD0000985291-01 | Dmg/Wlite-Xfmr/Grn Box Flash/Sprk | 2023-02-27 00:33 | 2023-02-26 23:10 | 2023-02-26 23:41 | Y | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility |  | Connector Damaged | 921-128 | Transformer | 50 | 921-128 | 921 |  | 56561 McKeown, John | NE O&E SUP |  | 32.9457 | -117.061 | 2023 | Non Conductor
OMD0000994640-01 | Emer-Specl Req - Fire/Police/Govt | 2023-03-28 11:13 | 2023-03-28 11:03 | 2023-03-28 11:03 | Y | Y | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | HIGH SIDE BUSHINGS ON TRANSFORMER ARE BURNED | Transformer Problem | 520-738 | Transformer | 15 | P712105 | 520 | REPLACE OH STA 520-625 ON P712105 | 01324 Serrano, Daniel | NE O&E SUP | STA 520-625, TRANSFORMER IS BAD, I | 33.4207 | -117.3098 | 2023 | Non Conductor
OMD0001005510-01 | Branch Outage | 2023-05-10 09:56 | 2023-05-10 08:00 | 2023-05-10 08:07 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Conductor Damaged | F659450 | Fuse | 25A | P107494 | 249 | POTHEAD BURNED UP AT P107494 | 01324 Serrano, Daniel | NE O&E SUP | POTHEAD BURNED UP AT P107494. I SEN | 33.3798 | -117.0841 | 2023 | OH to UG
OMD0001009162-01 | Dmg/Wlite-Wire Hanging Low | 2023-05-24 15:19 | 2023-05-24 14:02 | 2023-05-24 14:12 | N | N | N | N | N | Arching/Charring |  | 120 V | Contact by Object |  | Service Down | 794-639 | Transformer | 25 | p120675 | 794 | 130 ft street light service down from p120675 to p222545 | 10589 Trujillo, Elijah | NE O&E SUP | street light service down from p120 | 33.4406 | -117.6443 | 2023 | Other All
OMD0001029218-01 | Branch Outage | 2023-08-15 12:32 | 2023-08-15 12:14 | 2023-08-15 12:14 | Y | N | N | Y | N |  | 12 kV |  | Contact by Object | UNKNOWN, MAYBE BIRD CONTACT | Undetermined | 239-2213R | Recloser |  | P713907 | 239 |  | 01324 Serrano, Daniel | NE O&E SUP | AT P816806 LOOKS LIKE SOMETHING GOT | 33.3471 | -117.1356 | 2023 | Other All
OMD0001056374-01 | Emer-Specl Req - Fire/Police/Govt | 2023-11-27 19:03 | 2023-11-27 16:33 | 2023-11-27 16:33 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | car contact to switch knocked switch off pad | Conductor Damaged | 782-494 | Three Phase Transformer | 150 | d238238 | 782 | car vs mvi swi 782-1036f and run of cable damaged | 70169 Ransom, Ryan | NC O&E SUP | car vs mvi swi 782-1037 and cable | 33.1239 | -117.3213 | 2023 | UG Vehicle
OMD0001051595-01 | Branch Outage | 2023-11-07 08:25 | 2023-11-07 07:45 | 2023-11-07 07:45 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Foreign Object Contact Conductor | F157280 | Fuse | 80A | P71947 | 415 |  | 02479 Fergerson, Mike | NE O&E SUP |  | 32.8132 | -116.9316 | 2023 | Other Contact
OMD0001054283-01 | Dmg/Wlite-Other | 2023-11-16 15:39 | 2023-11-16 14:31 | 2023-11-16 14:31 | N | Y | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Wire to Wire Contact | 330-100 | Transformer | 100 | p22491 | 330 | thw in under arm fiber caused flash over @p22491 | 10589 Trujillo, Elijah | NE O&E SUP | thw in under arm fiber @p22941 flas | 33.4278 | -117.6136 | 2023 | Non Conductor
OMD0001072389-01 | Circuit Outage | 2024-01-29 07:37 | 2024-01-29 06:41 | 2024-01-29 07:33 | N | Y | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Heat Device/Overload | AV-12KV-521 | Circuit |  | P318711 | 521 |  | 01324 Serrano, Daniel | NE O&E SUP | ASSISTED KYLE, KYLE SENT IN DAF FOR | 33.382 | -117.2347 | 2024 | Non Conductor
OMD0001072629-01 | Emer-Specl Req - Fire/Police/Govt | 2024-01-29 15:05 | 2024-01-29 13:07 | 2024-01-29 13:19 | Y | N | N | Y | N |  | 12 kV |  | Contact by Object | goose | Foreign Object Contact Conductor | 233-2107 | Transformer | 150 | P12611 | 233 |  | 01324 Serrano, Daniel | NE O&E SUP | GOOSE GOT BETWEEN WIRE AT P12611 AN |  |  | 2024 | Animal
OMD0001073483-01 | Emer-Specl Req - Fire/Police/Govt | 2024-02-01 12:37 | 2024-02-01 11:48 | 2024-02-01 11:48 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | WIRE DOWN ON ASPHALT DRIVEWAY. MELTED DRIVEWAY | Weather Damaged Pole | 234-768 | Transformer | 50 | P319424 | 234 | REPLACE P319424. | 01324 Serrano, Daniel | NE O&E SUP | P319424 FELL OVER AND WIRE BURNED D | 33.3379 | -117.2304 | 2024 | Non Conductor
OMD0001074665-01 | Emer-Specl Req - Fire/Police/Govt | 2024-02-05 20:27 | 2024-02-05 19:58 | 2024-02-05 20:11 | Y | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Conductor Damaged | 454-256 | Transformer | 37.5 | P417225 | 454 | REPLACE DAMAGED OH SVC | 21460 Davis, John | NE O&E SUP | OH SVC DOWN, INSULATION FAILED. NEE | 33.1467 | -117.0614 | 2024 | Conductor
OMD0001112291-01 | Branch Outage | 2024-07-04 18:20 | 2024-07-04 18:15 | 2024-07-04 18:15 | N | N | N | Y | N |  | 12 kV |  | Vegetation Contact | HIT AND RUN | Wire Down | 183-440 | Switch |  |  | 183 |  | 56561 McKeown, John | NE O&E SUP |  | 33.1571 | -117.1294 | 2024 | Vehicle
OMD0001120556-02 | Branch Outage | 2024-08-06 11:06 | 2024-08-06 09:18 | 2024-08-06 09:51 | N | N | N | N | N | Arching/Charring | 12 kV |  | Contact by Object |  | Foreign Object Contact Conductor | 908-1370R | Recloser |  | P213337 | 908 | BIRD CONTACT DAMAGE | 53699 Marshall, Jim | NE O&E SUP | CREW TO REPLACE DAMAGED WIRE, LIGHT | 33.287 | -117.0236 | 2024 | Animal
OMD0001122969-02 | Branch Outage | 2024-08-15 05:08 | 2024-08-15 00:39 | 2024-08-15 01:07 | N | N | N | N | N | Arching/Charring | 12 kV |  | Vegetation Contact |  | Wire Down | <inline_jumper.24847> |  |  |  | 233 | WIRE DOWN @ P108332 TO P510868 | 01553 Amavisca, Luis | NE O&E SUP | CREW TO MAKE REPAIRS TO DOWN WIRE - |  |  | 2024 | Veg
OMD0001122971-01 | Emer-Specl Req - Fire/Police/Govt | 2024-08-15 05:44 | 2024-08-15 05:39 | 2024-08-15 05:39 | N | N | N | Y | N |  | 12 kV |  | Electric Facility |  | Weather Damaged Conductor | 233-1765 | Transformer | 25 | P108332 | 233 |  | 01324 Serrano, Daniel | NE O&E SUP | WIRE DOWN AT P108332. DAF WAS SENT | 33.2808 | -117.2449 | 2024 | Conductor
OMD0001128945-03 | Circuit Outage | 2024-09-05 18:04 | 2024-09-05 16:25 | 2024-09-05 16:37 | N | N | N | N | N |  | 12 kV |  | Other/Undetermined | HOT OIL IGNITED BARK AT BUTT OF POLE | Heat Transformer Overload | FE-12KV-470 | Circuit |  | P510628 | 470 | TRANSFORMER FAILURE | 53699 Marshall, Jim | NE O&E SUP | CREW TO REPLACE 470-355. | 33.0962 | -117.0606 | 2024 | Non Conductor
OMD0001129051-03 | Branch Outage | 2024-09-05 21:54 | 2024-09-05 18:14 | 2024-09-05 19:17 | Y | N | N | N | N |  | 12 kV |  | Electric Facility |  | Heat Device/Overload | 182-2240F | Switch Position |  | P203597 | 182 | wire down | 06594 Schelhorn, Brian | NE O&E SUP | Wire Down | 33.1102 | -117.1199 | 2024 | Non Conductor
OMD0001070570-01 | Branch Outage | 2024-01-23 13:14 | 2024-01-23 09:50 | 2024-01-23 10:06 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Weather Damaged Device | F359009 | Fuse | 150A | D155624 | 123 | Need crew to replace 3 phase fuse cabinet that was damaged i | 02766 Mcghen, Ryan | CM O&E SUP | Need crew to replace 3 phase fuse c | 32.7045 | -117.1525 | 2024 | UG Fuse
OMD0001142519-01 | Flickering Lights-Just Started | 2024-10-21 13:49 | 2024-10-21 12:47 | 2024-10-21 13:19 | Y | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility |  | Connector Damaged | 351-243 | Transformer | 25 | P617312 | 351 |  | 56561 McKeown, John | NE O&E SUP | REPLACED SEC CONNECTIONS ON STA POL | 33.2275 | -117.0726 | 2024 | Non Conductor
OMD0001144206-01 | Dmg/Wlite-Xfmr/Grn Box Flash/Sprk | 2024-10-29 09:56 | 2024-10-29 08:14 | 2024-10-29 08:33 | Y | Y | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | BAD CABLE IN CONDUIT AT P117304. MELTING AND CATCHING FIRE. | Weather Damaged Conductor | 522-88 | Transformer | 50 | P117304 | 522 | REPLACE BAD CABLE FROM P117304 TO STA 522-108. | 01324 Serrano, Daniel | NE O&E SUP | BAD CABLE FROM P117304 TO STA 522-1 | 33.3693 | -117.2464 | 2024 | Non Conductor
OMD0001150530-01 | Branch Outage | 2024-11-22 09:09 | 2024-11-22 07:28 | 2024-11-22 09:06 | N | N | Y | N | N |  | 12 kV |  | Vegetation Contact |  | Wire Down | F588695 | Fuse | 150A |  | 233 |  | 56561 McKeown, John | NE O&E SUP |  | 33.2938 | -117.2091 | 2024 | Veg
OMD0001152827-01 | Branch Outage | 2024-12-04 07:37 | 2024-12-04 05:17 | 2024-12-04 06:16 | N | N | N | Y | N |  | 12 kV |  | Electric Facility |  | Connector Damaged | F2468614 | Fuse | 30A | P815971 | 185 | wire down | 02479 Fergerson, Mike | NE O&E SUP |  | 33.1152 | -117.1519 | 2024 | Non Conductor
OMD0001152827-02 | Branch Outage | 2024-12-04 08:48 | 2024-12-04 05:17 | 2024-12-04 05:33 | N | N | N | N | N |  | 12 kV |  | Vegetation Contact |  | Connector Damaged | F2468614 | Fuse | 30A |  | 185 |  | 01553 Amavisca, Luis | NE O&E SUP | CREW TO REPLACE DAMAGE CONDUCTOR B | 33.1152 | -117.1519 | 2024 | Veg
OMD0001156263-01 | No Lights - Cause Unknown | 2024-12-16 02:35 | 2024-12-16 01:22 | 2024-12-16 01:59 | Y | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility | CUSTOMER PANEL | Customer Problem | 500-298 | Transformer | 25 | ------------------------------- | 500 |  | 56561 McKeown, John | NE O&E SUP | BAD CAR CHARGER BREAKER NO PA | 32.9654 | -117.1171 | 2024 | Non Conductor
OMD0001159100-01 | Dmg/Wlite-Flash or Sparks | 2024-12-30 08:12 | 2024-12-30 07:19 | 2024-12-30 07:37 | Y | Y | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | tracking | Wire Line Problem | 474-345 | Transformer | 75 | P417992 | 474 | Damaged Crossarm | B4629 Liversage Kyle JAMES | NE O&E SUP | Dmg/Wlite- 2602 GROTON PL- Tracking | 33.0874 | -117.0439 | 2024 | Non Conductor
ADV1000000000008872 | Dmg Dim/Nolite-WireDown Pole to | 2020-11-02 16:00 | 2020-11-02 14:43 | 2020-11-02 14:43 | Y | N | N | N | N | Arching/Charring |  | 240 V | Contact by Object | moving truck damaged OH service causing service down with arcing & sparking | Motor Vehicle Contact Services | 1081-267 | Transformer | 50 | P22594 | 1081 | OH service brought down by moving truck, damaging meter pane | 23170 Doshier, Richard | OC O&E SUP | P22594, moving truck brought down O | 33.018 | -117.2775 | 2020 | Vehicle
OMD0000646182-02 | Circuit Outage | 2019-07-23 09:09 | 2019-07-23 06:54 | 2019-07-23 07:14 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | WEDGE TAP STRUPP | Weather Damaged Connector | LNL-12KV-794 | Circuit |  | P120666 | 794 | STRUPP AT P120666 BURNT 1/0 CU WIRE DOWN BETWEEN P120665 -P1 | 03231 O'Mara, Simon | OC O&E SUP | WEDGE TAP STRUPP AT P120666 BURNT 1 | 33.4438 | -117.6493 | 2019 | Non Conductor
OMD0000647762-01 | Branch Outage | 2019-07-28 09:10 | 2019-07-28 04:01 | 2019-07-28 05:19 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | UNDERGROUND CABLE EXPOLDED IN HANDHOLE | Damaged Underground Cable | 410-50R | Recloser |  | H123360 | 410 |  | 02479 Fergerson, Mike | OC O&E SUP | ASSISTED CHRIS M. | 32.7785 | -116.9278 | 2019 | UG UG Cable
OMD0001074100-01 | Flickering Lights-Just Started | 2024-02-03 14:19 | 2024-02-03 11:27 | 2024-02-03 12:35 | N | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility |  | Connector Damaged | 567-87 | Transformer | 50 | D5300057415 | 567 | FOUND BAD 350 SEC CONNECTIONS IN STA 567-87...WILL NEED CREW | 00462 Macias, Damian | OC O&E SUP | FOUND BAD 350 SEC CONNECTIONS IN ST | 33.5991 | -117.6494 | 2024 | UG Connector
OMD0000650649-01 | Emer-Specl Req - Fire/Police/Gov | 2019-08-08 08:18 | 2019-08-08 04:58 | 2019-08-08 06:09 | N | N | N | Y | N | Actual Ignition |  | 208 V | Other/Undetermined | structure fire, sdge equipment not involved | Customer Problem | 66-269 | Three Phase Transformer | 150 | 66-269 | 66 |  | 23170 Doshier, Richard | OC O&E SUP | structure fire, de-energized electr | 32.9817 | -117.2494 | 2019 | Other All
OMD0000651707-01 | Emer-Specl Req - Fire/Police/Gov | 2019-08-12 17:12 | 2019-08-12 15:56 | 2019-08-12 16:29 | N | N | N | N | N | Arching/Charring |  | 120 V | Other/Undetermined | cust wire past cust breakers shorted out in panel, not sdge equipment | Customer Problem | 205-827 | Transformer | 25 |  | 205 |  | 23170 Doshier, Richard | OC O&E SUP | short in panel past cust breakers, | 33.1994 | -117.2241 | 2019 | Other All
OMD0000654629-01 | Dmg/Wlite-Flash or Sparks | 2019-08-23 11:17 | 2019-08-23 09:42 | 2019-08-23 10:27 | N | N | N | N | N | Arching/Charring |  | 240 V | Other/Undetermined | arcing/melting on cust side @ main breaker in meter panel | Customer Problem | 901-1173 | Transformer | 25 |  | 901 | damaged/burnt main breaker & bus, electrician will f/u with | 23170 Doshier, Richard | OC O&E SUP | damaged/burnt main breaker & bus, e | 33.2442 | -117.2835 | 2019 | Other All
OMD0001091017-01 | Branch Outage | 2024-04-06 22:20 | 2024-04-06 18:12 | 2024-04-06 18:20 | N | N | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | #4 copper burned in half | Weather Damaged Conductor | 380-841F | Switch |  | d2300075131 | 380 | #4 copper failed from sta to sta | 00108 Alvarez, Marco | CM O&E SUP | CREW TO C/O 50 NEP TO 75KVA NTS AND | 32.7934 | -117.0582 | 2024 | UG Connector
OMD0001107688-01 | Dmg Dim/Nolite-Xfmr/Grn Bx Oil lk | 2024-06-15 21:05 | 2024-06-15 18:08 | 2024-06-15 18:58 | N | N | N | N | N | Arching/Charring |  | 208 V | Electric Facility | SECONDARY BUSHING ON UNDERGROUND PAD MOUNT XMFR HEATING UP & SMOLDERING | Device Damaged | 61-231 | Three Phase Transformer | 500 | D113524 | 61 |  | 30566 Garegnani, Dominic | NC O&E SUP | #2 B PHASE SECONDARY BUSHING IS HOT | 32.9607 | -117.2656 | 2024 | UG transformer
OMD0000667453-01 | Transformer Outage | 2019-10-11 13:09 | 2019-10-11 10:38 | 2019-10-11 10:55 | N | N | N | N | Y | Arching/Charring | 12 kV |  | Electric Facility | Burned open jumper | Connector Damaged | 288-459 | Transformer | 25 | Z24533 | 288 | Burned oipen over the arm jumper, bad al. stirrups | 03417 Clark, Brian J | OC O&E SUP | Crew repairs needed to repair burne | 33.0386 | -117.2717 | 2019 | Non Conductor
OMD0000681284-01 | Emer-Specl Req - Fire/Police/Gov | 2019-11-28 16:15 | 2019-11-28 15:30 | 2019-11-28 15:30 | N | N | N | N | N | Arching/Charring | 12 kV |  | Vegetation Contact | Tree fell on conductors. @P210671. No damage to sdge facilities | Tree Damaged Conductor | 63-358 | Transformer | 25 | P210671 | 63 | Large eucalyptus tree down, contacting P210671 | 03417 Clark, Brian J | OC O&E SUP | Fallen eucalyptus trimmed @P210671. | 33.0021 | -117.2314 | 2019 | Veg
OMD0000692492-01 | Dmg/Wlite-Other | 2020-01-08 12:18 | 2020-01-08 12:04 | 2020-01-08 12:04 | N | N | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | POSSIBLY ARCING FROM BEING CLOSE TO COAST... | Device Damaged | 204-125 | Transformer | 501 | STA 204-125 | 204 | BURNT UP CUT-OUT BODY... | 00462 Macias, Damian | OC O&E SUP | CUT-OUT BODY TO STA 204-125 HAS BUR | 33.4009 | -117.5795 | 2020 | Non Conductor
OMD0000713561-01 | No Lights in Part-Just Started | 2020-04-03 12:26 | 2020-04-03 09:49 | 2020-04-03 10:04 | N | N | N | N | N | Arching/Charring |  | 120 V | Other/Undetermined | Elec. meter damaged due to burned up meter clip. Unable to determine the cause, Meter clip jumpered out. Cust. to make repairs. | Connector Damaged | EN1-138 | Transformer | 75 |  | EN1 |  | 03417 Clark, Brian J | OC O&E SUP | Here are the pics of a test block j | 33.0443 | -117.2941 | 2020 | Non Conductor
OMD0000723429-03 | Branch Outage | 2020-05-11 14:37 | 2020-05-11 12:30 | 2020-05-11 12:47 | N | N | N | N | Y | Arching/Charring | 12 kV |  | Contact by Object | MYLAR BALLONS | Foreign Object Contact Conductor | 311-14R | Recloser |  |  | 311 |  | 03231 O'Mara, Simon | OC O&E SUP | IMYLAR BALLOONS HIT O/H WIRES AROUN | 33.4987 | -117.7266 | 2020 | Balloon
OMD0000725372-01 | Dmg Dim/Nolite - Other | 2020-05-20 12:19 | 2020-05-20 10:21 | 2020-05-20 10:51 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | HOT HIGH SIDE BANK BUSHING LOOSE CONNECTION | Weather Damaged Device | 1243-126 | Transformer | 150 | P39059 | 1243 | INSPECT STA HIGH SIDE BUSHINGS ONE BUSHING GETTING HOT MIGHT | 03231 O'Mara, Simon | OC O&E SUP | 1x15 AMP FUSE BLEW AT STA 1243-126 | 33.5184 | -117.569 | 2020 | Non Conductor
OMD0000730728-01 | Dmg/Wlite-Flash or Sparks | 2020-06-08 21:49 | 2020-06-08 21:03 | 2020-06-08 21:23 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Device Damaged | 330-393 | Transformer | 25 | P205393 | 330 | ARCING CUT-OUT BODY... | 00462 Macias, Damian | OC O&E SUP | CUT OUT BODY ON P205393 IS ARCING B | 33.423 | -117.6193 | 2020 | Non Conductor
OMD0000731467-01 | Transformer Outage | 2020-06-10 20:21 | 2020-06-10 19:00 | 2020-06-10 19:36 | N | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility |  | Connector Damaged | 1070-87 | Transformer | 75 | SH733293 | 1070 |  | 00462 Macias, Damian | OC O&E SUP | FOUND A BAD MOLD IN SH733293...SINC | 33.4971 | -117.6949 | 2020 | UG transformer
OMD0000745931-01 | Emer-Specl Req - Fire/Police/Gov | 2020-08-02 03:56 | 2020-08-02 02:01 | 2020-08-02 02:47 | Y | Y | N | N | N | Actual Ignition | 12 kV | 120 V | Electric Facility |  | Device Deenergized for Safety | 781-594 | Three Phase Transformer | 75 | P26065 | 781 | BURNT UP STAND-OFF PIN AND ALSO SECONDARY CONNECTION... | 00462 Macias, Damian | OC O&E SUP | @P26065 STA 781-787..HIGH SIDE STAN | 33.163 | -117.3561 | 2020 | Non Conductor
OMD0000751510-01 | Emer-Specl Req - Fire/Police/Gov | 2020-08-18 19:38 | 2020-08-18 18:09 | 2020-08-18 18:09 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Heat Device/Overload | 799-403 | Transformer | 225 | P21492 | 799 | BURNT OPEN HOOKSTICKS @ SWI 799-2 P21492... | 00462 Macias, Damian | OC O&E SUP | WHEN LOAD WAS SWAPPED TO 799 A HOOK | 33.5235 | -117.6678 | 2020 | Non Conductor
OMD0000758853-01 | Dmg/Wlite-Tree on Wires | 2020-09-07 11:16 | 2020-09-07 09:41 | 2020-09-07 10:03 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Vegetation Contact | trimmed palm frond making contact with 12kv conductor, sent f/u to veg mgt | Palm Frond On Conductor | 512-184 | Transformer | 25 | P221161 | 512 | FYI, i trimmed (2) palm fronds that were burning off of 12k | 23170 Doshier, Richard | OC O&E SUP | trimmed palm frond off of 12kv cond | 32.9956 | -117.2739 | 2020 | Veg
OMD0000773919-02 | Emer-Specl Req - Fire/Police/Gov | 2020-11-01 16:45 | 2020-11-01 10:56 | 2020-11-01 11:22 | Y | N | N | Y | N | Arching/Charring | 12 kV |  | Vegetation Contact | palm frond making contact with 12kv conductor between P14678 & P14679 | Palm Frond On Conductor | 68-401 | Transformer | 50 | P14678 | 68 |  | 23170 Doshier, Richard | OC O&E SUP | tree trimmers onsite to trim palm f |  |  | 2020 | Other Contact
OMD0000775298-01 | Branch Outage | 2020-11-06 14:38 | 2020-11-06 11:38 | 2020-11-06 11:57 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Device Damaged | F615107 | Fuse | 150A | P128848 | 203 | DAMAGED CUT-OUT BODY AND DOOR...WILL NEED TO BE REPLACED... | 00462 Macias, Damian | OC O&E SUP | BURNT CUT-OUT BODY AND DOOR AT P128 | 33.3969 | -117.5946 | 2020 | Non Conductor
OMD0000782220-01 | Dmg/Wlite-Flash or Sparks | 2020-12-03 14:51 | 2020-12-03 14:50 | 2020-12-03 14:50 | N | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility | bare service connection made contact with dusk to dawn light on the mast @ Z90297, made temp rerpair & issued f/u to dist | Incomplete | 510-65 | Transformer | 75 | Z90297 | 510 |  | 23170 Doshier, Richard | OC O&E SUP | Z90297, someone made temp repair to | 32.9695 | -117.2618 | 2020 | Non Conductor
OMD0001109246-01 | Branch Outage | 2024-06-23 12:55 | 2024-06-23 05:59 | 2024-06-23 06:43 | N | N | N | N | N | Arching/Charring | 12 kV |  | Contact by Object |  | Equipment Contacted Device | F129226 | Fuse | 80A | d2289074951 | 380 | car contact witn 1 phase term | 00108 Alvarez, Marco | CM O&E SUP |  | 32.7929 | -117.0658 | 2024 | UG Vehicle
OMD0000806451-01 | Transformer Outage | 2021-02-28 16:57 | 2021-02-28 14:34 | 2021-02-28 14:59 | N | N | N | Y | N | Actual Ignition | 12 kV |  | Vegetation Contact | COULD NOT FIND BIRD SO MUST BE ONLY THE STICKS IT WAS USING TO BUILD NEST... | Foreign Object Contacted Device | 204-365 | Transformer | 225 | P227391... | 204 | BURNT UP TRANSFORMER ON STA 204-365... | 00462 Macias, Damian | OC O&E SUP | SO IT SEEMS THAT SOME BIRD WAS TRYI | 33.4355 | -117.5691 | 2021 | Animal
OMD0000853071-02 | Circuit Outage | 2021-09-08 12:44 | 2021-09-08 12:16 | 2021-09-08 12:16 | N | N | N | N | N | Arching/Charring | 12 kV |  | Contact by Object | MYLAR BALLOON... | Equipment Contacted Device | CP-12KV-799 | Circuit |  | P127401 | 799 | FLASHED OVER CUT-OUT BODY BY MYLAR BALLOON... | 00462 Macias, Damian | OC O&E SUP | DID FIND A FLASHED OVER CUT-OUT BOD | 33.5255 | -117.6718 | 2021 | Balloon
OMD0000876032-01 | Emer-Specl Req - Fire/Police/Govt | 2021-12-14 13:40 | 2021-12-14 12:13 | 2021-12-14 12:40 | Y | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility |  | Weather Damaged Service | 311-202 | Transformer | 50 | BETWEEN P26006 & P28372... | 311 | DOWN SEV SERVICE DROP...PLEASE PICK UP BURNT SERVICE DEBRI.. | 00462 Macias, Damian | OC O&E SUP | WHEN ARRIVED SERVICE HAD BLOWN ITSE | 33.5051 | -117.7421 | 2021 | Conductor
OMD0000877184-01 | Emer-Specl Req - Fire/Police/Govt | 2021-12-15 13:04 | 2021-12-15 13:04 | 2021-12-15 13:04 | N | N | N | N | N | Arching/Charring |  | 120 V | Contact by Object | 33062 NIGUEL RD HM...IS ACTUAL ADDRESS TO PEDISTAL | Device Deenergized for Safety | 1072-111 | Three Phase Transformer | 150 |  | 1072 |  | 00462 Macias, Damian | OC O&E SUP | PEDISTAL STARTED ARCING DUE TO LID | 33.483 | -117.7139 | 2021 | Non Conductor
OMD0000878588-03 | Circuit Outage | 2021-12-20 13:08 | 2021-12-20 12:41 | 2021-12-20 12:41 | N | N | N | N | N | Arching/Charring | 12 kV |  | Contact by Object | Heavy Equip. contact caused molten copper to hit the ground | Equipment Contacted Conductor | SM-12KV-299 | Circuit |  | P112648 | 299 | Heavy equipment contacted OH conductors | 03417 Clark, Brian J | OC O&E SUP | Crew repairs needed to replace dama | 33.1581 | -117.2216 | 2021 | Other Contact
OMD0000907883-01 | Dmg/Wlite-Other | 2022-05-04 21:20 | 2022-05-04 19:25 | 2022-05-04 19:25 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | PG CLAMP... | Connector Damaged | 310-72 | Transformer | 75 | P25939J | 310 | BAD PG CLAMPS... | 00462 Macias, Damian | OC O&E SUP | FOUND BAD PG CLAMP ON P25939J...WIL | 33.465 | -117.704 | 2022 | Non Conductor
OMD0000928315-01 |  | 2022-07-27 13:04 | 2022-07-27 07:53 | 2022-07-27 07:53 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Vegetation Contact | 12kv wire down pole to pole | Weather Damaged Connector | <inline_jumper.19513> |  |  | P121902 | 794 | 1 wire 1 span of 12kv down | 23170 Doshier, Richard | OC O&E SUP | 1 wire 1 span of 12kv down between | 33.448 | -117.6544 | 2022 | Veg
OMD0000930892-01 | Transformer Outage | 2022-08-06 19:14 | 2022-08-06 17:20 | 2022-08-06 17:50 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | BAD PARALLEL GROOVE CLAMP... | Connector Damaged | 310-73 | Transformer | 150 | P23236 | 310 | BURNT OPEN STIRUP... | 00462 Macias, Damian | OC O&E SUP | LOOKS LIKE A PARALLEL GROOVE CLAMP | 33.465 | -117.7031 | 2022 | Non Conductor
OMD0000938326-01 | No Lights - Cause Unknown | 2022-09-03 21:27 | 2022-09-03 19:59 | 2022-09-03 20:29 | N | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility |  | Connector Damaged | SC2-90 | Transformer | 55 | P122264J | SC2 | BAD SEC SERVICE... | 00462 Macias, Damian | OC O&E SUP | FOUND BAD SEC CONNECTION TO SERVICE | 33.4266 | -117.6149 | 2022 | Non Conductor
OMD0000954269-01 | Dmg/Wlite-Flash or Sparks | 2022-11-02 17:24 | 2022-11-02 15:29 | 2022-11-02 15:29 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | switch 195-42, one of the disconnects is arcing & sparking, de-energized for safety, crew enroute to make repairs | Device Deenergized for Safety | 195-203 | Three Phase Transformer | 75 | P258837 | 195 | P258837, switch 195-42, single side disconnect arcing & spar | 23170 Doshier, Richard | OC O&E SUP | switch 195-42 failed, crew enroute | 33.4958 | -117.6745 | 2022 | Non Conductor
OMD0000969631-01 | No Lights - Cause Unknown | 2023-01-04 14:38 | 2023-01-04 14:34 | 2023-01-04 14:34 | N | N | N | N | Y | Arching/Charring |  | 240 V | Electric Facility | per cust meter failed after solar co. reinstalled meter, flashed at meter socket? | Customer Problem | 995-417 | Transformer | 75 | cust 400amp meter panel | 995 |  | 23170 Doshier, Richard | OC O&E SUP | old electric meter failed after sol | 33.438 | -117.6352 | 2023 | Non Conductor
OMD0000998217-02 | Branch Outage | 2023-04-10 18:45 | 2023-04-10 15:15 | 2023-04-10 16:16 | Y | N | N | Y | N | Arching/Charring | 12 kV |  | Electric Facility | A large tree fell and caused OH wires to come down. | Tree Damaged Conductor | 66-1213R | Recloser |  | P311774 | 66 | wire down | 03417 Clark, Brian J | OC O&E SUP | Crew repairs needed to replaced Dag | 32.9842 | -117.2264 | 2023 | Veg
ADV1000000000802334 | Dmg/Wlite-Other | 2024-07-24 23:31 | 2024-07-24 22:08 | 2024-07-24 22:23 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Transformer Problem | 322-219 | Transformer | 25 | D1995775904 | 322 |  | 00832 Arevalo, Greg | NC O&E SUP | Primary bushing @ station 322-219 d | 32.7121 | -117.0333 | 2024 | UG transformer
OMD0001055793-02 | Transformer Outage | 2023-11-24 19:15 | 2023-11-24 18:00 | 2023-11-24 18:20 | N | N | N | N | N | Arching/Charring |  | 120 V | Other/Undetermined | OVERLOAD...LOOSE CONNECTION? | Damaged Underground Cable | 768-125 | Transformer | 100 | SH785501... | 768 | BAD SEC SERVICE WIRE AND MOLDS IN SH785501... | 00462 Macias, Damian | OC O&E SUP | FOUND BAD MOLDS AND BAD SEC WIRE IN | 33.5846 | -117.6836 | 2023 | UG Connector
OMD0001062179-01 | Flickering Lights-Just Started | 2023-12-20 11:16 | 2023-12-20 09:12 | 2023-12-20 10:17 | N | N | N | N | N | Arching/Charring |  | 120 V | Other/Undetermined | INSULINK CONNECTION... | Connector Damaged | 200-690 | Transformer | 50 |  | 200 | BAD SEC CONNECTIONS AT WEATHERHEAD... | 00462 Macias, Damian | OC O&E SUP | CUST HAS BAD NEUTRAL CONNECTION IN | 33.4271 | -117.6198 | 2023 | Non Conductor
OMD0001118964-01 | Emer-Specl Req - Fire/Police/Govt | 2024-07-31 01:26 | 2024-07-30 21:14 | 2024-07-30 23:10 | N | N | N | N | N |  |  | 208 V | Electric Facility | SUB PANEL CAUGHT FIRE IN ELECTRICAL ROOM. SDGE EQUIPMENT WAS NOT THE CAUSE. NO SDGE EQUIPMENT DAMAGED | Conductor Damaged | 209-102 | Three Phase Transformer | 500 | D3839570001 | 209 |  | 07093 Lasua, Keoni | NC O&E SUP | FIRE WAS IN ELECTRICAL ROOM AT A RE | 33.2182 | -117.2319 | 2024 | Other All
OMD0001074114-01 | No Lights in Part-Just Started | 2024-02-03 15:55 | 2024-02-03 14:20 | 2024-02-03 14:46 | N | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility | SEC MOLD | Connector Damaged | 989-225 | Transformer | 50 | SH779807 | 989 | BAD SEC MOLDS... | 00462 Macias, Damian | OC O&E SUP | FOUND BAD SEC MOLDS @SH779807...CRE | 33.5675 | -117.6651 | 2024 | UG Connector
OMD0001092968-01 | Dmg Dim/Nolite-Wire Down P to P | 2024-04-14 20:50 | 2024-04-14 19:51 | 2024-04-14 19:51 | N | N | N | N | N | Arching/Charring |  | 120 V | Other/Undetermined | OLD #6 STRANDED WIRE DAMAGES EASILY | Service Down | 330-224 | Transformer | 50 |  | 330 | SERVICE DOWN FROM P23069 TO WEATHER HEAD | D4086 Fannan, Jason | OC O&E SUP | SECONDARY/SERVICE WIRE DOWN FROM P2 | 33.4222 | -117.6173 | 2024 | Conductor
OMD0001103341-01 | Branch Outage | 2024-05-29 11:03 | 2024-05-29 08:47 | 2024-05-29 09:52 | Y | N | Y | N | N | Arching/Charring | 12 kV |  | Electric Facility | Tree trimmers bucket truck contacted 12Kv. lines causing the wire to burn down on top of 9401 LM and damaging the Lemmon Ave. | Equipment Contacted Conductor | 86-552F | Switch Position |  | P173719 | 86 | Tree trimmers caused wires down | 03417 Clark, Brian J | OC O&E SUP | Crew repairs needed to replace dama | 32.7702 | -117.0078 | 2024 | Other Contact
OMD0001115189-01 | Transformer Outage | 2024-07-17 10:27 | 2024-07-17 07:49 | 2024-07-17 08:23 | N | N | N | N | N | Arching/Charring |  | 120 V | Other/Undetermined | NOTHING AROUND WIRE... | Weather Damaged Service | 794-631 | Transformer | 50 |  | 794 | FLASHED OVER AERIAL CABLE FROM P124261 TO P120889... | 00462 Macias, Damian | OC O&E SUP | FLASHED OVER AERIAL CABLE FROM POLE | 33.4516 | -117.661 | 2024 | Undetermined
OMD0001116295-01 | Emer-Specl Req - Fire/Police/Govt | 2024-07-20 23:04 | 2024-07-20 21:11 | 2024-07-20 21:18 | N | N | N | N | Y | Arching/Charring | 12 kV | 240 V | Other/Undetermined | FIRE CAPTAIN SAID POSSIBLE DRUG HOUSE | Undetermined | 795-616 | Transformer | 50 |  | 795 |  | 92593 Keoveunxay, Phouthai | OC O&E SUP | STRUCTURE FIRE. FIRE CAPTAIN ASKED | 33.4597 | -117.671 | 2024 | Other All
OMD0001127882-03 | Circuit Outage | 2024-09-02 16:16 | 2024-09-02 11:28 | 2024-09-02 11:55 | N | Y | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | LBE WAS BURNING FROM SOMEHWERE,,, | Device Damaged | TB-12KV-556 | Circuit |  | D5251156370 | 556 |  | 00462 Macias, Damian | OC O&E SUP | LBE FAILED AND CAUSED OUTAGE TO CIR | 33.5996 | -117.6866 | 2024 | Other All
OMD0001128941-01 | Emer-Specl Req - Fire/Police/Govt | 2024-09-05 19:24 | 2024-09-05 16:01 | 2024-09-05 16:22 | Y | N | N | N | N |  | 12 kV | 208 V | Electric Facility |  | Service Down | 313-394 | Transformer | 150 | P21039 | 313 | Burnt open #2 Cu 4 wire 3 phase service | D4086 Fannan, Jason | OC O&E SUP | Burnt open 3phase service to El Ado | 33.5 | -117.6632 | 2024 | Conductor
OMD0001137472-02 | Branch Outage | 2024-10-01 16:52 | 2024-10-01 14:25 | 2024-10-01 14:44 | N | N | N | N | Y | Arching/Charring | 12 kV |  | Electric Facility |  | Weather Damaged Conductor | F691140 | Fuse | 100A | P26367 | 792 | 1 WIRE 1 SPAN PRIMARY WIRE DOWN FROM P26367 TO P121860 100FT | 03231 O'Mara, Simon | OC O&E SUP | ONE SPAN ONE WIRE DOWN BETWEEN POLE | 33.4685 | -117.7007 | 2024 | Conductor
OMD0001137504-01 | Emer-Specl Req - Fire/Police/Govt | 2024-10-01 18:07 | 2024-10-01 17:06 | 2024-10-01 17:16 | N | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility |  | Service Down | 795-545 | Transformer | 25 | P24683 | 795 | STREET LIGHT WIRE CAME DOWN BETWEEN POLE P24683 & P26256...W | 00462 Macias, Damian | OC O&E SUP | STREET LIGHT WIRE CAME DOWN BETWEEN | 33.4654 | -117.6746 | 2024 | Other All
OMD0001137905-01 | Dmg/Wlite-Flash or Sparks | 2024-10-02 19:52 | 2024-10-02 18:44 | 2024-10-02 19:07 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Transformer Problem | 795-597 | Transformer | 25 | STA 795-597... | 795 | CHANGE OUT OH TRANSFORMER...25KVA HE... | 00462 Macias, Damian | OC O&E SUP | TRANSFORMER ON P24818 IS TRACKING.. | 33.4637 | -117.6687 | 2024 | Non Conductor
OMD0001160218-01 | Emer-Specl Req - Fire/Police/Govt | 2025-01-04 12:25 | 2025-01-04 10:43 | 2025-01-04 11:09 | N | N | N | N | Y |  | 12 kV |  | Other/Undetermined | FIRE DEPARTMENT SAID POSSIBLE PROPANE | Undetermined | 557-855 | Transformer | 150 |  | 557 |  | 92593 Keoveunxay, Phouthai | OC O&E SUP | HOME EXPLOSION. METER HAS BEEN BOOT | 33.5774 | -117.7044 | 2025 | Other All
OMD0001166793-01 | Dmg Dim/Nolite-WireDown Pole to H | 2025-01-26 02:36 | 2025-01-26 00:25 | 2025-01-26 01:20 | N | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility |  | Service Down | 522-151 | Transformer | 50 | P318820J | 522 | REPLACE OH SEC 3-WIRE SERVICE... | 00462 Macias, Damian | OC O&E SUP | LOOKS LIKE #6 STRANDED SEC SERVICE | 33.3756 | -117.2349 | 2025 | Conductor
OMD0001166821-01 | Dmg/Wlite-Wire Hanging Low | 2025-01-26 04:58 | 2025-01-26 02:37 | 2025-01-26 03:36 | N | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility |  | Service Down | 507-677 | Transformer | 10 | P410400... | 507 | DOWN SEC 3-WIRE SERVICE...FROM P410400 TO WEATHERHEAD... | 00462 Macias, Damian | OC O&E SUP | SEC #6 STRANDED SERVICE WIRE CAME D | 33.1988 | -117.244 | 2025 | Conductor
OMD0001167108-01 | Dmg Dim/Nolite - Explosion | 2025-01-26 21:06 | 2025-01-26 19:17 | 2025-01-26 19:27 | N | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility |  | Service Deenergized For Safety | 1073-170 | Transformer | 50 | P220000J | 1073 | REPLACE OH 3-WIRE SSCU SERVICES...TO 33171 BIG SUR ST CUT IN | 00462 Macias, Damian | OC O&E SUP | SERVICE TO 33175 BIG SUR ST BURNT O | 33.4808 | -117.689 | 2025 | Conductor
OMD0001167109-01 | Dmg/Wlite-Flash or Sparks | 2025-01-26 21:07 | 2025-01-26 21:06 | 2025-01-26 21:06 | N | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility |  | Service Deenergized For Safety | 1073-170 | Transformer | 50 | P220000J | 1073 |  | 00462 Macias, Damian | OC O&E SUP | SERVICE TO 33175 BIG SUR ST BURNT O | 33.4808 | -117.689 | 2025 | Conductor
OMD0001167147-01 | Dmg/Wlite-Flash or Sparks | 2025-01-26 23:06 | 2025-01-26 21:08 | 2025-01-26 21:16 | N | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility |  | Service Down | 1073-168 | Transformer | 25 | P220018J | 1073 | BURNT OPEN SEC WIRE...FROM P220018J TO HOME... | 00462 Macias, Damian | OC O&E SUP | SEC SERV BURNT OPEN...SEC WIRE CAME | 33.478 | -117.6865 | 2025 | Conductor
OMD0001167353-01 | Dmg Dim/Nolite - Flash or Sparks | 2025-01-27 12:05 | 2025-01-27 11:13 | 2025-01-27 11:26 | N | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility |  | Open Neutral | 792-149 | Transformer | 25 | P123348... | 792 | REPLACE OH 3-WIRE SERVICE...OPEN NEUTRAL AND PHASE... | 00462 Macias, Damian | OC O&E SUP | WHEN ARRIVED CUSTOMER STATED HALF O | 33.4603 | -117.6556 | 2025 | Non Conductor
OMD0001167436-01 | Dmg Dim/Nolite - Explosion | 2025-01-27 13:25 | 2025-01-27 12:05 | 2025-01-27 12:24 | N | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility |  | Open Neutral | 310-505 | Transformer | 75 | HOME WEATHERHEAD... | 310 | OPEN NUETRAL AND PHASE TO SERVICE...NEED NEW ONE... | 00462 Macias, Damian | OC O&E SUP | FOUND AN OPEN NEUTRAL AND OPEN PHAS | 33.4721 | -117.6942 | 2025 | Non Conductor
PSTK1BPBG1D | Transmission Switching | 2019-10-04 07:21 | 2019-10-03 23:04 | 2019-10-03 23:46 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | BAD CONNECTION ON P254024... |  | JA | Switch |  | P254024 | JA | ARCING AND SPARKING CONNECTION ON P254024... | 00462 Macias, Damian | OC O&E SUP | BAD CONNECTIONS ON POLE P254024...A | 33.3737 | -117.5557 | 2019 | Non Conductor
OMD0000645799-01 | No Lights in Part-Just Started | 2019-07-22 00:44 | 2019-07-21 23:23 | 2019-07-22 00:41 | N | N | N | N | N | Arching/Charring |  | 120 V | Other/Undetermined | black marks in customer's panel | Customer Problem | 39-83 | Transformer | 300 |  | 39 |  | 03033 Laws, Jeffery | RA O&E SUP | good voltage @ customer's panel. | 32.7718 | -117.1529 | 2019 | Other All
OMD0000647740-03 | Branch Outage | 2019-07-27 23:36 | 2019-07-27 23:33 | 2019-07-27 23:33 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | Rack and elbow burned/ charred | Device Damaged | F283964 | Fuse | 100A | H2693374024 | 434 |  | 03033 Laws, Jeffery | RA O&E SUP |  | 32.9038 | -117.0991 | 2019 | UG Connector
OMD0000648868-01 | Emer-Specl Req - Fire/Police/Gov | 2019-08-01 06:26 | 2019-08-01 01:00 | 2019-08-01 01:16 | N | N | N | N | N | Arching/Charring | 12 kV |  | Contact by Object | Construction worker cut in to conduit | Equipment Contact UG Cable | 38-54 | Three Phase Transformer | 300 |  | 38 | Contractor cut in to energized cable between M2207171918 & H | 03033 Laws, Jeffery | RA O&E SUP |  | 32.7666 | -117.1675 | 2019 | UG Other COntact
OMD0001139203-03 | Branch Outage | 2024-10-08 10:17 | 2024-10-08 08:20 | 2024-10-08 08:37 | Y | Y | Y | Y | N |  | 12 kV |  | Contact by Object | CAR HIT UG STA 789-620, OIL IGNITED AS A RESULT | Motor Vehicle Contact with Xfmr | 789-16F | Switch Position |  | D127029 | 789 | CAR HIT UG STA 789-620 | 21460 Davis, John | NE O&E SUP | NEED CREW TO REPAIR DAMAGED TRANSFO | 33.0731 | -117.0777 | 2024 | UG Vehicle
OMD0001145322-01 | Emer-Specl Req - Fire/Police/Govt | 2024-11-01 14:26 | 2024-11-01 12:26 | 2024-11-01 13:40 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | FAULTED CAP BANK. | Device Deenergized for Safety | 306-963 | Transformer | 50 | D143626 | 306 | FAULTED UG CAP BANK | 07093 Lasua, Keoni | NC O&E SUP | CAP BANK 306-962CW FAULTED AND WAS | 33.0054 | -117.1989 | 2024 | UG Connector
OMD0000663801-01 | Branch Outage | 2019-09-27 04:56 | 2019-09-27 03:43 | 2019-09-27 03:43 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | Smoke coming out of top of conduit, steel conduit at ground level hot | Conductor Damaged | F102895 | Fuse | 125A | P95824J | 278 | Bad UG cable between P95824J & live front terminator D239257 | 03033 Laws, Jeffery | RA O&E SUP |  | 32.821 | -117.1716 | 2019 | OH to UG
OMD0000664419-04 | Circuit Outage | 2019-09-30 07:38 | 2019-09-30 04:53 | 2019-09-30 04:53 | Y | Y | Y | Y | N | Actual Ignition | 12 kV |  | Electric Facility | Xfmr pole fell over, pole and xfmr ignited, spreading to nearby brush. Total area burned approx. 100 sq ft. | Weather Damaged Pole | BR-12KV-171 | Circuit |  | P277947 | 171 | Anchor for P277947 rusted out, pole fell over & started fire | 03033 Laws, Jeffery | RA O&E SUP |  | 33.2616 | -116.3706 | 2019 | Non Conductor
OMD0000686972-01 | Dmg Dim/Nolite - Other | 2019-12-16 17:04 | 2019-12-16 16:46 | 2019-12-16 16:46 | Y | N | N | N | N | Arching/Charring |  | 120 V | Other/Undetermined | SERVICE NEUTRAL BURNED OPEN, | Open Neutral | 142-268 | Transformer | 50 | P579129J | 142 | SERVICE NEUTRAL BURNED OPEN | 23123 Domnitz, Jared | RA O&E SUP | SERVICE FAILED , SNYDER ELECTRIC MA | 32.7823 | -117.1614 | 2019 | Non Conductor
OMD0000688722-01 | Dmg/Wlite-Xfmr/Grn Box Flash/Spr | 2019-12-23 09:33 | 2019-12-23 08:14 | 2019-12-23 08:21 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Damaged Underground Cable | 972-284 | Switch |  | p119957 | 972 | faulted underground cable | 04142 Pearce, Jacob | RA O&E SUP | faulted underground cable at p11995 | 33.0333 | -116.8836 | 2019 | OH to UG
OMD0000701532-01 | Dmg Dim/Nolite-WireDown Pole to | 2020-02-13 14:25 | 2020-02-13 13:23 | 2020-02-13 14:01 | N | N | N | N | Y | Actual Ignition |  | 120 V | Other/Undetermined | house burnt down rolled up de-energized service from driveway | Customer Problem | 212-180 | Transformer | 40 |  | 212 |  | 04142 Pearce, Jacob | RA O&E SUP | rolled up service wire out of drive | 33.4114 | -116.8208 | 2020 | Other All
OMD0000703600-02 | Branch Outage | 2020-02-22 11:37 | 2020-02-22 09:49 | 2020-02-22 10:17 | N | N | N | N | Y | Arching/Charring | 12 kV |  | Other/Undetermined | lightning | Weather Damaged Conductor | F102950 | Fuse | 150A | P834241J | 279 | LIGHTNING DAMAGED WIRE. WIRE DOWN, MULTIPLE LOCATIONS | 23123 Domnitz, Jared | RA O&E SUP | STORM, LIGHTNING BURNED DOWN MULTIP | 32.8352 | -117.2042 | 2020 | Non Conductor
OMD0000714777-01 | Branch Outage | 2020-04-08 14:48 | 2020-04-08 12:14 | 2020-04-08 12:14 | N | N | N | N | N | Arching/Charring |  | 208 V | Other/Undetermined | VEHICLE HIT TRANSFORMER AND CUT SECONDARY WIRE CAUSING ARC FLASH ON CASE. | Motor Vehicle Contact with Xfmr | LBE.151275 |  |  |  | 950 | TRANSFORMER HIT BY CAR | 23123 Domnitz, Jared | RA O&E SUP | CART VS TRANSFORMER |  |  | 2020 | Vehicle
OMD0000719303-01 | Dmg/Wlite-Flash or Sparks | 2020-04-25 15:24 | 2020-04-25 12:43 | 2020-04-25 14:23 | N | N | N | N | N | Arching/Charring |  | 120 V | Electric Facility |  | Connector Damaged | 212-61 | Transformer | 25 | P233601 | 212 |  | 93065 Wheelock, Steve | RA O&E SUP |  | 33.3822 | -116.6839 | 2020 | Non Conductor
OMD0000720552-01 | Emer-Specl Req - Fire/Police/Gov | 2020-04-30 10:14 | 2020-04-30 08:49 | 2020-04-30 09:14 | N | N | N | N | N | Arching/Charring |  | 120 V | Contact by Object | Rats nest in cust. panel caused fire inside of box. | Customer Problem | 170-246 | Transformer | 150 |  | 170 |  | 93065 Wheelock, Steve | RA O&E SUP | Rats nest in cust. panel. Cust. r | 33.2931 | -116.3488 | 2020 | Non Conductor
OMD0000725962-01 | Dmg Dim/Nolite - Flash or Sparks | 2020-05-20 16:23 | 2020-05-20 15:17 | 2020-05-20 15:32 | Y | N | N | N | N | Arching/Charring |  | 240 V | Other/Undetermined | CUSTOMER OWNED METER PANEL, C/O BREAKER'S AND PANEL CAUGHT FIRE. | Customer Problem | 701-317 | Transformer | 25 |  | 701 |  | 23123 Domnitz, Jared | RA O&E SUP | CUSTOMER METER PANEL CAUGHT FIRE WH | 32.7986 | -117.1353 | 2020 | Other All
OMD0000726350-01 | Emer-Specl Req - Fire/Police/Gov | 2020-05-22 09:03 | 2020-05-22 07:02 | 2020-05-22 08:00 | N | Y | N | Y | N | Actual Ignition |  | 120 V | Other/Undetermined | Cust. refueling genarator. Cust was an off account. | Customer Problem | UNKNOWN | Switch |  |  | 0221 |  | 93065 Wheelock, Steve | RA O&E SUP | Cust. on genarator and burnt garage |  |  | 2020 | Other All
OMD0000729874-02 | Branch Outage | 2020-06-05 11:00 | 2020-06-05 05:48 | 2020-06-05 06:16 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Foreign Object Contacted Device | F284350 | Fuse | 150A | P196260 | 728 | DAMAGED GROUND CONCENTRIC ON POTHEAD. AND CUTOUT. | 23123 Domnitz, Jared | RA O&E SUP |  | 32.9213 | -117.0584 | 2020 | OH to UG
OMD0000752911-01 | Emer-Specl Req - Fire/Police/Gov | 2020-08-22 16:42 | 2020-08-22 15:50 | 2020-08-22 15:50 | Y | Y | Y | Y | N | Actual Ignition |  | 120 V | Vegetation Contact |  | Conductor Damaged | SL1-97 | Transformer | 50 | P31591 | SL1 | Burnt sec. neutral on 3/0 Areial cable | 93065 Wheelock, Steve | RA O&E SUP |  | 33.074 | -116.5765 | 2020 | Veg
OMD0000757259-01 | Emer-Specl Req - Fire/Police/Gov | 2020-09-05 20:41 | 2020-09-05 18:43 | 2020-09-05 19:07 | Y | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility | LOAD, MELTED SECONDARY CONNECTIONS | Connector Damaged | 948-182 | Transformer | 50 | P473708 | 948 | TRANSFORMER LEADS AND CONNECTIONS CAUGHT ON FIRE. | 23123 Domnitz, Jared | RA O&E SUP | OVERLOAD , SECONDARY CONNECTIONS ME | 32.8043 | -116.9995 | 2020 | Non Conductor
OMD0000760934-01 | Branch Outage | 2020-09-14 23:44 | 2020-09-14 22:14 | 2020-09-14 22:37 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Weather Damaged Device | F357684 | Fuse | 10A | p2035969704 | 481 |  | 23123 Domnitz, Jared | RA O&E SUP | FUSE DOOR BURNED OPEN. | 32.7213 | -117.2371 | 2020 | Non Conductor
OMD0000761747-01 | Branch Outage | 2020-09-17 16:45 | 2020-09-17 13:37 | 2020-09-17 13:53 | Y | Y | Y | Y | N | Arching/Charring | 12 kV |  | Contact by Object |  | Foreign Object Contact Conductor | 210-9R | Recloser |  | P215047 | 210 |  | 93065 Wheelock, Steve | RA O&E SUP | Repairs made. | 33.2787 | -116.6338 | 2020 | Other Contact
OMD0000796182-01 | Emer-Specl Req - Fire/Police/Gov | 2021-01-25 19:29 | 2021-01-25 18:20 | 2021-01-25 19:25 | N | N | N | N | Y | Arching/Charring | 12 kV |  | Other/Undetermined | WIRE CHARRED MID SPAN | Weather Damaged Conductor | 59-495 | Transformer | 50 |  | 59 |  | 23123 Domnitz, Jared | RA O&E SUP | WIRES SLAPPED TOGETHER IN THE WIND. | 32.8301 | -117.2511 | 2021 | Conductor
OMD0000812011-01 | Dmg Dim/Nolite - Other | 2021-03-22 16:00 | 2021-03-22 15:47 | 2021-03-22 15:47 | N | N | N | N | N | Arching/Charring | 12 kV | 120 V | Electric Facility | conductor on x-arm tracking to station ground | Foreign Object Contact Conductor | 171-135 | Transformer | 25 | P679094 | 171 | Conductor off the insulater laying on cross arm. | 93065 Wheelock, Steve | RA O&E SUP | Conductor on crossarm found on rout | 33.2374 | -116.3708 | 2021 | Conductor
OMD0000819665-01 | Circuit Outage | 2021-04-26 19:24 | 2021-04-26 14:31 | 2021-04-26 15:01 | Y | Y | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | POLE FIRE AT SWITCH | Fire Damaged Pole | CB-12KV-483 | Circuit |  | P245159 | 483 | POLE FIRE , TOP OF POLE BROKE OFF. | 23123 Domnitz, Jared | RA O&E SUP | POLE FIRE , AT SWITCH | 32.6974 | -117.2464 | 2021 | Non Conductor
OMD0000820601-01 | Non Outage Order | 2021-04-30 14:01 | 2021-04-30 13:55 | 2021-04-30 13:55 | N | N | N | N | N | Arching/Charring |  | 120 V | Other/Undetermined | wire broke at connection | Weather Damaged Service | 971-462 | Transformer | 25 |  | 971 | Broken service wire | 66254 Pearce, Troy | RA O&E SUP |  | 33.019 | -116.8675 | 2021 | Non Conductor
OMD0000824875-02 | Circuit Outage | 2021-05-19 11:45 | 2021-05-19 10:55 | 2021-05-19 11:05 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | WIRE SLAPPED TOGETHER. | Conductor Damaged | CM-12KV-275 | Circuit |  | Z92508 | 275 |  | 23123 Domnitz, Jared | RA O&E SUP | CONTRACTORS MOVING WIRE GOT WIRE TO | 32.8342 | -117.1841 | 2021 | Other Contact
OMD0000837069-01 | Branch Outage | 2021-07-07 22:30 | 2021-07-07 21:45 | 2021-07-07 21:45 | N | N | N | N | Y | Arching/Charring | 12 kV |  | Other/Undetermined | WIRE ON WIRE CHARRED. | Connector Damaged | F2029568 | Fuse | 100A | P932696 | 276 | WIRE DOWN 6/3 CU | 23123 Domnitz, Jared | RA O&E SUP | OLD HOT LINE CLAMP CAUSED THE WIRE | 32.8217 | -117.206 | 2021 | Other Contact
OMD0000868346-02 | Branch Outage | 2021-11-10 20:27 | 2021-11-10 18:30 | 2021-11-10 18:53 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Weather Damaged Device | F401807 | Fuse | 30A | P116269 | 288 | FAILED LIGHTNING ARRESTOR | 23123 Domnitz, Jared | RA O&E SUP | FAILED LIGHTNING ARRESTOR. | 33.0347 | -117.2395 | 2021 | Non Conductor
OMD0001154823-01 | Emer-Specl Req - Fire/Police/Govt | 2024-12-11 10:18 | 2024-12-11 07:12 | 2024-12-11 07:32 | Y | N | N | Y | N |  | 12 kV |  | Electric Facility | traveled about 6' | Damaged Underground Cable | 743-326 | Three Phase Transformer | 500 | d2602670488 | 743 | fire at live front term | 52851 Mackley, Scott | BC O&E SUP | live front term fire cir 744 -fd op | 32.8772 | -117.2112 | 2024 | UG UG Cable
OMD0000877043-02 | Branch Outage | 2021-12-15 09:25 | 2021-12-15 07:23 | 2021-12-15 09:16 | N | N | N | N | N | Arching/Charring | 4 kV |  | Contact by Object |  | Weather Damaged Conductor | F341 | Fuse | 40A |  | OK1 |  | 93065 Wheelock, Steve | RA O&E SUP | Crew to put wire back up | 33.0695 | -116.5865 | 2021 | Other Contact
OMD0000887010-01 | Dmg/Wlite-Other | 2022-01-28 02:00 | 2022-01-27 18:49 | 2022-01-27 19:08 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility | GLOWING CONNECTOR | Connector Damaged | 512-156 | Transformer | 50 | p221886 | 512 | DAMAGED MILLION LUG POT HEAD. GLOWING AT BOLT CONNECTION | 23123 Domnitz, Jared | RA O&E SUP | A PHASE GLOWING ON POTHEAD | 32.9802 | -117.2668 | 2022 | OH to UG
OMD0000887266-03 | Branch Outage | 2022-01-28 21:03 | 2022-01-28 18:25 | 2022-01-28 19:02 | N | N | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | jumper melted, 500 copper. | Connector Damaged | 303-16 | Switch |  | p20927 | 303 |  | 23123 Domnitz, Jared | RA O&E SUP | 500 copper jumper burned open at sw | 33.1416 | -117.3359 | 2022 | Non Conductor
OMD0000889063-01 | Voltage Problem-Low/Just Start | 2022-02-07 15:25 | 2022-02-07 12:58 | 2022-02-07 13:15 | N | N | N | N | Y | Arching/Charring |  | 240 V | Other/Undetermined | PARALELL GROVE CLAMP , FAILING CONNECTION. | Connector Damaged | 287-1072 | Transformer | 175 | P223560 | 287 | PARALLELL GROVE CLAMP FAILING 500 CU TO 3/0 AL. | 23123 Domnitz, Jared | RA O&E SUP | FAILING SECONDARY CONNECTION. | 33.0456 | -117.2776 | 2022 | Non Conductor
OMD0000898159-01 | No Lights - Cause Unknown | 2022-03-21 10:49 | 2022-03-21 09:25 | 2022-03-21 09:58 | N | N | N | N | N | Arching/Charring |  | 120 V | Other/Undetermined | Lightning struck meter | Customer Problem | 212-200 | Transformer | 25 |  | 212 |  | 93065 Wheelock, Steve | RA O&E SUP | Cust. panel damaged, electrican to |  |  | 2022 | Non Conductor
OMD0000899222-02 | Branch Outage | 2022-03-25 15:23 | 2022-03-25 13:24 | 2022-03-25 13:39 | N | N | N | N | Y | Arching/Charring | 12 kV |  | Electric Facility |  | Conductor Damaged | F402710 | Fuse | 150A | P611369 | 287 | TRUCK CONTACTED DOWN GUY | 23123 Domnitz, Jared | RA O&E SUP | TRUCK CONTACTED GUY WIRE, SLAPPED W | 33.0575 | -117.2352 | 2022 | Vehicle
OMD0000901509-01 | Dmg/Wlite-Wire Down Pole to Pole | 2022-04-06 12:07 | 2022-04-06 10:26 | 2022-04-06 11:12 | N | N | N | N | Y | Arching/Charring |  | 240 V | Other/Undetermined | ALUMINUM CONNECTOR ON COPPER WIRE | Connector Damaged | NVS1-154 | Transformer | 25 | P216526 - P214876 | NVS1 | WIRE DOWN, SECONDARY. | 23123 Domnitz, Jared | RA O&E SUP | WIRE BROKE MIDSPAN , ALUMINUM CONNE | 33.2211 | -117.2155 | 2022 | Conductor
OMD0000919232-02 | Branch Outage | 2022-06-21 12:50 | 2022-06-21 10:53 | 2022-06-21 12:39 | Y | Y | Y | Y | N |  | 12 kV |  | Contact by Object |  | Foreign Object Contacted Device | 220-298R | Recloser |  | P212277 | 220 |  | 93065 Wheelock, Steve | RA O&E SUP |  | 33.1787 | -116.699 | 2022 | Other Contact
OMD0000935718-04 | Branch Outage | 2022-08-26 16:43 | 2022-08-26 15:59 | 2022-08-26 15:59 | N | N | N | N | N | Arching/Charring | 12 kV |  | Other/Undetermined | Burned up jumper glass | Incomplete | 176-1836R | Recloser |  |  | 176 | Broken jumper glass. Pole is a climber | 66254 Pearce, Troy | RA O&E SUP | Burned up Jumper pin and glass | 32.9765 | -117.0276 | 2022 | Non Conductor
OMD0000939206-01 | Emer-Specl Req - Fire/Police/Govt | 2022-09-05 17:14 | 2022-09-05 17:14 | 2022-09-05 17:14 | Y | N | N | N | N | Arching/Charring |  | 240 V | Electric Facility | SECONDARY CONNECTOR MELTED. | Connector Damaged | 61-56 | Transformer | 150 | P62113J | 61 | MELTED SECONDARY CONNECTION | 23123 Domnitz, Jared | RA O&E SUP |  | 32.959 | -117.2658 | 2022 | Non Conductor
OMD0000953693-01 | Dmg/Wlite-Other | 2022-10-31 12:18 | 2022-10-31 11:26 | 2022-10-31 11:35 | N | N | N | N | N | Arching/Charring |  | 240 V | Other/Undetermined | Hot connection | Connector Damaged | 221-509 | Transformer | 25 |  | 221 |  | 93065 Wheelock, Steve | RA O&E SUP |  | 33.0681 | -116.5468 | 2022 | Non Conductor
OMD0000978507-01 | Dmg/Wlite-Flash or Sparks | 2023-02-02 13:18 | 2023-02-02 12:35 | 2023-02-02 12:35 | N | N | N | N | N | Arching/Charring |  | 480 V | Electric Facility |  | Connector Damaged | 170-292 | Transformer | 150 | P102406 | 170 | Burnt service wires and lead connectors at transformer | 93065 Wheelock, Steve | RA O&E SUP |  | 33.3064 | -116.3584 | 2023 | Non Conductor
OMD0000982920-01 | Transformer Outage | 2023-02-22 05:29 | 2023-02-22 02:27 | 2023-02-22 02:45 | Y | N | N | N | N | Arching/Charring | 12 kV |  | Vegetation Contact | PINE TREE BLEW OVER INTO POLE | Weather Damaged Pole | 191-148 | Transformer | 25 | P26202J | 191 | NEED A LINE TRUCK TO LIFT TRUNK OF PINE TREE OFF OF POLE P26 | 23123 Domnitz, Jared | RA O&E SUP | FOLLOW UP WITH LINE TRUCK TO REMOVE | 33.2051 | -117.348 | 2023 | Veg
OMD0001048507-01 | Dmg/Wlite-Other | 2023-10-24 13:34 | 2023-10-24 10:18 | 2023-10-24 10:36 | N | N | N | N | Y | Arching/Charring | 12 kV | 240 V | Other/Undetermined | tracking | Fire Damaged Pole | 289-888 | Transformer | 75 | P29462 | 289 | BURNED POLE AT SECONDARY, SECURE POLE WITH 2 - 10' CROSARMS | 23123 Domnitz, Jared | RA O&E SUP | BURNED POLE AT SECONDARY. | 33.0423 | -117.2963 | 2023 | Non Conductor
OMD0001116770-01 | Emer-Specl Req - Fire/Police/Govt | 2024-07-22 22:58 | 2024-07-22 21:37 | 2024-07-22 22:18 | Y | N | N | N | N | Arching/Charring | 4 kV |  | Other/Undetermined | FUSE DOOR, DETIORATED LOAD STARTED DOOR TO GLOW. | Heat Device/Overload | VS2-114 | Transformer | 50 | P15336 | VS2 |  | 23123 Domnitz, Jared | RA O&E SUP | FUSE DOOR FAILED . | 33.1909 | -117.2383 | 2024 | Non Conductor
OMD0001130366-01 | Emer-Specl Req - Fire/Police/Govt | 2024-09-08 20:20 | 2024-09-08 15:35 | 2024-09-08 15:54 | Y | N | N | N | N | Arching/Charring | 4 kV |  | Other/Undetermined | CEMENT STREET LIGHT POLE | Heat Device/Overload | 205-1599 | Three Phase Transformer | 150 |  | 205 |  | 23123 Domnitz, Jared | RA O&E SUP | ANNEALED 6/3 COPPER WIRE, F/U WITH | 33.2227 | -117.2235 | 2024 | Other All
OMD0001136996-01 | Transformer Outage | 2024-09-30 09:01 | 2024-09-30 08:46 | 2024-09-30 08:46 | N | N | N | N | N | Arching/Charring | 12 kV |  | Electric Facility |  | Vandalism | 289-164 | Transformer | 65 | P20795J | 289 | BURNED CROSSARM. DAMAGED NO OUATAGE. | 23123 Domnitz, Jared | RA O&E SUP | NO OUTAGE, BURNED CROSSARM, F/U TO | 33.0383 | -117.2943 | 2024 | Non Conductor
OMD0001144667-01 | Emer-Specl Req - Fire/Police/Govt | 2024-10-30 16:35 | 2024-10-30 12:17 | 2024-10-30 13:41 | N | N | N | N | N | Arching/Charring | 12 kV |  | Vegetation Contact |  | Conductor Damaged | 221-260 | Transformer | 25 | P412048 | 221 |  | 23123 Domnitz, Jared | RA O&E SUP | A TIE WIRE BROKE CAUSING A PHASE TO | 32.908 | -116.2432 | 2024 | Veg
PSTK5CLVIU8 | Transmission Switching | 2020-01-13 12:25 | 2020-01-13 09:24 | 2020-01-13 09:24 | N | N | N | N | N | Arching/Charring |  |  | Electric Facility | FUSE DISCONNECT JAW BURNED OPEN LINESIDE OF BANK 20. |  | DH | Switch |  | DUNHILL SUB | DH |  | 23123 Domnitz, Jared | RA O&E SUP | FUSE JAW BURNED OPEN CAUSING FUSE T |  |  | 2020 | Non Conductor
OMD0001054283-01 | Dmg/Wlite-Other | 2023-11-16 15:39 | 2023-11-16 14:31 | 2023-11-16 14:31 | N | Y | N | N | N | Arching/Charring |  | 240 V | Electric Facility |  | Wire to Wire Contact | 330-100 | Transformer | 100 | p22491 | 330 | thw in under arm fiber caused flash over @p22491 | 10589 Trujillo, Elijah | NC O&E SUP | thw in under arm fiber @p22941 flas | 33.4278 | -117.6136 | 2023 | Non Conductor

## CCC Efficacy
OH Distribution Ignition Drivers | Total Number of CPUC Reportable Ignitions and Evidence of Heat Events [2019 - 2024] | 2024/2025 SME Ignition Reduction (%) | Estimated Number of Ignitions Reduced
Animal Contact | 20 | 90% | 18
Balloon Contact | 27 | 90% | 24.3
Vehicle Contact | 20 | 80% | 16
Vegetation Contact | 72 | 90% | 64.8
Other Contact* | 47 | 50% | 23.5 | CC ME | 50.45%
Conductor | 123 | 90% | 110.7 | EFD ME | 16%
Equipment – Non-Conductor** | 412 | 39% | 160.68 | FCP ME | 8%
Other All*** | 151 | 10% | 15.1 | CCC ME | 1-((1-CC ME)*(1- EFD ME)*(1- FCP ME))
Undetermined**** | 10 | 70% | 7 |  | 61.71%
Overhead to Underground Connection | 20 | 75% | 15
Total | 902 | --- | 455.08
| CC Efficacy |  | 50.45%
* Other contacts include external contacts caused by SDG&E or non-SDG&E personnel, customers, and foreign objects (excluding animals, balloons, vegetation, and vehicles) in overhead electrical equipment.
** Equipment – Non-Conductor includes electrical equipment like lightning arrestors, fuses, and transformers.
*** Other All includes contamination, dig-ins, vandalism, and non-utility fires.
**** Undetermined includes outages/ignitions with no information in Primary or Secondary Cause.

## UG Efficacy
Overhead Distribution Ignition-Related Drivers | Overhead Distribution Ignition-Related Sub-Drivers | Total Number of CPUC Reportable Ignitions and Evidence of Heat Events [2019 - 2024] | 2024/2025 Subject Matter Expert Ignition-Related Reduction (%) | Estimated Number of Ignition-Related Events Reduced | Comments
Equipment | Conductor Failure | 123 | 100% | 123 | With the removal of overhead assets, it is assumed that there will be zero ignition incidents.
Equipment | Overhead Equipment (Non-Conductor) | 412 | 100% | 412 | With the removal of overhead assets, it is assumed that there will be zero ignition incidents.
External | Vehicle Contact (Pole) | 20 | 100% | 20 | With the removal of overhead assets, it is assumed that there will be zero ignition incidents.
Equipment | Overhead Equipment Failure Unknown | 10 | 100% | 10 | Ignitions with no information in Primary or Secondary Cause (unknown). With the removal of overhead assets, it is assumed that there will be zero ignition incidents.
Equipment | Overhead to Underground Connection | 20 | 100% | 20 | With the removal of overhead assets, it is assumed that there will be zero ignition incidents.
External | All Other Overhead | 151 | 99% | 149.49 | This category accounts for potential factors in the overhead system that could impact underground equipment (e.g., contamination and non-utility fires) and assumes that the enclosed nature of underground structures offers better protection and containment of potential ignitions, preventing them from spreading to surrounding areas.
External | Other Overhead Contact | 47 | 100% | 47 | With the removal of overhead assets, it is assumed that there will be zero ignition incidents. | SDG&E estimates the residual ignition risk associated with underground infrastructure at approximately 0.91%. This estimate is derived by comparing the relative frequency of ignition-related events per mile of overhead (OH) and underground (UG) infrastructure. Additionally, the calculation accounts for the increased cable length typically required when converting overhead assets to underground, estimated at approximately 20% more mileage. After incorporating the estimated residual risk, the adjusted Mitigation Effectiveness of SDG&E’s Strategic Undergrounding program is calculated at 98.52% (99.43% - 0.91%) . This value is based on ignition-related events recorded between 2019 and 2024, reflecting a comprehensive assessment of both the benefits of removing overhead infrastructure and the minimal ignition-related risk introduced by underground systems.
External | Vegetation Contact | 72 | 95% | 68.4 | The enclosed nature of underground structures is assumed to better contain an ignition, preventing spread to surrounding areas. The effectiveness rate accounts for potential vegetation contacts such as roots growing and encroaching on underground structures.
External | Balloon Contact | 27 | 100% | 27 | With the removal of overhead assets, it is assumed that there will be zero ignition incidents.
External | Animal Contact (OH) | 20 | 100% | 20 | With the removal of overhead assets, it is assumed that there will be zero ignition incidents.
|  | 902 | n/a | 896.89
|  |  |  | OH to UG Efficacy: | 99.43%
|  |  |  | Added Ignition Related Events | -0.91%
|  |  |  | SUG Mitigation Effectiveness | 98.52%