## Sheet1 (2) (hidden)
Source WMP | Regulator | Deliverable | Type | Deficiency | Page Reference (Deficiency) | Deficiency Title | Description | Utility MUST (Action Item) | Show Progress in (WMP) | External Link (Show Progress in ) | Juan - Page Reference for column K (Show Progress In) | Addressed In Document: | External Site (Addressed In Document) | Page Reference (Addressed in Document) | Met the Requirement (Y/N) | Comments | Source for Requirement Met | External Sites (Source for Requirement Met) | Track 2 Exhibit (Exisiting/New) - Will Fuller
WMP 2019 | CPUC | DECISION ON SDG&E's 2019 WMP PURSUANT TO SENATE BILL 901 | Order | 298908547.pdf | 29 |  | 1. In San Diego Gas & Electric Company’s next Wildfire Mitigation Plan, it shall include a summary of the results of the detailed inspections it conducts in the High Fire Threat District Tier 3 area of its service territory |  |  | TBD |  |  |  |  | TBD
WMP 2019 | CPUC | DECISION ON SDG&E's 2019 WMP PURSUANT TO SENATE BILL 901 | Order | 298908547.pdf | 29 |  | 2. San Diego Gas & Electric Company may proceed with its proposed Fire Risk Mitigation plan to replace wood poles with steel poles in this Wildfire Mitigation Plan cycle, but shall base its decisions for pole replacements on reasonable criteria and consider ingress and egress impacts as part of the decision |  |  | TBD |  |  |  |  | TBD
WMP 2019 | CPUC | DECISION ON SDG&E's 2019 WMP PURSUANT TO SENATE BILL 901 | Order | 298908547.pdf | 29 |  | 3. San Diego Gas & Electric Company shall continue to assess the best materials to use for poles in High Fire-Threat District areas, and in future Wildfire Mitigation Plans shall document that its selections for pole replacements are reasonable and consider ingress and egress impacts as part of the decision |  |  | TBD |  |  |  |  | TBD
WMP 2019 | CPUC | DECISION ON SDG&E's 2019 WMP PURSUANT TO SENATE BILL 901 | Order | 298908547.pdf | 29 |  | 4. San Diego Gas & Electric Company shall work with manufacturers to accelerate the production of new poles and covered conductors and conduct quality control on the production of this equipment. |  |  | TBD |  |  |  |  | TBD
WMP 2019 | CPUC | DECISION ON SDG&E's 2019 WMP PURSUANT TO SENATE BILL 901 | Order | 298908547.pdf | 30 |  | 5. San Diego Gas & Electric Company may implement a 25-foot post-trim clearance where necessary and feasible if such a practice is supported by scientific evidence or other data showing that such clearance will reduce risk under wildfire conditions. |  |  | Microsoft Word - SDG&E 2020 Wildfire Mitigation Plan Revised 03-02-2020 | 122 |  |  |  | Yes - via SDGE-21-04
WMP 2019 | CPUC | DECISION ON SDG&E's 2019 WMP PURSUANT TO SENATE BILL 901 | Order | 298908547.pdf | 30 |  | 6. In San Diego Gas & Electric Company’s next Wildfire Mitigation Plan, it shall propose detailed guidelines for where a 25-foot post-trim clearance for vegetation management is both feasible and necessary. |  |  | Microsoft Word - SDG&E 2020 Wildfire Mitigation Plan Revised 03-02-2020 | 122 |  |  |  | Yes - via SDGE-21-04
WMP 2019 | CPUC | DECISION ON SDG&E's 2019 WMP PURSUANT TO SENATE BILL 901 | Order | 298908547.pdf | 30 |  | 7. Prior to implementing a generator grant program, San Diego Gas & Electric Company shall consider technologies other than fossil generation that could provide benefits with safer and cleaner operation. | [7 empty] | TBD
WMP 2019 | CPUC | DECISION ON SDG&E's 2019 WMP PURSUANT TO SENATE BILL 901 | Order | 298908547.pdf | 30 |  | 8. The metrics portion of San Diego Gas & Electric Company’s future Wildfire Mitigation Plans shall be focused on outcomes, measuring the effectiveness by which the mitigation implemented reduces the risk of its electrical lines and equipment causing a catastrophic wildfire. | [7 empty] | TBD
WMP 2019 | CPUC | DECISION ON SDG&E's 2019 WMP PURSUANT TO SENATE BILL 901 | Order | 298908547.pdf | 30 |  | 9. Nothing in this decision changes the notice, communication, outreach or other requirements of the Commission’s de-energization decision issued concurrently in Rulemaking 18-12-005. | [7 empty] | TBD
WMP 2019 | CPUC | DECISION ON SDG&E's 2019 WMP PURSUANT TO SENATE BILL 901 | Order | 298908547.pdf | 30 |  | 10. San Diego Gas & Electric shall give the following customer support to utility customers affected by a wildfire, during, and after a wildfire: (a) support for low-income customers; (b) billing adjustments; (c) deposit waivers; (d) extended payment plans; (e) suspension of disconnection and nonpayment fees; (f) repair processing and timing; (g) access to utility representatives; and (h) access to outage reporting and emergency communications | [7 empty] | TBD
WMP 2019 | CPUC | DECISION ON SDG&E's 2019 WMP PURSUANT TO SENATE BILL 901 | Order | 298908547.pdf | 30 |  | 11. San Diego Gas & Electric shall communicate its plan for community outreach and public awareness before, during, and after in English, Spanish, Chinese (including Cantonese, Mandarin, and other Chinese languages), Tagalog, and Vietnamese, as well as Korean and Russian where those languages are prevalent in the service territory | [7 empty] | TBD
WMP 2019 | CPUC | DECISION ON SDG&E's 2019 WMP PURSUANT TO SENATE BILL 901 | Order | 298908547.pdf | 31 |  | 12. San Diego Gas & Electric’s 2020 Wildfire Mitigation Plan shall use the quantitative risk assessment framework adopted in Decision 18-12-014 in the Safety Model Assessment Proceeding to evaluate and compare the cost effectiveness of each of the mitigations that were under consideration in developing the Wildfire Mitigation Plan. The Wildfire Mitigation Plan shall provide the risk spend efficiency results of the quantitative risk analysis and include an explanation of the Multi-Attribute Variable Framework used and how it was constructed | [7 empty] | TBD
WMP 2019 | CPUC | DECISION ON SDG&E's 2019 WMP PURSUANT TO SENATE BILL 901 | Order | 298908547.pdf | 31 |  | 13. San Diego Gas & Electric is authorized to open the memorandum account described in Public Utilities Code Section 8386(e), which provides: “At the time it approves each plan, the commission shall authorize the utility to establish a memorandum account to track costs incurred to implement the plan.” | [7 empty] | TBD
WMP 2019 | CPUC | DECISION ON SDG&E's 2019 WMP PURSUANT TO SENATE BILL 901 | Order | 298908547.pdf | 31 |  | 14. San Diego Gas & Electric may not seek or obtain double recovery of the costs tracked in the Section 8386(e) account authorized in the previous paragraph, and the costs tracked in the memorandum account described in Public Utilities Code Section 8386(j), which the utility established with the Commission’s Energy Division’s approval. The Section 8386(j) account is described in Senate Bill 901 as follows: “(j) Each electrical corporation shall establish a memorandum account to track costs incurred for fire risk mitigation that are not otherwise covered in the electrical corporation’s revenue requirements.” | [7 empty] | TBD
WMP 2019 | CPUC | DECISION ON SDG&E's 2019 WMP PURSUANT TO SENATE BILL 901 | Order | 298908547.pdf | 31 | N/A | 15. Nothing in this decision relieves San Diego Gas & Electric of the requirement to conform all of the activities described in its Wildfire Mitigation Plan to existing law, regulation and Commission General Orders | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
WMP 2019 | CPUC | DECISION ON SDG&E's 2019 WMP PURSUANT TO SENATE BILL 901 | Order | 298908547.pdf | 31 | N/A | 16. This proceeding remains open. This order is effective today. Dated May 30, 2019, at San Francisco, California. | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
WMP 2020 | WSD | SDG&E’s First Quarterly Report | Class B (applicable to all utilities ) | WSD 002 - Deficiencies and Condition; https://docs.cpuc.ca.gov/PublishedDocs/Published/G000/M340/K859/340859823.PDF; https://docs.cpuc.ca.gov/PublishedDocs/Published/G000/M340/K883/340883294.pdf | A1 | Guidance 1 – Lack of RSE Information WMPs contain sparse and sporadic detail regarding RSEs of WMP initiatives | Insufficient • Does not calculate a separate ignition or wildfire consequence risk values, instead providing a percentage reduction for either one or the other. • States some initiatives are still grouped together but does not provide an explanation for each instance in which this occurs. • The actual consequences of PSPS that SDG&E is planning to take into account are not provided. | In its first quarterly report, each electrical corporation shall provide the following: i - its calculated reduction in ignition risk for each initiative in its 2020 WMP; ii - its calculated reduction in wildfire consequence risk for each initiative in its 2020 WMP and the risk models used to calculate (i) and (ii) | SDGE Quarterly Report on 2020 WMP for Q3 2020 09-09-2020.pdf | https://energysafety.ca.gov/wp-content/uploads/docs/wmp-2020/sdge-first-quarterly-report-on-2020-wmp-9-9-2020.pdf | 5-18 | Supplemental Filing Addressing 2020 WMP Qtr Insufficiencies |  | 2-16 | No | Conditions not met: progress being monitored. | WSD-019 Action Statement SDGE_2021WMP - Appendix 10.pdf | https://energysafety.ca.gov/wp-content/uploads/docs/misc/docket/387708478.pdf
WMP 2020 | WSD | SDG&E’s First Quarterly Report | Class B (applicable to all utilities ) | WSD 002 - Deficiencies and Condition; https://docs.cpuc.ca.gov/PublishedDocs/Published/G000/M340/K859/340859823.PDF; https://docs.cpuc.ca.gov/PublishedDocs/Published/G000/M340/K883/340883294.pdf | A2 | Guidance 2 – Lack of alternatives analysis for chosen initiatives | 2020 WMP submissions contain little to no detail regarding utilities’ process for comparing potential WMP initiatives. While most WMP initiatives are generally assumed to reduce utility wildfire risk, there are typically several alternatives that can address specific drivers of utility ignitions and near misses. However, 2020 WMPs generally do not include any discussion of which alternatives were considered, how the utility evaluated the efficacy of each alternative, and how the utility ultimately decided upon the suite of initiatives presented in its 2020 WMP | In its first quarterly report, each electrical corporation shall provide the following: i. all alternatives considered for each grid hardening or vegetation management initiative in its 2020 WMP; ii. all tools, models, and other resources used to compare alternative initiatives; iii. how it quantified and determined the risk reduction benefits of each initiative; and iv. why it chose to implement each initiative over alternative options. | SDGE Quarterly Report on 2020 WMP for Q3 2020 09-09-2020.pdf | https://energysafety.ca.gov/wp-content/uploads/docs/wmp-2020/sdge-first-quarterly-report-on-2020-wmp-9-9-2020.pdf | 19-26 | San Diego Gas & Electric 2021 WMP Action Statement Supplemental - November 1, 2021 |  | 24 | Yes; via SDGE-21-09 SDG&E’s Decision‐Making Process | Conditions not met: folded into new condition SDGE-21-9 (Inadequate transparency associated with SDG&E’s decision-making process) 2021 Supplemental - Utility sufficiently addressed the required remedy. For related areas for continued improvement, see Sections 4.6.3 and 4.6.4 of this Decision | Final Decision on WMP 2022 - Table A-1 | https://energysafety.ca.gov/wp-content/uploads/docs/misc/docket/387708478.pdf
WMP 2020 | WSD | SDG&E’s Remedial Compliance Plan | Class A | WSD 002 - Deficiencies and Condition; https://docs.cpuc.ca.gov/PublishedDocs/Published/G000/M340/K859/340859823.PDF; https://docs.cpuc.ca.gov/PublishedDocs/Published/G000/M340/K883/340883294.pdf | A3 | Condition Guidance-3: Lack of Risk Modeling to Inform Decision-making | • The information provided in the RCP lacks any depth of detail and does not provide sufficient insight or transparency regarding the nature of SDG&E’s Wildfire Next Generation System (WiNGS) risk model or how it applies to SDG&E’s decision-making regarding asset management, vegetation management, grid hardening, or Public Safety Power Shutoff (PSPS). • While WiNGS represents the “next generation” of SDG&E’s risk modeling approach, it provides no insight into the decision-making process that supported its selected portfolio of initiatives presented in SDG&E’s 2020 WMP. | Action SDGE-1: SDG&E shall provide a high-level description of its risk-informed decision-making approach used to select the portfolio of mitigation initiatives presented in its 2020 WMP. Action SDGE-2: SDG&E shall provide initiative-level details on the current and future approaches to its decision-making in selecting WMP initiatives, identifying where systematic and programmatic advancements are expected. These initiative-level details shall minimally include: 1) an identification the specific risk being mitigated or problem being addressed, 2) how the initiative or program was selected, 3) how prioritization or targeting is approached for each initiative or program, 4) future plans to improve risk modeling for the initiative or program, and 5) a timeline for the implementation and updating of risk modeling to support the decision-making for each initiative or program. At a minimum, these details shall be provided for every initiative associated with asset management, vegetation management, grid hardening, and PSPS identified in SDG&E’s 2020 WMP. Action SDGE-3: SDG&E shall provide a table describing its risk assessment techniques used for each initiative in the format used by SCE. | San Diego Gas & Electric Company’s 2020 Wildfire Mitigation Plan Remedial Compliance Plan |  |  | SDGE WMP Remedial Compliance Plan 07-27-2020 (R.18-10-007).pdf |  | 2-4 | N/A - Yes | No longer applicable: resolved. | WSD-019 Action Statement SDGE_2021WMP - Appendix 10.pdf | https://energysafety.ca.gov/wp-content/uploads/docs/misc/docket/387708478.pdf
WMP 2020 | WSD | SDG&E’s First Quarterly Report | Class B (applicable to all utilities ) | WSD 002 - Deficiencies and Condition; https://docs.cpuc.ca.gov/PublishedDocs/Published/G000/M340/K859/340859823.PDF; https://docs.cpuc.ca.gov/PublishedDocs/Published/G000/M340/K883/340883294.pdf | A4 | Guidance 4 – Lack of discussion on PSPS impacts | Across 2020 WMP submissions, utilities indicate goals of reducing the scope, frequency and duration of PSPS events but also indicate intentions of continuing to implement PSPS as a wildfire mitigation measure in the immediate future. Considering the rapid expansion of PSPS use as a wildfire mitigation measure, and the numerous hardships, inconveniences and hazards created by its vast implementation, it is concerning that 2020 WMPs provide no discussion of how the chosen portfolio of initiatives will allow the utility to achieve its goals for reducing PSPS impacts. Specifically, no 2020 WMPs discuss the relationship between various grid hardening, vegetation management, and asset management initiatives and the corresponding impacts on thresholds for initiating PSPS events. | In its first quarterly report, each electrical corporation shall detail whether and how each initiative in its WMP: i. affects its threshold values for initiating PSPS events; ii. is expected to reduce the frequency (i.e. number of events) of PSPS events; iii. is expected to reduce the scope (i.e. number of customers impacted) of PSPS events; iv. is expected to reduce the duration of PSPS events; and v. supports its directional vision for necessity of PSPS, as outlined in Section 4.4 of its WMP | SDGE Quarterly Report on 2020 WMP for Q3 2020 09-09-2020.pdf | https://energysafety.ca.gov/wp-content/uploads/docs/wmp-2020/sdge-first-quarterly-report-on-2020-wmp-9-9-2020.pdf | 27-38 | Supplemental Filing Addressing 2020 WMP Qtr Insufficiencies |  | 29-37 | Yes | Conditions met: deficiency resolved. | WSD-019 Action Statement SDGE_2021WMP - Appendix 10.pdf | https://energysafety.ca.gov/wp-content/uploads/docs/misc/docket/387708478.pdf
WMP 2020 | WSD | SDG&E’s First Quarterly Report | Class B (applicable to all utilities ) | WSD 002 - Deficiencies and Condition; https://docs.cpuc.ca.gov/PublishedDocs/Published/G000/M340/K859/340859823.PDF; https://docs.cpuc.ca.gov/PublishedDocs/Published/G000/M340/K883/340883294.pdf | A5 | Guidance 5 – Aggregation of initiatives into programs | In their 2020 WMP submissions, electrical corporations often combine various initiatives into broader programs and report cost, risk and other related data at the program level. This aggregation of initiatives and bundled reporting creates several issues. First, because cost data is typically reported across programs and not individual initiatives, it is not possible for the WSD to evaluate the efficacy of each initiative. Second, when initiatives are bundled and reported together as programs, it prevents the WSD from being able to assess which initiatives are effectively reducing utility wildfire risk. Consequently, this creates the challenge that ineffective elements of broad programs cannot be determined and future considerations of initiatives within programs can only be done collectively. | In its first quarterly report, each electrical corporation shall: i. break out its programs outlined in section 5.3 into individual initiatives; ii. report its spend on each individual initiative; iii. describe the effectiveness of each initiative at reducing ignition probability or wildfire consequence; iv. list all data and metrics used to evaluate effectiveness described in (iii), including the threshold values used to differentiate between effective and ineffective initiatives; and v. provide the information required for each initiative in section 5.3 of the Guidelines. | SDGE Quarterly Report on 2020 WMP for Q3 2020 09-09-2020.pdf | https://energysafety.ca.gov/wp-content/uploads/docs/wmp-2020/sdge-first-quarterly-report-on-2020-wmp-9-9-2020.pdf | 39 | Supplemental Filing Addressing 2020 WMP Qtr Insufficiencies |  | 38 | Yes | Conditions met: deficiency resolved. | WSD-019 Action Statement SDGE_2021WMP - Appendix 10.pdf | https://energysafety.ca.gov/wp-content/uploads/docs/misc/docket/387708478.pdf
WMP 2020 | WSD | SDG&E’s First Quarterly Report | Class B (applicable to all utilities ) | WSD 002 - Deficiencies and Condition; https://docs.cpuc.ca.gov/PublishedDocs/Published/G000/M340/K859/340859823.PDF; https://docs.cpuc.ca.gov/PublishedDocs/Published/G000/M340/K883/340883294.pdf | A6 | Guidance 6 – Failure to disaggregate WMP initiatives from standard operations | While WMPs are designed to outline and detail filer’s plans and initiatives for mitigating wildfire risk, many existing programs also provide wildfire risk reduction benefits. For example, General Order 165 requires annual patrol inspections and detailed inspections every five years for electrical infrastructure. These programs and initiatives are often referenced in 2020 WMPs as “supporting,” “routine,” “enabling,” “standard,” or “foundational” work. For these types of programs, in most cases, electrical corporations do not report cost or risk reduction data, as the work is considered part of their electric operations and it is indicated that this information is not tracked independently. Several electrical corporations state that their programs for inspecting and maintaining crossarms, poles, transformers, transmission towers and similar infrastructure, which also reduce wildfire risk, are embedded within standard maintenance programs litigated in GRCs. Consequently, it is difficult to determine whether and how these programs incrementally impact wildfire risk reduction or if related WMP initiatives are redundant and unnecessary. While utilities may not have historically considered the costs and effectiveness of such programs and initiatives, given that numerous WMP initiatives have apparent overlap or potential redundancy, it is imperative that utilities provide such data to validate the need for and effectiveness of additional programs. It is not clear how electrical corporations are tracking their WMP activities in memorandum accounts if they do not budget for them by type of initiative. The Commission will scrutinize electrical corporations’ memorandum accounts for WMP carefully, and if all costs are simply lumped together or included in general operations and maintenance accounts, electrical corporations risk failing to provide entitlement to cost recovery. | In its first quarterly report, each electrical corporation shall: i. clearly identify each initiative in Section 5.3 of its WMP as “Standard Operations” or “Augmented Wildfire Operations;” ii. report WMP required data for all Standard Operations and Augmented Wildfire Operations; iii. confirm that it is budgeting and accounting for WMP activity of each initiative; and iv. include a “ledger” of all subaccounts that show a breakdown by initiative. | SDGE Quarterly Report on 2020 WMP for Q3 2020 09-09-2020.pdf | https://energysafety.ca.gov/wp-content/uploads/docs/wmp-2020/sdge-first-quarterly-report-on-2020-wmp-9-9-2020.pdf | 40-41 | SDGE Quarterly Report on 2020 WMP for Q3 2020 09-09-2020.pdf |  | ? | Yes | Conditions met: deficiency resolved. | WSD-019 Action Statement SDGE_2021WMP - Appendix 10.pdf | https://energysafety.ca.gov/wp-content/uploads/docs/misc/docket/387708478.pdf
WMP 2020 | WSD | SDG&E’s First Quarterly Report | Class B (applicable to all utilities ) | WSD 002 - Deficiencies and Condition; https://docs.cpuc.ca.gov/PublishedDocs/Published/G000/M340/K859/340859823.PDF; https://docs.cpuc.ca.gov/PublishedDocs/Published/G000/M340/K883/340883294.pdf | A7 | Guidance 7 – Lack of detail on effectiveness of “enhanced” inspection programs | Utilities engage in numerous ‘enhanced’ inspection programs, but it is unclear if such ‘enhanced’ programs are incrementally effective over routine patrol and detailed inspections, particularly if patrol and detail inspections are scheduled based on risk rather than GO 95 minimums. | In its first quarterly report, each electrical corporation shall detail: i. the incremental quantifiable risk identified by such ‘enhanced’ inspection programs; ii. whether it addresses the findings uncovered by ‘enhanced’ programs differently than findings discovered through existing inspections; and iii. a detailed cost-benefit analysis of combining elements of such ‘enhanced’ inspections into existing inspection programs. | SDGE Quarterly Report on 2020 WMP for Q3 2020 09-09-2020.pdf | https://energysafety.ca.gov/wp-content/uploads/docs/wmp-2020/sdge-first-quarterly-report-on-2020-wmp-9-9-2020.pdf | 42-45 | Supplemental Filing Addressing 2020 WMP Qtr Insufficiencies |  | Supplemental: 39-41 | Yes | Conditions met: deficiency resolved. | WSD-019 Action Statement SDGE_2021WMP - Appendix 10.pdf | https://energysafety.ca.gov/wp-content/uploads/docs/misc/docket/387708478.pdf
WMP 2020 | WSD |  | Class C | WSD 002 - Deficiencies and Condition; https://docs.cpuc.ca.gov/PublishedDocs/Published/G000/M340/K859/340859823.PDF; https://docs.cpuc.ca.gov/PublishedDocs/Published/G000/M340/K883/340883294.pdf | A8 | Guidance 8 - (Class C) Prevalence of equivocating language – failure of commitment. | While there have been many improvements and advancements reflected in 2020 WMPs, a key concern remains regarding discussion of WMP objectives and the prevalent use of “equivocating language” to avoid making measurable, quantifiable, and verifiable commitments. While electrical corporations make promises to quantifiably reduce PSPS impacts and the frequency of near misses and ignitions, other promises are far less specific. Terms such as, “track,” “assess,” “evaluate,” and “evolve” are repeated hundreds of times throughout the 2020 WMPs. Without sufficient details, none of these terms provide the WSD or the public with a measurable, quantifiable, and verifiable goal against which electrical corporations could be held. | In its 2021 WMP update, each electrical corporation shall: i. include objectives for each of its initiatives that are measurable, quantifiable, and verifiable by the WSD; ii. provide targets and timelines for all strategies, plans, and approaches to wildfire mitigation that are measurable, quantifiable and verifiable by the WSD; and iii. dispense with empty rhetoric and not use terms that are ambiguous, misleading, or otherwise have the result of diluting commitments. Continued use of equivocating language may result in denial of future WMPs. | SDGE Quarterly Report on 2020 WMP for Q3 2020 09-09-2020.pdf | https://energysafety.ca.gov/wp-content/uploads/docs/wmp-2020/sdge-first-quarterly-report-on-2020-wmp-9-9-2020.pdf | ? |  |  | ? | No | Conditions not met: progress being monitored, see related issue description for remedy in 5.8. Resource Allocation Methodology. | WSD-019 Action Statement SDGE_2021WMP - Appendix 10.pdf | https://energysafety.ca.gov/wp-content/uploads/docs/misc/docket/387708478.pdf
WMP 2020 | WSD | SDG&E’s First Quarterly Report | Class B (applicable to all utilities ) | WSD 002 - Deficiencies and Condition; https://docs.cpuc.ca.gov/PublishedDocs/Published/G000/M340/K859/340859823.PDF; https://docs.cpuc.ca.gov/PublishedDocs/Published/G000/M340/K883/340883294.pdf | A9 | Guidance 9 – Insufficient discussion of pilot programs | Electrical corporations do not describe how they will evaluate and expand the use of successfully piloted technology or which piloted technology has proven ineffective. To ensure pilots that are successful result in expansion, if warranted and justified with quantitative data, electrical corporations must evaluate each pilot or demonstration and describe how it will expand use of successful pilots. | In its quarterly report, each electrical corporation shall detail: i. all pilot programs or demonstrations identified in its WMP; ii. status of the pilot, including where pilots have been initiated and whether the pilot is progressing toward broader adoption; iii. results of the pilot, including quantitative performance metrics and quantitative risk reduction benefits; and ii.iv. how the electrical corporation remedies ignitions or faults revealed during the pilot on a schedule that promptly mitigates the risk of such ignition or fault, and incorporates such mitigation into its operational practices; and iv.v. a proposal for how to expand use of the technology if it reduces ignition risk materially. | SDGE Quarterly Report on 2020 WMP for Q3 2020 09-09-2020.pdf | https://energysafety.ca.gov/wp-content/uploads/docs/wmp-2020/sdge-first-quarterly-report-on-2020-wmp-9-9-2020.pdf | 46-54 | Supplemental Filing Addressing 2020 WMP Qtr Insufficiencies |  | 42-47 | Yes | Conditions met: deficiency resolved. | WSD-019 Action Statement SDGE_2021WMP - Appendix 10.pdf | https://energysafety.ca.gov/wp-content/uploads/docs/misc/docket/387708478.pdf
WMP 2020 | WSD | SDG&E’s First Quarterly Report | Class B (applicable to all utilities ) | WSD 002 - Deficiencies and Condition; https://docs.cpuc.ca.gov/PublishedDocs/Published/G000/M340/K859/340859823.PDF; https://docs.cpuc.ca.gov/PublishedDocs/Published/G000/M340/K883/340883294.pdf | A10 | Guidance 10 – Data issues general | Although the availability of data, including GIS data, provides unprecedented insight into utility infrastructure and operations, inconsistencies and gaps in the data present a number of challenges and hurdles. As it relates to GIS data, electrical corporation submissions often had inconsistent file formats and naming conventions, contained little to no metadata, were incomplete or missing many data attributes and utilized varying schema. These deficiencies rendered cross-utility comparisons impossible without substantive, resource- and timeconsuming manipulation of the data. Additional data challenges included varying interpretations of WMP Guideline data requirements, leading to inconsistency of data submitted. | Electrical corporations shall ensure that all future data submissions to the WSD adhere to the forthcoming data taxonomy and schema currently being developed by the WSD. Additionally, each electrical corporation shall file a quarterly report detailing: i. locations where grid hardening, vegetation management, and asset inspections were completed over the prior reporting period, clearly identifying each initiative and supported with GIS data, ii. the type of hardening, vegetation management and asset inspection work done, and the number of circuit miles covered, supported with GIS data iii. the analysis that led it to target that specific area and hardening, vegetation management or asset inspection initiative, and iv. hardening, vegetation management, and asset inspection work scheduled for the following reporting period, with the detail in (i) – (iii). | SDGE Quarterly Report on 2020 WMP for Q3 2020 09-09-2020.pdf | https://energysafety.ca.gov/wp-content/uploads/docs/wmp-2020/sdge-first-quarterly-report-on-2020-wmp-9-9-2020.pdf | 55-56 |  |  | ? | Yes | Conditions met: deficiency resolved | WSD-019 Action Statement SDGE_2021WMP - Appendix 10.pdf | https://energysafety.ca.gov/wp-content/uploads/docs/misc/docket/387708478.pdf
WMP 2020 | WSD | SDG&E’s First Quarterly Report | Class B (applicable to all utilities ) | WSD 002 - Deficiencies and Condition; https://docs.cpuc.ca.gov/PublishedDocs/Published/G000/M340/K859/340859823.PDF; https://docs.cpuc.ca.gov/PublishedDocs/Published/G000/M340/K883/340883294.pdf | A11 | Guidance 11 – Lack of detail on plans to address personnel | Electrical corporations do not explain in detail the range of activities that they are undertakingto recruit and train personnel to grow the overall pool of talent in areas of personnel shortage. | In its first quarterly report, each electrical corporation shall detail: i. a listing and description of its programs for recruitment and training of personnel, including for vegetation management; ii. a description of its strategy for direct recruiting and indirect recruiting via contractors and subcontractors; and iii. its metrics to track the effectiveness of its recruiting programs, including metrics to track the percentage of recruits that are newly trained, percentage from out of state, and the percentage that were working for another California utility immediately prior to being hired | SDGE Quarterly Report on 2020 WMP for Q3 2020 09-09-2020.pdf | https://energysafety.ca.gov/wp-content/uploads/docs/wmp-2020/sdge-first-quarterly-report-on-2020-wmp-9-9-2020.pdf | 57-60 | Supplemental Filing Addressing 2020 WMP Qtr Insufficiencies |  | 48 | Yes | Conditions met: deficiency resolved. | WSD-019 Action Statement SDGE_2021WMP - Appendix 10.pdf | https://energysafety.ca.gov/wp-content/uploads/docs/misc/docket/387708478.pdf
WMP 2020 | WSD | SDG&E’s First Quarterly Report | Class B (applicable to all utilities ) | WSD 002 - Deficiencies and Condition; https://docs.cpuc.ca.gov/PublishedDocs/Published/G000/M340/K859/340859823.PDF; https://docs.cpuc.ca.gov/PublishedDocs/Published/G000/M340/K883/340883294.pdf | A12 | Guidance 12 – Lack of detail of long-term planning | Electrical corporations do not provide sufficient detail regarding long-term wildfire mitigation plans and how the initiatives in their WMPs align with and support those long-term plans. | In their first quarterly report, each electrical corporations shall detail: i. its expected state of wildfire mitigation in 10 years, including 1) a description of wildfire mitigation capabilities in 10 years, 2) a description of its grid architecture, lines, and equipment; ii. a year-by-year timeline for reaching these goals; iii. a list of activities that will be required to achieve this end goal; and iv. a description of how the electrical corporation’s three -year WMP is a step on the way to this 10-year goal. | SDGE Quarterly Report on 2020 WMP for Q3 2020 09-09-2020.pdf | https://energysafety.ca.gov/wp-content/uploads/docs/wmp-2020/sdge-first-quarterly-report-on-2020-wmp-9-9-2020.pdf | 61-95 | Supplemental Filing Addressing 2020 WMP Qtr Insufficiencies |  | 49-52 | Yes | Conditions met: deficiency resolved. | WSD-019 Action Statement SDGE_2021WMP - Appendix 10.pdf | https://energysafety.ca.gov/wp-content/uploads/docs/misc/docket/387708478.pdf
WMP 2020 | WSD | SDG&E’s First Quarterly Report | SDG&E Class B (aplicable to SDGE) | WSD-005 SDGE Appendix A.pdf | A1 | SDGE-1 – Higher number of ignitions related to balloon contact | Although SDG&E has relatively low volume of ignitions (annual average over five-year reporting period of 23, compared to 440 for PG&E and 106 for SCE), over the past five years, SDG&E reports a high percentage (18%) of ignitions related to balloon contact when normalized for overhead circuit miles. Compared to PG&E, SDG&E reports more than three times the rate of such balloon contact ignitions. However, SDG&E’s percentage of balloon contact ignitions as a fraction of total ignitions is similarto SCE's, which seems to indicate that this issue is more concentrated in southern California. Considering the fact that SDG&E has substantially less overhead circuitry, as compared to peer utilities, the higher incidence of balloon caused ignitions potentially correlates to an increased risk from this ignition driver in SDG&E's service territory. However, beyond some targeted covered conductor installation and undergrounding and covered conductor initiatives, SDG&E's WMP lacks detail on which initiatives it is implementing to reduce the risk of balloon contact ignitions. | In its first quarterly report, SDG&E shall: i. list and describe the actions it is taking to study the occurrence and potential consequence of metallic balloon caused ignitions in its service territory; ii. efforts it is taking to mitigate the occurrence of such ignitions in the future; iii. the status of the action and efforts identified in (i) and (ii) above, including timelines for completion; iv. the specific initiatives in its 2020 WMP that aim to reduce the risk of balloon caused ignitions; and v. its goals, targets and quantitative measures for evaluating effectiveness of the initiatives identified in (iv) at reducing the risk of balloon caused ignitions. | SDGE Quarterly Report on 2020 WMP for Q3 2020 09-09-2020.pdf |  | 96-103 | Supplemental Filing Addressing 2020 WMP Qtr Insufficiencies |  | 53 | Yes | Conditions met: deficiency resolved. | WSD-019 Action Statement SDGE_2021WMP - Appendix 10.pdf | https://energysafety.ca.gov/wp-content/uploads/docs/misc/docket/387708478.pdf
WMP 2020 | WSD | SDG&E’s First Quarterly Report | SDG&E Class B (aplicable to SDGE) | WSD-005 SDGE Appendix A.pdf | A2 | SDGE-2 – Higher number of ignitions related to vehicle contact | Although SDG&E has relatively low volume of ignitions (annual average over five-year reporting period of 23, compared to 440 for PG&E and 106 for SCE), over the past five years, SDG&E reports approximately twice the rate of ignitions related to vehicle contact compared to PG&E and SCE, when normalized for overhead circuit miles. Considering the fact that SDG&E has substantially less overhead circuitry, as compared to peer utilities, the higher incidence of vehicle contact ignitions potentially correlates to an increased risk from this ignition driver in SDG&E's service territory. However, beyond undergrounding, SDG&E's WMP lacks detail on which initiatives it is implementing to reduce the risk of vehicle contact ignitions. | In its first quarterly report, SDG&E shall: i. list and describe the actions it is taking to study the occurrence and potential consequence of vehicle contact caused ignitions in its service territory; ii. efforts it is taking to mitigate the occurrence of such ignitions in the future; iii. the status of the action and efforts identified in (i) and (ii) above, including timelines for completion; iv. the specific initiatives in its 2020 WMP that aim to reduce the risk of vehicle contact caused ignitions; and v. its goals, targets and quantitative measures for evaluating effectiveness of the initiatives identified in (iv) at reducing the risk of vehicle contact caused ignitions. | SDGE Quarterly Report on 2020 WMP for Q3 2020 09-09-2020.pdf |  | 104-107 | Supplemental Filing Addressing 2020 WMP Qtr Insufficiencies |  | 54-56 | Yes | Conditions met: deficiency resolved. | WSD-019 Action Statement SDGE_2021WMP - Appendix 10.pdf | https://energysafety.ca.gov/wp-content/uploads/docs/misc/docket/387708478.pdf
WMP 2020 | WSD | SDG&E’s First Quarterly Report | SDG&E Class B (aplicable to SDGE) | WSD-005 SDGE Appendix A.pdf | A3 | SDGE-3 – Incorporate lessons learned into updates of its risk models | In Section 5.3.1.1 of its WMP, SDG&E fails to explain how it plans to incorporate lessons learned into updates of its risk models. For instance, the model does not currently factor in spot fires or emergency resources | In its first quarterly report, SDG&E shall describe: i. how it plans to incorporate learnings into its risk models, including a specific timeline for implementation; ii. changes or updates to its risk models identified after 2020 WMP submission; and iii. the status of implementing the changes and updates identified in (ii) above, including the expected timeframe for completion. | SDGE Quarterly Report on 2020 WMP for Q3 2020 09-09-2020.pdf |  | 108-109 | Supplemental Filing Addressing 2020 WMP Qtr Insufficiencies |  | 57-59 | Yes | Conditions met: deficiency resolved | WSD-019 Action Statement SDGE_2021WMP - Appendix 10.pdf | https://energysafety.ca.gov/wp-content/uploads/docs/misc/docket/387708478.pdf
WMP 2020 | WSD | SDG&E’s First Quarterly Report | SDG&E Class B (aplicable to SDGE) | WSD-005 SDGE Appendix A.pdf | A3 | SDGE-4 – Detail on strategic undergrounding pilots | In addressing its undergrounding efforts, SDG&E states it will determine a need to strategically underground lines through pilots that establish a baseline for project scope, cost and schedule, but does not provide sufficient detail on how it will report and share its findings. | In its first quarterly report, SDG&E shall: i. detail its plans to report and share the findings of its undergrounding pilotinitiatives; ii. outline what data it plans to collect and report for project scope, cost and schedule of these projects, and iii. explain how it intends to track and measure the effectiveness of these projects in comparison to other WMP initiatives | SDGE Quarterly Report on 2020 WMP for Q3 2020 09-09-2020.pdf | https://energysafety.ca.gov/wp-content/uploads/docs/wmp-2020/sdge-first-quarterly-report-on-2020-wmp-9-9-2020.pdf | 110-114 | Supplemental Filing Addressing 2020 WMP Qtr Insufficiencies |  | 60-65 | No | Conditions not met: progress being monitored. | WSD-019 Action Statement SDGE_2021WMP - Appendix 10.pdf | https://energysafety.ca.gov/wp-content/uploads/docs/misc/docket/387708478.pdf
WMP 2020 | WSD | SDG&E’s First Quarterly Report | SDG&E Class B (aplicable to SDGE) | WSD-005 SDGE Appendix A.pdf | A4 | SDGE-5 – Detail on need for regulatory assistance | SDG&E acknowledges potential easement and line extension barriers (from main road to house) related to undergrounding efforts, and requests regulatory assistance to alleviate barriers. However, SDG&E does not provide specific detail regarding the type of regulatory assistance needed, the required timeframe for such actions, or its plans for obtaining the needed assistance from regulators | In its first quarterly report, SDG&E shall: i. list and describe all regulatory barriers to implementation of its undergroundinginitiatives, ii. detail its proposals for specific regulatory changes needed to eliminate the barriers identified in (i) above; and iii. describe its efforts and actions over the past 3 years to collaborate with regulators and other entities responsible for implementing the regulatory changes identified in (ii) above, including status and expected timeline for implementation | SDGE Quarterly Report on 2020 WMP for Q3 2020 09-09-2020.pdf |  | 115 | Supplemental Filing Addressing 2020 WMP Qtr Insufficiencies |  | 115 | N/A - Yes | No longer applicable: resolved. | WSD-019 Action Statement SDGE_2021WMP - Appendix 10.pdf | https://energysafety.ca.gov/wp-content/uploads/docs/misc/docket/387708478.pdf
WMP 2020 | WSD | SDG&E’s First Quarterly Report | SDG&E Class B (aplicable to SDGE) | WSD-005 SDGE Appendix A.pdf | A5 | SDGE-6 – Detail on plans for reinforcing transmission lines | SDG&E’s WMP lacks sufficient detail to demonstrate the efficacy of its plans for reinforcing transmission lines – to have at least one hardened line into every transmission substation in the HFTD by 2020 and to harden 66 miles within a three-year period | In its first quarterly report, SDG&E shall: i. detail how it plans to measure and report the efficacy of its plans to reinforce transmission lines and, specifically, to have at least one hardened line into every transmission substation in the HFTD by 2020 and to harden 66 miles within the three-year plan period; ii. list and describe the specific actions and initiatives it plans to implement to achieve this plan for its transmission lines; and iii. the status and timeline for completion of all actions and initiatives identified in (ii)above. | SDGE Quarterly Report on 2020 WMP for Q3 2020 09-09-2020.pdf |  | 116-117 | Supplemental Filing Addressing 2020 WMP Qtr Insufficiencies |  | 66 | Yes | Conditions met: deficiency resolved. | WSD-019 Action Statement SDGE_2021WMP - Appendix 10.pdf | https://energysafety.ca.gov/wp-content/uploads/docs/misc/docket/387708478.pdf
WMP 2020 | WSD | SDG&E’s First Quarterly Report | SDG&E Class B (aplicable to SDGE) | WSD-005 SDGE Appendix A.pdf | A5 | SDGE-7 – Potential redundancies in VM activities | The scope and magnitude of its vegetation management activities raised concerns about potential redundancies. SDG&E seems to provide potentially redundant programs and measures, and greater evaluation of its “Master Schedule” as mentioned throughout Section 5.3.5 was needed. The Master Schedule, supplied in response to a WSD data request, only displays the schedule for routine vegetation inspections and work | In its first quarterly report, SDG&E shall: i. describe how it assesses its vegetation management processes to determine effectiveness; and ii. provide additional evaluation on how inspections overlap with one another both in timing and scope, including evaluation of effectiveness in terms of number and quality of findings per inspection. For example, if not many findings are being made, then SDG&E should provide an assessment of whether additional efforts are necessary. | SDGE Quarterly Report on 2020 WMP for Q3 2020 09-09-2020.pdf | https://energysafety.ca.gov/wp-content/uploads/docs/wmp-2020/sdge-first-quarterly-report-on-2020-wmp-9-9-2020.pdf | 118-119 | Supplemental Filing Addressing 2020 WMP Qtr Insufficiencies |  | 67 | No | Conditions not met: progress being monitored, see related issue description for remedy. | WSD-019 Action Statement SDGE_2021WMP - Appendix 10.pdf | https://energysafety.ca.gov/wp-content/uploads/docs/misc/docket/387708478.pdf
WMP 2020 | WSD | SDG&E’s First Quarterly Report | SDG&E Class B (aplicable to SDGE) | WSD-005 SDGE Appendix A.pdf | A6 | SDGE-8 – Consideration of environmental impacts, local community input | SDG&E does not provide sufficient detail regarding how it measures and accounts for the potential environmental impacts related to its vegetation management work or how it incorporates input from local stakeholders in planning and executing its vegetation management work. | In its first quarterly report, SDG&E shall describe: i. how it measures and accounts for the potential environmental impacts related to its vegetation management work; and ii. how it incorporates input from local stakeholders in planning and executing its vegetation management work. | SDGE Quarterly Report on 2020 WMP for Q3 2020 09-09-2020.pdf | https://energysafety.ca.gov/wp-content/uploads/docs/wmp-2020/sdge-first-quarterly-report-on-2020-wmp-9-9-2020.pdf | 120 | Supplemental Filing Addressing 2020 WMP Qtr Insufficiencies |  | 68-69 | No | Conditions not met: progress being monitored, see related issue description for remedy in 5.5. Vegetation Management and Inspections. | WSD-019 Action Statement SDGE_2021WMP - Appendix 10.pdf | https://energysafety.ca.gov/wp-content/uploads/docs/misc/docket/387708478.pdf
WMP 2020 | WSD | SDG&E’s First Quarterly Report | SDG&E Class B (aplicable to SDGE) | WSD-005 SDGE Appendix A.pdf | A6 | SDGE-9 – Explain how investments in undergrounding reduce planned VM spend | SDG&E indicates in its WMP plans for significant investment in undergrounding. We anticipate that increased underground infrastructure will result in cost savings from reduced or eliminated need for vegetation management for underground infrastructure. However, SDG&E's WMP reports no changes in vegetation management costs over the plan period (i.e. 2020-2022) and lacks detail on how its planned investment in undergrounding initiatives correlates to cost savings in other initiatives, such as vegetation management. | In its first quarterly report, SDG&E shall describe: i. whether and how it takes ancillary cost savings into account when evaluating the effectiveness of undergrounding initiatives; and ii. how SDG&E plans to account for realized cost savings through a reduced need for certain vegetation management activities, resulting from its undergrounding investments. | SDGE Quarterly Report on 2020 WMP for Q3 2020 09-09-2020.pdf |  | 121 | Supplemental Filing Addressing 2020 WMP Qtr Insufficiencies |  | 70 | Yes | Conditions met: deficiency resolved. | WSD-019 Action Statement SDGE_2021WMP - Appendix 10.pdf | https://energysafety.ca.gov/wp-content/uploads/docs/misc/docket/387708478.pdf
WMP 2020 | WSD |  | SDGE Class C | WSD-005 SDGE Appendix A.pdf | A7 | SDGE-10(Class C) Use of outside entities for fuel reduction | SDG&E was asked to describe whether outside entities are conducting fuel reduction projects and how this work relates to the effectiveness of the overall vegetation management program. | In its annual update, SDG&E shall detail: i. whether fuel reduction projects via outside entities are being completed, and ii. how they tie into the overall vegetation management program in terms ofeffectiveness | SDGE Quarterly Report on 2020 WMP for Q3 2020 09-09-2020.pdf |  | ? |  |  | ? | Yes | Conditions met: deficiency resolved.
WMP 2020 | WSD | SDG&E’s First Quarterly Report | SDG&E Class B (aplicable to SDGE) | WSD-005 SDGE Appendix A.pdf | A7 | SDGE-11 – Details on VM around substations | In Section 5.3.5, SDG&E's WMP lacks detail regarding its vegetation management efforts for substations beyond maintaining conductor clearance. | In its first quarterly report, SDG&E shall: i. describe how it plans fuels reduction work around its substations; and ii. whether and how it maintains defensible space around its substations. | SDGE Quarterly Report on 2020 WMP for Q3 2020 09-09-2020.pdf |  | 122 |  |  | ? | Yes | Conditions met: deficiency resolved. | WSD-019 Action Statement SDGE_2021WMP - Appendix 10.pdf | https://energysafety.ca.gov/wp-content/uploads/docs/misc/docket/387708478.pdf
WMP 2020 | WSD | SDG&E’s First Quarterly Report | SDG&E Class B (aplicable to SDGE) | WSD-005 SDGE Appendix A.pdf | A8 | SDGE-12 – Details of quality assurance, quality control | SDG&E's WMP describes a quality assurance and quality control efforts designed to evaluate and ensure the effectiveness of its vegetation management and inspection activities. However, SDG&E's WMP lacks sufficient detail regarding how these quality assurance and quality control efforts measure and evaluate the effectiveness of vegetation management and inspection activities. | In its first quarterly report, SDG&E shall: i. describe the process and measures for how its quality assurance and quality control (QA/QC) efforts evaluate the effectiveness of vegetation management and inspection activities, ii. list and describe all QA/QC audits performed, the timing of the audits, and the quantitative results of such audits, and iii. list and describe all changes implemented as a result of QA/QC audit findings. | SDGE Quarterly Report on 2020 WMP for Q3 2020 09-09-2020.pdf | https://energysafety.ca.gov/wp-content/uploads/docs/wmp-2020/sdge-first-quarterly-report-on-2020-wmp-9-9-2020.pdf | 123-124 | 2020-2022 Wildfire Mitigation Plan Update | https://www.sdge.com/sites/default/files/regulatory/SDG%26E%202022%20WMP%20Update%2002-11-2022.pdf | 7-21 | Yes; Via SDGE-21-04 Effectiveness of Enhanced Clearances SDGE-21-05 Vegetation Species and Record Keeping SDGE-21-06 Quantitative Analysis to Identify “At‐Risk” Species SDGE-21-07 Quantified Vegetation Management Compliance Targets | Utility sufficiently addressed the required remedy | Final Decision on San Diego Gas & Electric Company’s WMP 2022 Update | https://energysafety.ca.gov/wp-content/uploads/docs/misc/docket/387708478.pdf
WMP 2020 | WSD | SDG&E’s Remedial Compliance Plan | Class A | WSD-005 SDGE Appendix A.pdf | A9 | SDGE-13: Lack of Risk Reduction or Other Supporting Data for Increased Time-of-Trim Clearances | • SDG&E’s research plan for a study of the effectiveness of extended vegetation clearances is incomplete and ineffective. • SDG&E provides minimal details on its methodology, and presents a rudimentary explanation of what data will be collected and how it will be compared, in contrast to submissions from other utilities. | o Action SDGE-4: SDG&E shall provide a detailed plan for how it intends to analyze and use extended vegetation clearance data, including specific statistical methods it expects to use, how it will control for environmental variables (e.g. wind, soil, elevation, and tree species), and how it will approach the collection and reporting of required data. o Action SDGE-5: SDG&E along with PG&E and SCE shall submit a joint, unified plan that reflects collaborative efforts and contains uniform definitions, methodology, timeline, data standards, and assumptions. | San Diego Gas & Electric Company’s 2020 Wildfire Mitigation Plan Remedial Compliance Plan |  | 125-129 | 2020-2022 Wildfire Mitigation Plan Update |  | 7-11 | Yes - via SDGE-21-04 | Conditions not met: folded into new condition SDGE-21-04 (Inadequate joint plan to study the effectiveness of enhanced clearances). | Final Decision on WMP 2022 - Table A-1
WMP 2020 | WSD | SDG&E’s First Quarterly Report | SDG&E Class B (aplicable to SDGE) | WSD-005 SDGE Appendix A.pdf | A10 | 14 – Granularity of “at-risk species” Lacks detail to identify the tree species SDG&E considers “at risk” | SDG&E identifies five types of "at-risk" trees - eucalyptus, palm, oak, pine, and sycamore. However, SDG&E identifies these trees by their genus, and based on additional review, the WSD has discovered that not all tree species within a genus are considered "at-risk" trees. As such, SDG&E's WMP lacks sufficient detail to identify the tree species it considers "at-risk" and subject to its enhanced vegetation management programs. | In its first quarterly report, SDG&E shall detail the following: i. all tree species within the genera identified in its list of "at-risk"trees, ii. the measures, properties and characteristics it considers in identifying "at-risk" trees, and iii. the threshold values of the measures, properties and characteristics identified in (ii) above that result in a species being defined as "at-risk." | SDGE Quarterly Report on 2020 WMP for Q3 2020 09-09-2020.pdf |  | 129-132 | 2020-2022 Wildfire Mitigation Plan Update |  | 7-18 | Yes - via SDGE-21-04, SDGE-21-05, SDGE-21-06 | Conditions not met: folded into new conditions SDGE-21-04 (Inadequate joint plan to study the effectiveness of enhanced clearances), SDGE-21-05 (Incomplete identification of vegetation species and record keeping), and SDGE-21-06 (Limited evidence of quantitative analysis to identify “at-risk” species). | Final Decision on WMP 2022 - Table A-1
WMP 2020 | WSD | SDG&E’s First Quarterly Report | SDG&E Class B (aplicable to SDGE) | WSD-005 SDGE Appendix A.pdf | A10 | 15 – Details of centralized data repository | SDG&E indicates efforts to create a centralized data repository, however, its WMP lacks sufficient detail of the data to be included. | In its first quarterly report, SDG&E shall: i. list and describe all data it plans to provide in its centralized repository; ii. list and describe the sources and treatment of all data identified in (i) above; and iii. describe the frequency it plans to update all data identified in (i) above. | SDGE Quarterly Report on 2020 WMP for Q3 2020 09-09-2020.pdf |  | 133-134 | Supplemental Filing Addressing 2020 WMP Qtr Insufficiencies |  | 76-77 | Yes | Conditions met: deficiency resolved. | WSD-019 Action Statement SDGE_2021WMP - Appendix 10.pdf | https://energysafety.ca.gov/wp-content/uploads/docs/misc/docket/387708478.pdf
WMP 2020 | WSD | SDG&E’s First Quarterly Report | SDG&E Class B (aplicable to SDGE) | WSD-005 SDGE Appendix A.pdf | A11 | 16 – Details of cooperative fuel reduction work | A large portion of SDG&E’s HFTD area falls within federal lands. As such, it is imperative that SDG&E maintain close coordination and working relationships with the U.S. Forest Service (USFS), who is responsible for managing federal lands. SDG&E identifies specific ways in which it coordinates with the USFS, which appear sufficient for receiving permits for fuel reduction, but SDG&E does not address the resources needed to collaborate on fuel reductionefforts and establish formal agreements. | In its first quarterly report, SDG&E shall describe: i. whether it plans to collaborate with the USFS on fuel reduction programs in its service territory; ii. what programs or agreements, if any, it has in place with the USFS for fuel reduction programs; iii. the timeline for implementing initiatives identified in (i) and (ii); iv. how it plans to identify the resources needed to collaborate with the USFS on fuel reduction; and v. the status of reaching any formal agreements on fuel reduction efforts. | SDGE Quarterly Report on 2020 WMP for Q3 2020 09-09-2020.pdf |  | 135 | Supplemental Filing Addressing 2020 WMP Qtr Insufficiencies |  | 78 | Yes | Conditions met: deficiency resolved. | WSD-019 Action Statement SDGE_2021WMP - Appendix 10.pdf | https://energysafety.ca.gov/wp-content/uploads/docs/misc/docket/387708478.pdf
WMP 2021 | WSD-019 | WSD-019 Attachment A: Draft Action Statement on San Diego Gas & Electric Company’s 2021 Wildfire Mitigation Plan Update | SDGE-21-01 Table 1: Key areas for improvement and remedies. | Link to deficiency | Table 1 - Page 6 | SDGE-21-01: Inadequate transparency in accounting for ignition sources in risk modelling and mitigation selection | SDG&E identifies vehicle contact and balloon contact as the first and second highest ignition risks but does not explain how that affects its risk models or mitigation selection. | SDG&E must fully explain: 1. How third-party ignition sources feed into SDG&E’s risk models; 2. How ignition sources impact 3. SDG&E’s mitigation selection process, including: a. How SDG&E prioritizes ignition sources; b. If SDG&E treats third-party ignition sources that are not under c. SDG&E’s direct control differently than other ignition sources, and if so, how d. How SDG&E targets its mitigations efforts to reduce ignitions that are more likely to result in catastrophic wildfire conditions. | San Diego Gas & Electric 2021 WMP Action Statement Supplemental - Nov 1 2021 |  | 6 | San Diego Gas & Electric 2021 WMP Action Statement Supplemental - November 1, 2021 |  | 6 | Yes | Utility sufficiently addressed the required remedy. For a related area for continued improvement, see Section 4.6.1 of this Decision | Final Decision on WMP 2022 - Table A-1 | https://energysafety.ca.gov/what-we-do/electrical-infrastructure-safety/wildfire-mitigation-and-safety/wildfire-mitigation-plans/2022-wmp/
WMP 2021 | WSD-019 | WSD-019 Attachment A: Draft Action Statement on San Diego Gas & Electric Company’s 2021 Wildfire Mitigation Plan Update | SDGE-21-02 Table 1: Key areas for improvement and remedies. | Link to deficiency | Table 1 - Page 7 | SDGE-21-02: Lack of consistency in approach to wildfire risk modeling across utilities | The utilities do not have a consistent approach to wildfire risk modeling. For example, in their wildfire risk models, utilities use different types of data, use their individual data sets in different ways, and use different third-party vendors. The WSD recognizes that the utilities have differing service territory characteristics, differing data availability, and are at different stages in developing their wildfire risk models. However, the utilities face similar enough circumstances that there should be some level of consistency in statewide approaches to wildfire risk modeling. | The utilities must collaborate through a working group facilitated by Energy Safety to develop a more consistent statewide approach to wildfire risk modeling. After the WSD completes its evaluation of all the utilities’ 2021 WMP Updates, it will provide additional detail on the specifics of this working group. A working group to address wildfire risk modeling will allow for: 1. Collaboration among the utilities; 2. Stakeholder and academic expert input; and 3. Increased transparency. | San Diego Gas & Electric 2021 WMP Action Statement Supplemental - Nov 1 2021 |  | 7 | San Diego Gas & Electric 2021 WMP Action Statement Supplemental - November 1, 2021 |  | 7 | Yes | Utility has sufficiently addressed the required remedy thus far; Energy Safety will continue to monitor progress | Final Decision on WMP 2022 - Table A-1 | https://energysafety.ca.gov/what-we-do/electrical-infrastructure-safety/wildfire-mitigation-and-safety/wildfire-mitigation-plans/2022-wmp/
WMP 2021 | WSD-019 | WSD-019 Attachment A: Draft Action Statement on San Diego Gas & Electric Company’s 2021 Wildfire Mitigation Plan Update | SDGE-21-03 Table 1: Key areas for improvement and remedies. | Link to deficiency | Table 1 - Page 7 | SDGE-21-03: Limited evidence to support the effectiveness of covered conductor | The rationale to support the selection of covered conductor as a preferred initiative to mitigate wildfire risk lacks consistency among the utilities, leading some utilities to potentially expedite covered conductor deployment without first demonstrating a full understanding of its long-term risk reduction and cost-effectiveness. The utilities’ current covered conductor pilot efforts are limited in scope and therefore fail to provide a full basis for understanding how covered conductor will perform in the field. Additionally, utilities justify covered conductor installation by alluding to reduced PSPS risk but fail to provide adequate comparison to other initiatives’ ability to reduce PSPS risk. | The utilities must coordinate to develop a consistent approach to evaluating the long-term risk reduction and cost-effectiveness of covered conductor deployment, including: 1. The effectiveness of covered conductor in the field in comparison to alternative initiatives. 2. How covered conductor installation compares to other initiatives in its potential to reduce PSPS risk. | San Diego Gas & Electric 2021 WMP Action Statement Supplemental - Nov 1 2021 |  | 8-12 | San Diego Gas & Electric 2021 WMP Action Statement Supplemental - November 1, 2021 |  | 8-12 | Yes | Utility has sufficiently addressed the required remedy thus far; Energy Safety will continue to monitor progress. For discussion of progress and related areas for continued improvement, see Section 4.6.5.3 of this Decision. | Final Decision on WMP 2022 - Table A-1 | https://energysafety.ca.gov/what-we-do/electrical-infrastructure-safety/wildfire-mitigation-and-safety/wildfire-mitigation-plans/2022-wmp/
WMP 2021 | WSD-019 | WSD-019 Attachment A: Draft Action Statement on San Diego Gas & Electric Company’s 2021 Wildfire Mitigation Plan Update | SDGE-21-04 Table 1: Key areas for improvement and remedies. | Link to deficiency | Table 1 - Page 8 | SDGE-21-04: Inadequate joint plan to study the effectiveness of enhanced clearances | RCP Action-SDGE-4 (Class A) required SDG&E, PG&E, and SCE to “submit a joint, unified plan” to begin a study of the effectiveness of extended vegetation clearances. SDG&E submitted its plan to study the effectiveness of extended vegetation clearance as part of its 2021 WMP Update. SDG&E, PG&E, and SCE presented the “joint, unified” plan to the WSD on February 18, 2021. While it was apparent the three large utilities had discussed a unified approach, each utility presented differing analyses that would be performed to measure the effectiveness of enhanced clearances. This presentation’s content was not included in the February 26, 2021, “Supplemental Filing Addressing 2020 Wildfire Mitigation Plan Quarterly Report Insufficiencies.” The WSD acknowledges the complexity of this issue; any study performed assessing the effectiveness of enhanced clearances will take years of data collection and rigorous analysis. | SDG&E, PG&E, and SCE will participate in a multi-year vegetation clearance study. The WSD will confirm the details of this study in due course. The objectives of this study are to: 1. Establish uniform data collection standards. 2. Create a cross-utility database of tree-caused risk events (i.e., outages and ignitions caused by vegetation contact). 3. Incorporate biotic and abiotic factors into the determination of outage and ignition risk caused by vegetation contact. 4. Assess the effectiveness of enhanced clearances. n preparation for this study and the eventual analysis, SDG&E must collect the relevant data; the required data are currently defined by the WSD Geographic Information System (GIS Data Reporting Standard for California Electrical Corporations - V2). Table 2 below outlines the feature classes which the WSD believes will be most relevant to the study. Additional requirements related to this study may be included in the Action Statements for PG&E and SCE’s 2021 WMP Updates. The WSD will also be updating the GIS Reporting Standards in 2021, which may include additional data attributes for vegetation-related risk events. | San Diego Gas & Electric 2021 WMP Action Statement Supplemental - Nov 1 2021 |  | 13-14 | San Diego Gas & Electric 2021 WMP Action Statement Supplemental - November 1, 2021 |  | 13-14 | Yes | Utility has sufficiently addressed the required remedy thus far; Energy Safety will continue to monitor progress. For discussion of progress and related areas for continued improvement, see Section 4.6.5.3 of this Decision | Final Decision on WMP 2022 - Table A-1 | https://energysafety.ca.gov/what-we-do/electrical-infrastructure-safety/wildfire-mitigation-and-safety/wildfire-mitigation-plans/2022-wmp/
WMP 2021 | WSD-019 | WSD-019 Attachment A: Draft Action Statement on San Diego Gas & Electric Company’s 2021 Wildfire Mitigation Plan Update | SDGE-21-05 Table 1: Key areas for improvement and remedies. | Link to deficiency | Table 1 - Page 9 | SDGE-21-05: Incomplete identification of vegetation species and record keeping | SDG&E reports that it targets trees based on characteristics of the species. SDG&E targets “eucalyptus, palm, oak, pine, and sycamore.” However, these are not tree species, but tree genera. SDG&E needs to ensure proper identification of trees to the species level. | 1. Use scientific names in its reporting (as opposed to common names). This change will be reflected in the upcoming updates to the WSD GIS Reporting Standard. 2. Add genus and species designation input capabilities into its systems which track vegetation (e.g., vegetation inventory system and vegetation-caused outage reports). 3. If the tree’s species designation is unknown (i.e., if the inspector knows the tree as “Quercus” but is unsure whether the tree is, for example, Quercus kelloggii, Quercus lobata, or Quercus agrifolia), it must be recorded as such. Instead of simply “Quercus,” use “Quercus sp.” If referencing multiple species within a genus use “spp.” (e.g., Quercus spp.).32 4. Require its vegetation management (VM) and outage reporting personnel to use the unknown “sp.” designation only as a last resort by including this requirement in its standard operating protocols and training programs for such work. 5. Notwithstanding (4), identify the genus and species of a tree that has caused an outage33 or ignition34 in the Quarterly Data Reports (in these cases, an unknown “sp.” designation is not acceptable). 6. Teach tree species identification skills in its VM personnel training programs, both in initial and continuing education. 7. Where possible SDG&E must remedy any unknown species designations made in the field by the time SDG&E submits each Quarterly Data Report, by, for example, allowing inspectors to upload pictures of tree-identifying characteristics and having a qualified individual identify the species using the inspector’s report. | San Diego Gas & Electric 2021 WMP Action Statement Supplemental - Nov 1 2021 |  | 15-16 | San Diego Gas & Electric 2021 WMP Action Statement Supplemental - November 1, 2021 |  | 15-16 | Yes | Utility sufficiently addressed the required remedy. Energy Safety will monitor compliance through quality checks of SDG&E’s Quarterly Data Reports | Final Decision on WMP 2022 - Table A-1 | https://energysafety.ca.gov/what-we-do/electrical-infrastructure-safety/wildfire-mitigation-and-safety/wildfire-mitigation-plans/2022-wmp/
WMP 2021 | WSD-019 | WSD-019 Attachment A: Draft Action Statement on San Diego Gas & Electric Company’s 2021 Wildfire Mitigation Plan Update | SDGE-21-06 Table 1: Key areas for improvement and remedies. | Link to deficiency | Table 1 - Page 11 | SDGE-21-06: Limited evidence of quantitative analysis to identify “at-risk” species | Mussey Grade Road Alliance (MGRA) analyzed SDG&E’s vegetation-caused outage data to determine the outages per 1000 trees per year by tree genus. MGRA found that palm, cypress, and century plant constituted the highest risk with >1 outage per 1000 trees per year. These data are inconsistent with SDG&E’s statement that it “targeted species identified as a higher risk due to growth potential, failure characteristics and relative outage frequency. These species include eucalyptus, sycamore, oak, pine, and palm.” Only palms are common to both lists. Additionally, QR Action-SDGE-46 (Class B), from Jan. 8, 2021, required SDG&E to “define quantitative threshold values […] for the criteria used to define a tree as ‘at-risk.’” SDG&E responded to this requirement stating, “evaluation is based more on qualitative factors rather than quantitative.” SDG&E must use quantitative data to inform its “at-risk” species targeting; qualitative evaluation of a tree’s risk does not adequately address the quantitative risk of ignition or outage. | In Section 7.3.5.15 (or equivalent) of its 2022 WMP Update, SDG&E must: 1. Describe its methodologies for determining what species it considers “at-risk.” 2. Explain in complete detail why discrepancies exist between the genera with the highest number of outages per 1000 trees per year and SDG&E’s “targeted species identified as a higher risk due to growth potential, failure characteristics and relative outage frequency.” 3. Define quantitative threshold values (whether a standard value, a range of values, or an example of a typical value) for the criteria used to define a tree as “at-risk.” | San Diego Gas & Electric 2021 WMP Action Statement Supplemental - Nov 1 2021 |  | 17-20 | San Diego Gas & Electric 2021 WMP Action Statement Supplemental - November 1, 2021 |  | 17-20 | Yes | Utility sufficiently addressed the required remedy | Final Decision on WMP 2022 - Table A-1 | https://energysafety.ca.gov/what-we-do/electrical-infrastructure-safety/wildfire-mitigation-and-safety/wildfire-mitigation-plans/2022-wmp/
WMP 2021 | WSD-019 | WSD-019 Attachment A: Draft Action Statement on San Diego Gas & Electric Company’s 2021 Wildfire Mitigation Plan Update | SDGE-21-07 Table 1: Key areas for improvement and remedies. | Link to deficiency | Table 1 - Page 12 | SDGE-21-07: Need for quantified vegetation management (VM) compliance targets | In Table 12, SDG&E only defines quantitative targets for four of 20 VM initiatives. The WSD is statutorily required to audit SDG&E when a “substantial portion” of SDG&E’s VM work is complete; without quantifiable targets in the WMP and subsequent reporting on those targets in the Quarterly Data Report (QDR) and Quarterly Initiative Update (QIU), the WSD cannot fully realize its statutory obligations. | SDG&E must define quantitative targets for all VM initiatives in Table 12. If quantitative targets are not applicable to an initiative, SDG&E must fully justify this, define goals within that initiative, and include a timeline in which it expects to achieve those goals. | San Diego Gas & Electric 2021 WMP Action Statement Supplemental - Nov 1 2021 |  | 21-22 | San Diego Gas & Electric 2021 WMP Action Statement Supplemental - November 1, 2021 |  | 21-22 | Yes | Utility sufficiently addressed the required remedy | Final Decision on WMP 2022 - Table A-1 | https://energysafety.ca.gov/what-we-do/electrical-infrastructure-safety/wildfire-mitigation-and-safety/wildfire-mitigation-plans/2022-wmp/
WMP 2021 | WSD-019 | WSD-019 Attachment A: Draft Action Statement on San Diego Gas & Electric Company’s 2021 Wildfire Mitigation Plan Update | SDGE-21-08 Table 1: Key areas for improvement and remedies. | Link to deficiency | Table 1 - Page 12 | SDGE-21-08: Non-communicative remote-controlled switches | SDG&E experienced several incidents in which non-communicative Supervisory Control and Data Acquisition (SCADA) switches caused customers to be de-energized without notice. SDG&E indicates that it has no plans to alter its existing practices to ensure this issue does not continue in the future. In its WMP Update, SDG&E does not discuss any plans to take system-level proactive steps to validate that existing SCADA switches remain fully functional or to ensure that newly installed SCADA switches are fully functional. | 1. Discuss its plans to take systemlevel proactive steps to validate that existing SCADA switches remain fully functional. 2. Discuss its plans to ensure that newly installed SCADA switches are fully functional. 3. Describe the steps it is taking to increase and improve inspectionsand testing of SCADA switches. | San Diego Gas & Electric 2021 WMP Action Statement Supplemental - Nov 1 2021 |  | 23 | San Diego Gas & Electric 2021 WMP Action Statement Supplemental - November 1, 2021 |  | 23 | Yes | Utility sufficiently addressed the required remedy. For more information, see Section 4.6.6 of this Decision | Final Decision on WMP 2022 - Table A-1 | https://energysafety.ca.gov/what-we-do/electrical-infrastructure-safety/wildfire-mitigation-and-safety/wildfire-mitigation-plans/2022-wmp/
WMP 2021 | WSD-019 | WSD-019 Attachment A: Draft Action Statement on San Diego Gas & Electric Company’s 2021 Wildfire Mitigation Plan Update | SDGE-21-09 Table 1: Key areas for improvement and remedies. | Link to deficiency | Table 1 - Page 13 | SDGE-21-09: Inadequate transparency associated with SDG&E’s decision-making process | SDG&E does not clearly explain its initiative selection process or how RSE estimates impact the process. For example, SDG&E does not quantitively justify the selection of undergrounding compared to other mitigation alternatives. RSE estimates provide a quantitative pathway to assess the relative risk reduction benefit provided by mitigation initiatives and inform the initiative selection process. | 1. Elaborate on its decision-making process to include a thorough overview of its initiative selection procedure. The overview must show the rankings of the relative decision-making factors (e.g., planning and execution lead times, resource constraints, etc.) and pinpoint where quantifiable risk reductions and RSE estimates are considered in the initiative selection process. The WSD recommends a cascading, dynamic “if-then” style flowchart to effectively demonstrate this prioritization process and satisfy this requirement. 2. Using the newly developed decision-making overview, demonstrate that its undergrounding projects are a reasonable and effective use of resources to achieve risk reduction compared to other mitigation alternatives. | San Diego Gas & Electric 2021 WMP Action Statement Supplemental - Nov 1 2021 |  | 24 | San Diego Gas & Electric 2021 WMP Action Statement Supplemental - November 1, 2021 |  | 24 | Yes | Utility sufficiently addressed the required remedy. For related areas for continued improvement, see Sections 4.6.3 and 4.6.4 of this Decision | Final Decision on WMP 2022 - Table A-1 | https://energysafety.ca.gov/what-we-do/electrical-infrastructure-safety/wildfire-mitigation-and-safety/wildfire-mitigation-plans/2022-wmp/
WMP 2021 | WSD-019 | WSD-019 Attachment A: Draft Action Statement on San Diego Gas & Electric Company’s 2021 Wildfire Mitigation Plan Update | SDGE-21-10 Table 1: Key areas for improvement and remedies. | Link to deficiency | Table 1 - Page 13 | SDGE-21-10: Insufficient detail regarding prioritization of HFTD in undergrounding and covered conductor mitigation efforts | Stakeholders expressed concerns that SDG&E is not adequately targeting its covered conductor installations and undergrounding efforts to high-risk circuits in its HFTD areas.46 It can be more cost-effective to bundle projects in proximate geographic areas47 than to perform mitigation initiatives strictly from the highest priority circuit segment to the lowest. Additionally, a strictly hierarchical strategy would not necessarily reduce PSPS events in the near term. It is therefore theoretically possible that a strategy of directing 100% of mitigation efforts to HFTD areas may not be the most reasonable and cost-effective strategy for reducing wildfire risk and PSPS events. However, SDG&E does not provide sufficient detail regarding its strategy for determining workflow to fully assess if SDG&E is sufficiently prioritizing HFTD areas in its undergrounding and covered conductor mitigation efforts. SDG&E must effectively demonstrate that its mitigation efforts are focused on efficiently reducing wildfire risk and PSPS events. | SDG&E must fully demonstrate that its undergrounding and covered conductor mitigation efforts are focused on efficiently reducing wildfire risk and PSPS events, including a description of how SDG&E determines the order in which circuit segments are scheduled for mitigation. | San Diego Gas & Electric 2021 WMP Action Statement Supplemental - Nov 1 2021 |  | 25 | San Diego Gas & Electric 2021 WMP Action Statement Supplemental - November 1, 2021 |  | 25 | Yes | Utility sufficiently addressed the required remedy. For more information, see SDG&E Progress under Sections 4.6.1 and 4.6.3 of this Decision | Final Decision on WMP 2022 - Table A-1 | https://energysafety.ca.gov/what-we-do/electrical-infrastructure-safety/wildfire-mitigation-and-safety/wildfire-mitigation-plans/2022-wmp/
WMP 2021 | WSD-019 | WSD-019 Attachment A: Draft Action Statement on San Diego Gas & Electric Company’s 2021 Wildfire Mitigation Plan Update | SDGE-21-11 Table 1: Key areas for improvement and remedies. | Link to deficiency | Table 1 - Page 14 | SDGE-21-11: RSE values vary across utilities | The WSD is concerned by the stark variances in RSE estimates, sometimes on several orders of magnitude, for the same initiatives calculated by different utilities. For example, PGE’s RSE for covered conductor installation was 4.08,48 SDGE’s RSE was 76.73,49 and SCE’s RSE was 4,192.50 These drastic differences reveal that there are significant discrepancies between the utilities’ inputs and assumptions, which further support the need for exploration and alignment of these calculations. | The utilities51 must collaborate through a working group facilitated by Energy Safety52 to develop a more standardized approach to the inputs and assumptions used for RSE calculations. After the WSD completes its evaluation of the 2021 WMP Updates, it will provide additional detail on the specifics of this working group. | San Diego Gas & Electric 2021 WMP Action Statement Supplemental - Nov 1 2021 |  | 26 | San Diego Gas & Electric 2021 WMP Action Statement Supplemental - November 1, 2021 |  | 26 | Yes | Utility has sufficiently addressed the required remedy thus far; Energy Safety will continue to monitor progress | Final Decision on WMP 2022 - Table A-1 | https://energysafety.ca.gov/what-we-do/electrical-infrastructure-safety/wildfire-mitigation-and-safety/wildfire-mitigation-plans/2022-wmp/
WMP 2022 | Energy Safety | Final Decision on San Diego Gas & Electric Company’s WMP 2022 Update | Section 7: List of Utility Areas for Continued Improvement and Required Progres | https://efiling.energysafety.ca.gov/eFiling/Getfile.aspx?fileid=52635&shareable=true | 108 | SDGE-22-01. Prioritized List of Wildfire Risks and Drivers | SDG&E’s prioritized list of wildfire risks and drivers (2022 WMP Update Table 4-6) weighs the risk drivers by average outage multiplied by ignition rate; it does not account for the likelihood of the ignition to cause a catastrophic wildfire. | SDG&E must further refine its prioritized list of wildfire risks and drivers. It must do so by weighting each risk driver by likelihood of causing a catastrophic wildfire (e.g., does this ignition tend to happen in high wildfire risk areas identified by SDG&E’s risk models, including the HFTD). | SDGE_2023_WMP_R2.1.pdf |  | Appendix D - Page 1-2 | 2021 WMP Action Statement |  | Appendix D - Page 1-2 | Yes | SDG&E has sufficiently addressed the required remedy | Draft Res SPD-16 WMP Decision 2023 - Table A-1.pdf | https://www.cpuc.ca.gov/-/media/cpuc-website/divisions/safety-policy-division/documents/final-resolution-spd16--sdge-wmp-decision-2023.pdf
WMP 2022 | Energy Safety | Final Decision on San Diego Gas & Electric Company’s WMP 2022 Update | Section 7: List of Utility Areas for Continued Improvement and Required Progres | https://efiling.energysafety.ca.gov/eFiling/Getfile.aspx?fileid=52635&shareable=true | 108 | SDGE-22-02. Collaboration and Research in Best Practices in Relation to Climate Change Impacts and Wildfire Risk and Consequence Modeling. | SDG&E and the other large IOUs are currently pursuing their own efforts at integrating the potential impacts of climate change in their risk and consequence modeling. They are not actively collaborating with each other on these efforts nor taking advantage of the existing climate change modeling expertise of state agencies and academic institutions | SDG&E must participate in an Energy Safety-led scoping meeting to discuss how utilities can best learn from each other, external agencies, and outside experts. | SDGE_2023_WMP_R2.1.pdf | https://www.sdge.com/sites/default/files/regulatory/2024-06-07_SDGE_2023_WMP_R2.1.pdf | Appendix D - Page 3 | 2023-2025 WILDFIRE MITIGATION PLAN | https://www.sdge.com/sites/default/files/regulatory/2024-06-07_SDGE_2023_WMP_R2.1.pdf | Appendix D - Page 3 | Yes | SDG&E has sufficiently addressed the required progress thus far; Energy Safety will continue to monitor progress. | Draft Res SPD-16 WMP Decision 2023 - Table A-1.pdf | https://www.cpuc.ca.gov/-/media/cpuc-website/divisions/safety-policy-division/documents/final-resolution-spd16--sdge-wmp-decision-2023.pdf
WMP 2022 | Energy Safety | Final Decision on San Diego Gas & Electric Company’s WMP 2022 Update | Section 7: List of Utility Areas for Continued Improvement and Required Progres | https://efiling.energysafety.ca.gov/eFiling/Getfile.aspx?fileid=52635&shareable=true | 109 | • SDGE-22-03. Utility Arborist Training Initiatives. | SDG&E does not provide details on the scope of Utility Arborist training initiatives it is developing or supporting. | SDG&E must provide more details on utility vegetation management workforce training initiatives it is developing and/or supporting. Details to include are as follows: 1. The number of people entering classes using the Utility Arborist Trainee curriculum at California community colleges and/or other training programs developed and/or supported by SDG&E. 2. The number completing the classes or other training programs. 3. The number of those completing the classes or other training programs subsequently joining the utility vegetation management workforce. 4. Any additional details on how SDG&E is addressing utility vegetation management labor constraints. | SDGE_2023_WMP_R2.1.pdf |  | Appendix D - Page 4-5 | 2023 WMP - Appendix D - ACIs |  | Appendix D - Page 4-5 | Yes | SDG&E has sufficiently addressed the required progress | Draft Res SPD-16 WMP Decision 2023 - Table A-1.pdf | https://www.cpuc.ca.gov/-/media/cpuc-website/divisions/safety-policy-division/documents/final-resolution-spd16--sdge-wmp-decision-2023.pdf
WMP 2022 | Energy Safety | Final Decision on San Diego Gas & Electric Company’s WMP 2022 Update | Section 7: List of Utility Areas for Continued Improvement and Required Progres | https://efiling.energysafety.ca.gov/eFiling/Getfile.aspx?fileid=52635&shareable=true | 109 | • SDGE-22-04. Inclusion of Community Vulnerability in Consequence Modeling. | SDG&E does not currently include the impacts of wildfire on communities, such as community vulnerability, within consequence modeling | SDG&E must participate in an Energy Safety-led scoping meeting to discuss how to best learn from each other, external agencies and outside experts | SDGE_2023_WMP_R2.1.pdf |  | Appendix D - Page 6 | 2023 WMP - Appendix D - ACIs |  | Appendix D - Page 6 | Yes | SDG&E has sufficiently addressed the required progress thus far; Energy Safety will continue to monitor progress. | Draft Res SPD-16 WMP Decision 2023 - Table A-1.pdf | https://www.cpuc.ca.gov/-/media/cpuc-website/divisions/safety-policy-division/documents/final-resolution-spd16--sdge-wmp-decision-2023.pdf
WMP 2022 | Energy Safety | Final Decision on San Diego Gas & Electric Company’s WMP 2022 Update | Section 7: List of Utility Areas for Continued Improvement and Required Progres | https://efiling.energysafety.ca.gov/eFiling/Getfile.aspx?fileid=52635&shareable=true | 110 | • SDGE-22-05. Fire Suppression Considerations. | SDG&E’s fire spread modeling does not currently factor in fire suppression effects (e.g., fire department efforts). | SDG&E must work with other utilities to evaluate how to best account for, quantify, and model suppression effects on wildfire spread. Further guidance will be determined and covered during the risk model working group meetings established by Energy Safety’s 2021 WMP Action Statements. | SDGE_2023_WMP_R2.1.pdf |  | Appendix D - Page 7 | 2023 WMP - Appendix D - ACIs |  | Appendix D - Page 7 | Yes | SDG&E has sufficiently addressed the required progress thus far; Energy Safety will continue to monitor progress. | Draft Res SPD-16 WMP Decision 2023 - Table A-1.pdf | https://www.cpuc.ca.gov/-/media/cpuc-website/divisions/safety-policy-division/documents/final-resolution-spd16--sdge-wmp-decision-2023.pdf
WMP 2022 | Energy Safety | Final Decision on San Diego Gas & Electric Company’s WMP 2022 Update | Section 7: List of Utility Areas for Continued Improvement and Required Progres | https://efiling.energysafety.ca.gov/eFiling/Getfile.aspx?fileid=52635&shareable=true | 110 | • SDGE-22-06. Eight-Hour Fire Spread Simulations. | SDG&E’s eight-hour fire spread simulations may be impacting the accuracy of its wildfire spread consequence modeling | 1. SDG&E must benchmark against other utilities to account for catastrophic fire risk that occurs more than eight hours post-ignition and provide a summary of lessons learned in its 2023 WMP. Further guidance may be determined and covered within the risk model working group established by the 2021 WMP Action Statements. 2. SDG&E must include a description of resulting changes to its wildfire spread consequence modeling or anticipated changes and a timeline for implementation. | SDGE_2023_WMP_R2.1.pdf |  | Appendix D - Page 8 | 2023 WMP - Appendix D - ACIs |  | Appendix D - Page 8 | Yes | SDG&E has sufficiently addressed the required progress thus far; Energy Safety will continue to monitor progress. | Draft Res SPD-16 WMP Decision 2023 - Table A-1.pdf | https://www.cpuc.ca.gov/-/media/cpuc-website/divisions/safety-policy-division/documents/final-resolution-spd16--sdge-wmp-decision-2023.pdf
WMP 2022 | Energy Safety | Final Decision on San Diego Gas & Electric Company’s WMP 2022 Update | Section 7: List of Utility Areas for Continued Improvement and Required Progres | https://efiling.energysafety.ca.gov/eFiling/Getfile.aspx?fileid=52635&shareable=true | 111 | • SDGE-22-07. Risk Prioritization for Mitigation Measures. | SDG&E only calculated the cumulative top risk coverage estimates based on risk model output for covered conductor and undergrounding | SDG&E must provide an update on its progress using risk model output to inform its initiative plans based on highest risk areas, including determination of top risk percentages, for all initiatives, including covered conductor and undergrounding. | SDGE_2023_WMP_R2.1.pdf |  | Appendix D - Page 9 | 2023 WMP - Appendix D - ACIs |  | Appendix D - Page 9 | Yes; Via ACI SDGE-23-06 | SDG&E has not sufficiently addressed the required progress. For related areas for continued improvement, see section 8.1 and 11 of this Decision. SDGE-23B-06 - SDG&E sufficiently addressed the required progres | Draft Res SPD-16 WMP Decision 2023 - Table A-1.pdf | https://www.cpuc.ca.gov/-/media/cpuc-website/divisions/safety-policy-division/documents/final-resolution-spd16--sdge-wmp-decision-2023.pdf
WMP 2022 | Energy Safety | Final Decision on San Diego Gas & Electric Company’s WMP 2022 Update | Section 7: List of Utility Areas for Continued Improvement and Required Progres | https://efiling.energysafety.ca.gov/eFiling/Getfile.aspx?fileid=52635&shareable=true | 111 | • SDGE-22-08. Evaluation of Wildfire Risk Outside of the HFTD. | SDG&E has yet to evaluate the potential need for adjustment of the HFTD. | • SDG&E must analyze its service territory to determine if there are additional higher wildfire risk areas outside of the HFTD boundaries and include in its 2023 WMP its findings and a description of the analysis performed, including factors considered, and include any territory newly classified by SDG&E as high risk within the treatment area for its mitigation initiatives. • If it identifies any new areas of higher wildfire risk, SDG&E must provide a process outlining the formal steps necessary to have those areas considered for recognition in the CPUC-defined HFTD | SDGE_2023_WMP_R2.1.pdf |  | Appendix D - Page 10 | 2023 WMP - Appendix D - ACIs |  | Appendix D - Page 10 | Yes | SDG&E has sufficiently addressed the required progress thus far; Energy Safety will continue to monitor progress. | Draft Res SPD-16 WMP Decision 2023 - Table A-1.pdf | https://www.cpuc.ca.gov/-/media/cpuc-website/divisions/safety-policy-division/documents/final-resolution-spd16--sdge-wmp-decision-2023.pdf
WMP 2022 | Energy Safety | Final Decision on San Diego Gas & Electric Company’s WMP 2022 Update | Section 7: List of Utility Areas for Continued Improvement and Required Progres | https://efiling.energysafety.ca.gov/eFiling/Getfile.aspx?fileid=52635&shareable=true | 111 | • SDGE-22-09. Evaluation of Wind Gust Effects on Vegetation-Related Failures. | SDG&E does not currently account for wind gust effects within its vegetation probability of failure (PoF) model | 1. Provide a description of any analysis it has completed to evaluate the effects of wind gust effects on vegetation failures (including factors considered, weighing of various factors, and wind studies used) and provide a description of any additional analysis needed to evaluate wind gust effects on vegetation-related failures. 2. Provide an update on any changes made to its PoF model as a result of its analysis of wind gust effects on vegetation failures. 3. Provide a timeline for any future analyses on wind gust effects, as applicable, including reasoning for the need of future analysis, and cadence for performance of future analysis. 4. Provide a timeline for any future changes to its model related to wind gust effects | SDGE_2023_WMP_R2.1.pdf |  | Appendix D - Page 11-12 | 2023 WMP - Appendix D - ACIs |  | Appendix D - Page 11-12 | Yes | SDG&E has sufficiently addressed the required progress thus far; Energy Safety will continue to monitor progress. | Draft Res SPD-16 WMP Decision 2023 - Table A-1.pdf | https://www.cpuc.ca.gov/-/media/cpuc-website/divisions/safety-policy-division/documents/final-resolution-spd16--sdge-wmp-decision-2023.pdf
WMP 2022 | Energy Safety | Final Decision on San Diego Gas & Electric Company’s WMP 2022 Update | Section 7: List of Utility Areas for Continued Improvement and Required Progres | https://efiling.energysafety.ca.gov/eFiling/Getfile.aspx?fileid=52635&shareable=true | 112 | • SDGE-22-10. Wildfire Consequence Modeling Improvements. | SDG&E does not use its wildfire consequence modeling as a tool to model potential ignitions in near real-time as faults/outages occur in the HFTD | SDG&E must discuss how it explored the use of its wildfire consequence modeling and/or developed processes to locate, prioritize, and respond to the locations of faults/outages in the HFTD as they happen. | SDGE_2023_WMP_R2.1.pdf |  | Appendix D - Page 13 | 2023 WMP - Appendix D - ACIs |  | Appendix D - Page 13 | Yes | SDG&E has sufficiently addressed the required progress | Draft Res SPD-16 WMP Decision 2023 - Table A-1.pdf | https://www.cpuc.ca.gov/-/media/cpuc-website/divisions/safety-policy-division/documents/final-resolution-spd16--sdge-wmp-decision-2023.pdf
WMP 2022 | Energy Safety | Final Decision on San Diego Gas & Electric Company’s WMP 2022 Update | Section 7: List of Utility Areas for Continued Improvement and Required Progres | https://efiling.energysafety.ca.gov/eFiling/Getfile.aspx?fileid=52635&shareable=true | 112 | • SDGE-22-11. Applying Joint Lessons Learned Concerning Covered Conductor. | SDG&E has not yet provided goals and timelines for implementing lessons learned from the covered conductor effectiveness joint study. | Provide a concrete list of goals with planned dates of implementation for any lessons learned in the covered conductor effectiveness joint study. Provide a table indicating which WMP sections include changes (compared to its 2021 and 2022 Updates) as a result of the covered conductor effectiveness joint study. This should include, but not be limited to: a. Changes made to covered conductor effectiveness calculations. b. Changes made to initiative selection based on effectiveness and benchmarking across alternatives. c. Inclusion of rapid earth fault current limiter (REFCL), open phase detection (OPD), early fault detection (EFD), and distribution fault anticipation (DFA) as alternatives, including for PSPS considerations. d. Changes made to cost impacts and drivers. e. An update on data sharing across utilities on measured effectiveness of covered conductor in-field and pilot results, including collective evaluation. | SDGE_2023_WMP_R2.1.pdf |  | Appendix D - Page 14 | 2023 WMP - Appendix D - ACIs |  | Appendix D - Page 14 | Yes | SDG&E has sufficiently addressed the required progress. For related areas for continued improvement, see Sections 8.1 and 11 of this Decision. | Draft Res SPD-16 WMP Decision 2023 - Table A-1.pdf | https://www.cpuc.ca.gov/-/media/cpuc-website/divisions/safety-policy-division/documents/final-resolution-spd16--sdge-wmp-decision-2023.pdf
WMP 2022 | Energy Safety | Final Decision on San Diego Gas & Electric Company’s WMP 2022 Update | Section 7: List of Utility Areas for Continued Improvement and Required Progres | https://efiling.energysafety.ca.gov/eFiling/Getfile.aspx?fileid=52635&shareable=true | 113 | • SDGE-22-12. Covered Conductor Inspection and Maintenance. | SDG&E lacks specific directives for inspection procedures regarding covered conductor inspection and maintenance. | All electrical corporations (not including independent transmission operators) must work to share and determine best practices for inspecting and maintaining covered conductor, including either augmenting existing practices or developing new programs. This should be considered as a continuation of the covered conductor study established by Energy Safety’s 2021 WMP Action Statements. The study will continue to be utility-led, with the expectation for Energy Safety to be included as a participant. A report on progress on this continuation of the covered conductor effectiveness joint study will be expected in the 2023 WMPs. | SDGE_2023_WMP_R2.1.pdf |  | Appendix D - Page 15 | 2023 WMP - Appendix D - ACIs |  | Appendix D - Page 15 | Yes; via ACI SDGE-23-12 | SDG&E has not sufficiently addressed the required progress. For related areas for continued improvement, see Sections 8.1 and 11 of this Decision. SDGE-23-12: SDG&E sufficiently addressed the required progress. | Draft Res SPD-16 WMP Decision 2023 - Table A-1.pdf | https://www.cpuc.ca.gov/-/media/cpuc-website/divisions/safety-policy-division/documents/final-resolution-spd16--sdge-wmp-decision-2023.pdf
WMP 2022 | Energy Safety | Final Decision on San Diego Gas & Electric Company’s WMP 2022 Update | Section 7: List of Utility Areas for Continued Improvement and Required Progres | https://efiling.energysafety.ca.gov/eFiling/Getfile.aspx?fileid=52635&shareable=true | 113 | • SDGE-22-13. New Technologies Evaluation and Implementation. | SDG&E is not moving forward with its REFCL pilot and does not provide a plan for exploring new technologies that could increase effectiveness against ignition or wildfire risk. | All electrical corporations (not including independent transmission operators) must collaborate to evaluate the effectiveness of new technologies that support grid hardening and situational awareness such as REFCL and DFA/EFD, particularly in combination with other initiatives. Utilities must also share practices and evaluate implementation strategies for these new technologies. This should be considered as a continuation of the covered conductor effectiveness joint study established by Energy Safety’s 2021 WMP Action Statements. The scope of this study should now be expanded to cover grid hardening overall. The study will continue to be utility-led, with the expectation for Energy Safety to be included as a participant. A report on progress on this expansion of the covered conductor effectiveness joint study will be expected in the 2023 WMPs. | SDGE_2023_WMP_R2.1.pdf |  | Appendix D - Page 16 | 2023 WMP - Appendix D - ACIs |  | Appendix D - Page 16 | Yes & Ongoing; via ACIs SDGE-23-08, SDGE-23-09 | SDG&E has not sufficiently addressed the required progress. For related areas for continued improvement, see Sections 8.1 and 11 of this Decision. SDGE-23-08: Continuation of Grid Hardening Joint Studies - Continue in WMP 2026-2028 SDGE-23-09: New Technologies Evaluation and REFCL - ImplementatioSDG&E sufficiently addressed the required progress | Draft Res SPD-16 WMP Decision 2023 - Table A-1.pdf | https://www.cpuc.ca.gov/-/media/cpuc-website/divisions/safety-policy-division/documents/final-resolution-spd16--sdge-wmp-decision-2023.pdf
WMP 2022 | Energy Safety | Final Decision on San Diego Gas & Electric Company’s WMP 2022 Update | Section 7: List of Utility Areas for Continued Improvement and Required Progres | https://efiling.energysafety.ca.gov/eFiling/Getfile.aspx?fileid=52635&shareable=true | 114 | • SDGE-22-14. Grid Hardening Decision-Making Process Transparency. | SDG&E’s description of how it selects mitigation initiatives based on risk factors lacks detail, such as how its listed considerations affect initiative selection. | 1. A description of its analysis of how it selects mitigation initiatives based on risk factors evident in certain locations. This should include how SDG&E selects mitigation initiatives to optimize risk reduction for specific ignition risks. 2. Details on how each consideration listed in Figure 7-4 row 3 “Desktop Feasibility” in SDG&E’s 2022 Update is weighted, and how each consideration affects SDG&E’s initiative selection for grid hardening. | SDGE_2023_WMP_R2.1.pdf |  | Appendix D - Page 17-19 | 2023 WMP - Appendix D - ACIs |  | Appendix D - Page 17-19 | Yes; Via ACI SDGE-23-06 | SDG&E has not sufficiently addressed the required progress. For related areas for continued improvement, see section 8.1 and 11 of this Decision. SDGE-23B-06 - SDG&E sufficiently addressed the required progres | Draft Res SPD-16 WMP Decision 2023 - Table A-1.pdf | https://www.cpuc.ca.gov/-/media/cpuc-website/divisions/safety-policy-division/documents/final-resolution-spd16--sdge-wmp-decision-2023.pdf
WMP 2022 | Energy Safety | Final Decision on San Diego Gas & Electric Company’s WMP 2022 Update | Section 7: List of Utility Areas for Continued Improvement and Required Progres | https://efiling.energysafety.ca.gov/eFiling/Getfile.aspx?fileid=52635&shareable=true | 114 | • SDGE-22-15. Undergrounding Risk-Spend Efficiency Demonstration. | SDG&E plans on ramping up future undergrounding efforts without adequately demonstrating costeffectiveness based on specific ignition risks. | SDG&E must provide a description of its decision-making process demonstrating risk/cost benefit analysis as it pertains to future undergrounding installations. | SDGE_2023_WMP_R2.1.pdf |  | Appendix D - Page 20-21 | 2023 WMP - Appendix D - ACIs |  | Appendix D - Page 20-21 | Yes; Via ACI SDGE-23-06 | SDG&E has not sufficiently addressed the required progress. For related areas for continued improvement, see section 8.1 and 11 of this Decision. SDGE-23B-06 - SDG&E sufficiently addressed the required progres | Draft Res SPD-16 WMP Decision 2023 - Table A-1.pdf | https://www.cpuc.ca.gov/-/media/cpuc-website/divisions/safety-policy-division/documents/final-resolution-spd16--sdge-wmp-decision-2023.pdf
WMP 2022 | Energy Safety | Final Decision on San Diego Gas & Electric Company’s WMP 2022 Update | Section 7: List of Utility Areas for Continued Improvement and Required Progres | https://efiling.energysafety.ca.gov/eFiling/Getfile.aspx?fileid=52635&shareable=true | 115 | • SDGE-22-16. Enabling Circuits with Advanced Protection. | SDG&E has not been meeting its targets for enabling circuits with advanced protection. | SDG&E must explain how it will meet its current and future targets for enabling circuits with advanced protection and provide a detailed description of that plan in its 2023 WMP. | SDGE_2023_WMP_R2.1.pdf |  | Appendix D - Page 22 | 2023 WMP - Appendix D - ACIs |  | Appendix D - Page 22 | Yes | SDG&E has sufficiently addressed the required progress. For related areas for continued improvement, see Sections 8.1 and 11 of this Decision. | Draft Res SPD-16 WMP Decision 2023 - Table A-1.pdf | https://www.cpuc.ca.gov/-/media/cpuc-website/divisions/safety-policy-division/documents/final-resolution-spd16--sdge-wmp-decision-2023.pdf
WMP 2022 | Energy Safety | Final Decision on San Diego Gas & Electric Company’s WMP 2022 Update | Section 7: List of Utility Areas for Continued Improvement and Required Progres | https://efiling.energysafety.ca.gov/eFiling/Getfile.aspx?fileid=52635&shareable=true | 115 | SDGE-22-17. Further Development of Integrating Risk-Informed Decision Making for Inspection Scheduling and Planning | While SDG&E has some risk-informed prioritization for cyclical schedules (e.g., every three years) based on Tier 2 and Tier 3 designations, SDG&E has not yet implemented risk modeling-informed prioritization for its inspections | G&E must provide a concrete timeline detailing when SDG&E plans to implement risk modelinginformed prioritization for each of its inspection types. | SDGE_2023_WMP_R2.1.pdf |  | Appendix D - Page 23 | 2023 WMP - Appendix D - ACIs |  | Appendix D - Page 23 | Yes | SDG&E has sufficiently addressed the required progress thus far; Energy Safety will continue to monitor progress. | Draft Res SPD-16 WMP Decision 2023 - Table A-1.pdf | https://www.cpuc.ca.gov/-/media/cpuc-website/divisions/safety-policy-division/documents/final-resolution-spd16--sdge-wmp-decision-2023.pdf
WMP 2022 | Energy Safety | Final Decision on San Diego Gas & Electric Company’s WMP 2022 Update | Section 7: List of Utility Areas for Continued Improvement and Required Progres | https://efiling.energysafety.ca.gov/eFiling/Getfile.aspx?fileid=52635&shareable=true | 115 | • SDGE-22-18. Evaluation and Interpretation of “Other” Equipment Failures. | Within Tables 7.1 and 7.2 (2022 Update), many of SDG&E’s equipment failures are grouped in a category defined as “other,” with some causes seemingly falling under other existing categories, or represented as “null.” | 1. A review of the categories that fall under “other” in order to ensure the categories accurately reflect the causes of equipment failures. 2. A clear justification for why causes are categorized as “other,” including an explanation for why “weather related” causes are listed as such. 3. A breakout of the events that fall under “other.” | SDGE_2023_WMP_R2.1.pdf |  | Appendix D - Page 24 | 2023 WMP - Appendix D - ACIs |  | Appendix D - Page 24 | Yes | SDG&E sufficiently addressed the required progress. | Draft Res SPD-16 WMP Decision 2023 - Table A-1.pdf | https://www.cpuc.ca.gov/-/media/cpuc-website/divisions/safety-policy-division/documents/final-resolution-spd16--sdge-wmp-decision-2023.pdf
WMP 2022 | Energy Safety | Final Decision on San Diego Gas & Electric Company’s WMP 2022 Update | Section 7: List of Utility Areas for Continued Improvement and Required Progres | https://efiling.energysafety.ca.gov/eFiling/Getfile.aspx?fileid=52635&shareable=true | 116 | • SDGE-22-19. Plan to Address Missing Asset Data. | Less than one percent of SDG&E’s data on installation dates for older assets is missing, but SDG&E lacks a proactive plan to address the missing data | 1. Provide a plan, including a timeline, to obtain and address the missing installation dates within asset data. This includes developing a plan to determine missing installation dates and fill estimated installation dates into asset databases where possible. a. Include an explanation for instances where installation dates cannot be estimated. 2. Evaluate whether using installation dates would increase predictability within the PoI and evaluate any additional causes for limitations on data quality | SDGE_2023_WMP_R2.1.pdf |  | Appendix D - Page 25 | 2023 WMP - Appendix D - ACIs |  | Appendix D - Page 25 | Yes | SDG&E sufficiently addressed the required progress. | Draft Res SPD-16 WMP Decision 2023 - Table A-1.pdf | https://www.cpuc.ca.gov/-/media/cpuc-website/divisions/safety-policy-division/documents/final-resolution-spd16--sdge-wmp-decision-2023.pdf
WMP 2022 | Energy Safety | Final Decision on San Diego Gas & Electric Company’s WMP 2022 Update | Section 7: List of Utility Areas for Continued Improvement and Required Progres | https://efiling.energysafety.ca.gov/eFiling/Getfile.aspx?fileid=52635&shareable=true | 116 | • SDGE-22-20. Progression of Effectiveness of Enhanced Clearances Joint Study. | The 2021 Action Statements required the large IOUs to conduct a study assessing the effectiveness of enhanced clearances. Progress has been made in the study; however, the study must continue to progress. | SDG&E, along with PG&E and SCE, must (1) standardize the data collection process for the cross-utility database of tree-caused risk events, (2) determine where and in what form the database will exist, (3) examine, to the best of their ability, whether the correlation between enhanced clearances and the lower number of tree-caused outage events may be attributable to other factors beyond clearances, such as the management of hazard trees and the installation of covered conductor. | SDGE_2023_WMP_R2.1.pdf |  | Appendix D - Page 26 | 2023 WMP - Appendix D - ACIs |  | Appendix D - Page 26 | Yes | SDG&E sufficiently addressed the required progress. for related areas of continued improvement, see sections 8.2.4 and 11 of this Decision. | Draft Res SPD-16 WMP Decision 2023 - Table A-1.pdf | https://www.cpuc.ca.gov/-/media/cpuc-website/divisions/safety-policy-division/documents/final-resolution-spd16--sdge-wmp-decision-2023.pdf
WMP 2022 | Energy Safety | Final Decision on San Diego Gas & Electric Company’s WMP 2022 Update | Section 7: List of Utility Areas for Continued Improvement and Required Progres | https://efiling.energysafety.ca.gov/eFiling/Getfile.aspx?fileid=52635&shareable=true | 117 | • SDGE-22-21. Consideration of Alternatives to Fuels Treatment Activity. | SDG&E’s practice of removing dead or dying fine fuels within a 50-foot radius of selected poles is not a long-term solution to this particular wildfire mitigation challenge | 1. SDG&E must present an analysis of alternatives to its fuels treatment activity including consideration of, but not limited to, undergrounding, REFCL, and pole replacement (e.g., with steel). SDG&E must provide a discussion of its progress in quantifying the additional risk reduction in its 2023 WMP. 2. SDG&E must quantify the additional risk reduction achieved by removing dead or dying fine fuels within a 50-foot radius as compared to the Public Resources Code Section 4292 standard | SDGE_2023_WMP_R2.1.pdf |  | Appendix D - Page 27 | 2023 WMP - Appendix D - ACIs |  | Appendix D - Page 27 | Yes | SDG&E sufficiently addressed the required progress. | Draft Res SPD-16 WMP Decision 2023 - Table A-1.pdf | https://www.cpuc.ca.gov/-/media/cpuc-website/divisions/safety-policy-division/documents/final-resolution-spd16--sdge-wmp-decision-2023.pdf
WMP 2022 | Energy Safety | Final Decision on San Diego Gas & Electric Company’s WMP 2022 Update | Section 7: List of Utility Areas for Continued Improvement and Required Progres | https://efiling.energysafety.ca.gov/eFiling/Getfile.aspx?fileid=52635&shareable=true | 117 | SDGE-22-22. Participation in Vegetation Management Best Management Practices Scoping Meeting. | Vegetation management processes and protocols for the reduction of wildfire risk are not uniform across electrical corporations. | SDG&E and all other electrical corporations (not including independent transmission operators) must participate in an Energy Safety-led scoping meeting to discuss how utilities can best learn from each other and future topics to explore regarding vegetation management best management practices for wildfire risk reduction. They must also participate in any follow-on activities to this meeting. This vegetation management best management practices scoping meeting may result in additional meetings or workshops or the formation of a working group. Energy Safety will provide additional details on the specifics of this scoping meeting in due course. | SDGE_2023_WMP_R2.1.pdf |  | Appendix D - Page 28 | 2023 WMP - Appendix D - ACIs |  | Appendix D - Page 28 | Yes | SDG&E sufficiently addressed the required progress. | Draft Res SPD-16 WMP Decision 2023 - Table A-1.pdf | https://www.cpuc.ca.gov/-/media/cpuc-website/divisions/safety-policy-division/documents/final-resolution-spd16--sdge-wmp-decision-2023.pdf
WMP 2022 | Energy Safety | Final Decision on San Diego Gas & Electric Company’s WMP 2022 Update | Section 7: List of Utility Areas for Continued Improvement and Required Progres | https://efiling.energysafety.ca.gov/eFiling/Getfile.aspx?fileid=52635&shareable=true | 117 | SDGE-22-23. PSPS Wind Threshold Change Evaluations | SDG&E has not yet evaluated PSPS threshold changes as a result of installing covered conductor. | 1. Coordinate with other utilities to understand the impacts of installing covered conductor and associated changes that could be made to PSPS thresholds as a result. 2. Provide a summary of key findings, including any changes implemented to SDG&E’s PSPS procedures or practices. 3. Provide any studies completed by third-parties on wind speed thresholds for covered conductor, or, if not yet completed, a timeline for completion. 4. Provide a description and associated justification of any modifications to PSPS wind speed thresholds since the 2022 Update. | SDGE_2023_WMP_R2.1.pdf |  | Appendix D - Page 29 | 2023 WMP - Appendix D - ACIs |  | Appendix D - Page 29 | Yes | SDG&E has sufficiently addressed the required progress thus far; Energy Safety will continue to monitor progress. | Draft Res SPD-16 WMP Decision 2023 - Table A-1.pdf | https://www.cpuc.ca.gov/-/media/cpuc-website/divisions/safety-policy-division/documents/final-resolution-spd16--sdge-wmp-decision-2023.pdf
WMP 2022 | Energy Safety | Final Decision on San Diego Gas & Electric Company’s WMP 2022 Update | Section 7: List of Utility Areas for Continued Improvement and Required Progres | https://efiling.energysafety.ca.gov/eFiling/Getfile.aspx?fileid=52635&shareable=true | 118 | • SDGE-22-24. Replacing Protective Devices for Sensitivity Setting Capabilities. | SDG&E does not have a plan to proactively replace old field devices to include protective device sensitivity setting capabilities. | SDG&E must evaluate whether it should replace field devices with sensitivity setting capabilities. SDG&E must include in this evaluation a survey of existing coverage and determination of which areas could benefit from replacements. The evaluation should assess the extent to which replacements for increased sensitivity settings would reduce ignition risk. If SDG&E determines that field device replacement would decrease ignition risk, SDG&E must create and implement a plan to do so. If SDG&E determines that replacement of field devices would not effectively decrease ignition risk, SDG&E must explain why it would not. | SDGE_2023_WMP_R2.1.pdf |  | WMP Base - 30 | 2024-07-05_SDGE_2025_WMP-Update_R2.pdf | https://www.sdge.com/sites/default/files/regulatory/2024-07-05_SDGE_2025_WMP-Update_R2.pdf | 2025 WMP Update Pg 101-102 | Yes; via 2025 WMP Update ACI SDGE-23-15 Evaluation of Sensitive Relay Profile in highest Risk Areas | SDG&E sufficiently addressed the required progress. | FINAL_Decision_for_SDGE_2025_WMP_Update.pdf
WMP 2022 | Energy Safety | Final Decision on San Diego Gas & Electric Company’s WMP 2022 Update | Section 7: List of Utility Areas for Continued Improvement and Required Progres | https://efiling.energysafety.ca.gov/eFiling/Getfile.aspx?fileid=52635&shareable=true | 119 | • SDGE-22-25. Validation of Vegetation Risk Index (VRI). | SDG&E states that it does not conduct any standard verification or validation on the Vegetation Risk Index (VRI) because “this is not a predictive model but rather a qualitative index.” Regardless of the nature of the index, if it is being used to drive decisions about PSPS as claimed, there should be evidence that there is in fact some relationship between the output and results (in this case, that the ratings of low/medium/high are correlated with increasing rates of vegetation-related outages) | 1. Evaluate the VRI output and report on the results of that effort. 2. Evaluate post-PSPS event data and compare to the VRI model to check for validity of output. 3. Adjust the model as needed based on lessons learned or provide a timeline and plan for associated adjustments. | SDGE_2023_WMP_R2.1.pdf |  | Appendix D - Page 31 | 2023 WMP - Appendix D - ACIs |  | Appendix D - Page 31 | Yes | SDG&E has sufficiently addressed the required progress. For related areas for continued improvement, see Sections 7 and 11 of this Decision. | Draft Res SPD-16 WMP Decision 2023 - Table A-1.pdf | https://www.cpuc.ca.gov/-/media/cpuc-website/divisions/safety-policy-division/documents/final-resolution-spd16--sdge-wmp-decision-2023.pdf
WMP 2022 | Energy Safety | Final Decision on San Diego Gas & Electric Company’s WMP 2022 Update | Section 7: List of Utility Areas for Continued Improvement and Required Progres | https://efiling.energysafety.ca.gov/eFiling/Getfile.aspx?fileid=52635&shareable=true | 119 | • SDGE-22-26. Validation of Wildfire Risk Reduction Model (WRRM). | SDG&E describes the validation of its WRRM as consisting only of visual verification by comparison using GIS software to determine that the results of the model “coincide with known conditions around the service territory.” As described in its 2022 Update Section 4.5.1.3, the WRRM incorporates 10 separate data elements, many of which could be validated in a more robust fashion to determine sources and magnitude of uncertainty in the model | SDG&E must determine which inputs to its WRRM can be more rigorously validated, conduct such validation, or provide a plan including a timeline to conduct such validation, and report on the results of that effort. | SDGE_2023_WMP_R2.1.pdf |  | Appendix D - Page 32 | 2023 WMP - Appendix D - ACIs |  | Appendix D - Page 32 | Yes | SDG&E has sufficiently addressed the required progress. For related areas for continued improvement, see Sections 7 and 11 of this Decision. | Draft Res SPD-16 WMP Decision 2023 - Table A-1.pdf | https://www.cpuc.ca.gov/-/media/cpuc-website/divisions/safety-policy-division/documents/final-resolution-spd16--sdge-wmp-decision-2023.pdf
WMP 2022 | Energy Safety | Final Decision on San Diego Gas & Electric Company’s WMP 2022 Update | Section 7: List of Utility Areas for Continued Improvement and Required Progres | https://efiling.energysafety.ca.gov/eFiling/Getfile.aspx?fileid=52635&shareable=true | 119 | • SDGE-22-27. Improvements to Capital Allocation Methodology. | SDG&E’s progress on the Maturity Survey for capability 41 under the Resource Allocation Methodology Section H.V “Portfolio-wide initiative allocation methodology” is limited by question H.V. that asks “to what extent does the utility allocate capital to initiatives based on [RSE]?” Based on SDG&E’s response to this question, the utility anticipates no progress on this question in 2022 | SDG&E must provide a timeline with attainable benchmarks for using accurate RSE estimates to determine capital allocation at a portfolio level | SDGE_2023_WMP_R2.1.pdf |  | Appendix D - Page 33 | 2023 WMP - Appendix D - ACIs |  | Appendix D - Page 33 | Yes | SDG&E has sufficiently addressed the required progress thus far; Energy Safety will continue to monitor progress. | Draft Res SPD-16 WMP Decision 2023 - Table A-1.pdf | https://www.cpuc.ca.gov/-/media/cpuc-website/divisions/safety-policy-division/documents/final-resolution-spd16--sdge-wmp-decision-2023.pdf
WMP 2022 | Energy Safety | Final Decision on San Diego Gas & Electric Company’s WMP 2022 Update | Section 7: List of Utility Areas for Continued Improvement and Required Progres | https://efiling.energysafety.ca.gov/eFiling/Getfile.aspx?fileid=52635&shareable=true | 120 | • SDGE-22-28. Improvements to the RSE Verification Process. | SDG&E does not currently, nor does it plan to, verify its RSE estimates with independent experts or other utilities in California | SDG&E must provide a timeline with attainable benchmarks to verify its RSE estimates with independent experts or other utilities in California | SDGE_2023_WMP_R2.1.pdf |  | WMP Base - 34 | 2024-07-05_SDGE_2025_WMP-Update_R2.pdf | https://www.sdge.com/sites/default/files/regulatory/2024-07-05_SDGE_2025_WMP-Update_R2.pdf | 2025 WMP Update Pg 45-50 | Yes; via 2025 WMP Update ACI SDGE-23-03: PSPS and Wildfire Risk Trade-Off Transparency | SDG&E sufficiently addressed the required progress. | FINAL_Decision_for_SDGE_2025_WMP_Update.pdf
WMP 2022 | Energy Safety | Final Decision on San Diego Gas & Electric Company’s WMP 2022 Update | Section 7: List of Utility Areas for Continued Improvement and Required Progres | https://efiling.energysafety.ca.gov/eFiling/Getfile.aspx?fileid=52635&shareable=true | 120 | • SDGE-22-29. Mitigation Plan for Frequently De-Energized Circuits. | SDG&E does not go far enough in its plans to reduce the future risk of PSPS on its most frequently deenergized circuits, identified in Table 8.6-1 (2022 Update | SDG&E must demonstrate that it is planning to achieve a greater level of PSPS risk reduction on the frequently de-energized circuits identified in Table 8.6-1. This must include a greater percentage of risk reduction, a higher percentage of customers who will no longer be de-energized, and a greater percentage of circuit miles mitigated | SDGE_2023_WMP_R2.1.pdf |  | Appendix D - Page 35 | 2023 WMP - Appendix D - ACIs |  | Appendix D - Page 35 | Yes | SDG&E has sufficiently addressed the required progress. | Draft Res SPD-16 WMP Decision 2023 - Table A-1.pdf | https://www.cpuc.ca.gov/-/media/cpuc-website/divisions/safety-policy-division/documents/final-resolution-spd16--sdge-wmp-decision-2023.pdf
WMP 2022 | Energy Safety | Final Decision on San Diego Gas & Electric Company’s WMP 2022 Update | Section 7: List of Utility Areas for Continued Improvement and Required Progres | https://efiling.energysafety.ca.gov/eFiling/Getfile.aspx?fileid=52635&shareable=true | 121 | • SDGE-22-30. Improvements to the WiNGS-Ops and WiNGS-Planning Models. | SDG&E indicates it is planning enhancements to its WiNGS-Ops model in 2022. Additionally, SDG&E indicates that the WiNGS-Planning model does not include customers impacted by sectionalizing and resiliency programs | SDG&E must provide a progress report on the performance of WiNGS-Ops as used in its 2022 PSPS decision-making process, including successes, issues encountered, and lessons learned. 1. In particular, SDG&E must include in its report the progress it made prior to September 1, 2022, in incorporating WiNGS-Ops in the PSPS decision-making process. 2. SDG&E must also report any progress it made on incorporating PSPS risk reduction quantification to include customers impacted by sectionalizing and resiliency programs through the WiNGS-Planning model. | SDGE_2025_WMP-Update_R2.pdf |  | 2025 WMP Update Pg 65-84 | 2023 WMP - Appendix D - ACIs |  | 2025 WMP Update Pg 65-84 | Ongoing; Showed Progress via: SDGE-22-30, SDGE-23-07: Third-Party Recommendations for Model Improvements | SDG&E must respond to this revised area for continued improvement in its 2026-2028 Base WMP | FINAL_Decision_for_SDGE_2025_WMP_Update.pdf |  |  | Final Decision on SDGE's 2022 Wildfire Mitigation Plan Update.pdf
Note on R18: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This final link should be: Final Action Statement on SDG&E 2021 WMP Update

## Sheet1
Source WMP | SDG&E or All IOUs | Deficiency Source | Type | Source Link | Page Ref | Deficiency Title | Description | Utility MUST (Action Item) | SDG&E Shown Progress: | Source Link | Page Ref | SDG&E Deficiency Addressed in: | Source Link | Page Ref | Met the Requirement (Y/N) | Regulator Acknowlegement of Requirement Met | Source Link | Page Reference
WMP 2019 | SDG&E | D.19-05-039: CPUC Decision on SDG&E's 2019 WMP Per SB 901 | Order | Link | 29 | N/A | 1. In San Diego Gas & Electric Company’s next Wildfire Mitigation Plan, it shall include a summary of the results of the detailed inspections it conducts in the High Fire Threat District Tier 3 area of its service territory | See Description | N/A | N/A | N/A | SDG&E 2020 WMP - Revised (Ex SDG&E-T2-01R-A) | Link | 105 | Yes | N/A | N/A | N/A
WMP 2019 | SDG&E | D.19-05-039 | Order | Link | 29 | N/A | 2. San Diego Gas & Electric Company may proceed with its proposed Fire Risk Mitigation plan to replace wood poles with steel poles in this Wildfire Mitigation Plan cycle, but shall base its decisions for pole replacements on reasonable criteria and consider ingress and egress impacts as part of the decision | See Description | N/A | N/A | N/A | SDG&E 2020 WMP - Revised (Ex SDG&E-T2-01R-A) | Link | 146 | Yes | N/A | N/A | N/A
WMP 2019 | SDG&E | D.19-05-039 | Order | Link | 29 | N/A | 3. San Diego Gas & Electric Company shall continue to assess the best materials to use for poles in High Fire-Threat District areas, and in future Wildfire Mitigation Plans shall document that its selections for pole replacements are reasonable and consider ingress and egress impacts as part of the decision | See Description | N/A | N/A | N/A | SDG&E 2020 WMP - Revised (Ex SDG&E-T2-01R-A) | Link | 75 | Yes | N/A | N/A | N/A
WMP 2019 | SDG&E | D.19-05-039 | Order | Link | 29 | N/A | 4. San Diego Gas & Electric Company shall work with manufacturers to accelerate the production of new poles and covered conductors and conduct quality control on the production of this equipment. | See Description | N/A | N/A | N/A | SDG&E 2020 WMP - Revised (Ex SDG&E-T2-01R-A) | Link | 75 | Yes | N/A | N/A | N/A
WMP 2019 | SDG&E | D.19-05-039 | Order | Link | 30 | N/A | 5. San Diego Gas & Electric Company may implement a 25-foot post-trim clearance where necessary and feasible if such a practice is supported by scientific evidence or other data showing that such clearance will reduce risk under wildfire conditions. | See Description | N/A | N/A | N/A | SDG&E 2020 WMP - Revised (Ex SDG&E-T2-01R-A) | Link | 122 | Yes | N/A | N/A | N/A
WMP 2019 | SDG&E | D.19-05-039 | Order | Link | 30 | N/A | 6. In San Diego Gas & Electric Company’s next Wildfire Mitigation Plan, it shall propose detailed guidelines for where a 25-foot post-trim clearance for vegetation management is both feasible and necessary. | See Description | N/A | N/A | N/A | SDG&E 2020 WMP - Revised (Ex SDG&E-T2-01R-A) | Link | 122 | Yes | N/A | N/A | N/A
WMP 2019 | SDG&E | D.19-05-039 | Order | Link | 30 | N/A | 7. Prior to implementing a generator grant program, San Diego Gas & Electric Company shall consider technologies other than fossil generation that could provide benefits with safer and cleaner operation. | See Description | N/A | N/A | N/A | SDG&E 2020 WMP - Revised (Ex SDG&E-T2-01R-A) | Link | 77, 82-84 | Yes | N/A | N/A | N/A
WMP 2019 | SDG&E | D.19-05-039 | Order | Link | 30 | N/A | 8. The metrics portion of San Diego Gas & Electric Company’s future Wildfire Mitigation Plans shall be focused on outcomes, measuring the effectiveness by which the mitigation implemented reduces the risk of its electrical lines and equipment causing a catastrophic wildfire. | See Description | N/A | N/A | N/A | SDG&E 2020 WMP - Revised (Ex SDG&E-T2-01R-A) | Link | 43 | Yes | N/A | N/A | N/A
WMP 2019 | SDG&E | D.19-05-039 | Order | Link | 31 | N/A | 12. San Diego Gas & Electric’s 2020 Wildfire Mitigation Plan shall use the quantitative risk assessment framework adopted in Decision 18-12-014 in the Safety Model Assessment Proceeding to evaluate and compare the cost effectiveness of each of the mitigations that were under consideration in developing the Wildfire Mitigation Plan. The Wildfire Mitigation Plan shall provide the risk spend efficiency results of the quantitative risk analysis and include an explanation of the Multi-Attribute Variable Framework used and how it was constructed | See Description | N/A | N/A | N/A | SDG&E 2020 WMP - Revised (Ex SDG&E-T2-01R-A) | Link | p. 18 | Yes | Resolution WSD-005 ratifying WSD approval of SDG&E's 2020 WMP | Link | 23-24
WMP 2020 | All IOUs | WSD Guidance Resolution 002 on 2020 WMPs Per PUC Sec 8386 (Appendix A) | Class B | Link | A1 | Guidance 1 – Lack of RSE Information WMPs contain sparse and sporadic detail regarding RSEs of WMP initiatives | Insufficient • Does not calculate a separate ignition or wildfire consequence risk values, instead providing a percentage reduction for either one or the other. • States some initiatives are still grouped together but does not provide an explanation for each instance in which this occurs. • The actual consequences of PSPS that SDG&E is planning to take into account are not provided. | In its first quarterly report, each electrical corporation shall provide the following: i - its calculated reduction in ignition risk for each initiative in its 2020 WMP; ii - its calculated reduction in wildfire consequence risk for each initiative in its 2020 WMP and the risk models used to calculate (i) and (ii) | SDG&E Q3 2020 Report on 2020 WMP (Ex SDG&E-T2-ALJ-01) | Link | 5-18 | SDG&E Supplemental Filing Addressing 2020 WMP Qtr Insufficiencies (Ex SDG&E-T2-ALJ-03) | Link | 2-16 | Yes | Action Statement on SDG&E 2021 Wildfire Mitigation Plan Update (Appx. at p.4); See also OEIS Final Decision on SDG&E's WMP 2023 Update: ACI SDGE-23-06 (page A8). | Link | Appendix - 4
WMP 2020 | All IOUs | WSD-002, Appendix A | Class B | Link | A2 | Guidance 2 – Lack of alternatives analysis for chosen initiatives | 2020 WMP submissions contain little to no detail regarding utilities’ process for comparing potential WMP initiatives. While most WMP initiatives are generally assumed to reduce utility wildfire risk, there are typically several alternatives that can address specific drivers of utility ignitions and near misses. However, 2020 WMPs generally do not include any discussion of which alternatives were considered, how the utility evaluated the efficacy of each alternative, and how the utility ultimately decided upon the suite of initiatives presented in its 2020 WMP | In its first quarterly report, each electrical corporation shall provide the following: i. all alternatives considered for each grid hardening or vegetation management initiative in its 2020 WMP; ii. all tools, models, and other resources used to compare alternative initiatives; iii. how it quantified and determined the risk reduction benefits of each initiative; and iv. why it chose to implement each initiative over alternative options. | SDG&E Q3 2020 Report on 2020 WMP (Ex SDG&E-T2-ALJ-01) | Link | 19-26 | SDG&E 2021 WMP Action Statement Supplemental - Nov 1, 2021 at SDGE 21-09 (Ex SDG&E-T2-ALJ-04) | Link | 24 | Yes | SDG&E OEIS Final Decision on SDG&E’s WMP 2022 Update | Link | Appendix A - Page A2 & A3 (Table A-1)
WMP 2020 | All IOUs | WSD-002, Appendix A | Class A | Link | A3 | Condition Guidance-3: Lack of Risk Modeling to Inform Decision-making | • The information provided in the RCP lacks any depth of detail and does not provide sufficient insight or transparency regarding the nature of SDG&E’s Wildfire Next Generation System (WiNGS) risk model or how it applies to SDG&E’s decision-making regarding asset management, vegetation management, grid hardening, or Public Safety Power Shutoff (PSPS). • While WiNGS represents the “next generation” of SDG&E’s risk modeling approach, it provides no insight into the decision-making process that supported its selected portfolio of initiatives presented in SDG&E’s 2020 WMP. | Action SDGE-1: SDG&E shall provide a high-level description of its risk-informed decision-making approach used to select the portfolio of mitigation initiatives presented in its 2020 WMP. Action SDGE-2: SDG&E shall provide initiative-level details on the current and future approaches to its decision-making in selecting WMP initiatives, identifying where systematic and programmatic advancements are expected. These initiative-level details shall minimally include: 1) an identification the specific risk being mitigated or problem being addressed, 2) how the initiative or program was selected, 3) how prioritization or targeting is approached for each initiative or program, 4) future plans to improve risk modeling for the initiative or program, and 5) a timeline for the implementation and updating of risk modeling to support the decision-making for each initiative or program. At a minimum, these details shall be provided for every initiative associated with asset management, vegetation management, grid hardening, and PSPS identified in SDG&E’s 2020 WMP. Action SDGE-3: SDG&E shall provide a table describing its risk assessment techniques used for each initiative in the format used by SCE. | N/A | N/A | N/A | SDG&E 2020 WMP Remedial Compliance Plan (Ex SDG&E-T2-ALJ-02) | Link | 2-4 | Yes | Action Statement on SDG&E 2021 Wildfire Mitigation Plan Update | Link | Appendix - 5
WMP 2020 | All IOUs | WSD-002, Appendix A | Class B | Link | A4 | Guidance 4 – Lack of discussion on PSPS impacts | Across 2020 WMP submissions, utilities indicate goals of reducing the scope, frequency and duration of PSPS events but also indicate intentions of continuing to implement PSPS as a wildfire mitigation measure in the immediate future. Considering the rapid expansion of PSPS use as a wildfire mitigation measure, and the numerous hardships, inconveniences and hazards created by its vast implementation, it is concerning that 2020 WMPs provide no discussion of how the chosen portfolio of initiatives will allow the utility to achieve its goals for reducing PSPS impacts. Specifically, no 2020 WMPs discuss the relationship between various grid hardening, vegetation management, and asset management initiatives and the corresponding impacts on thresholds for initiating PSPS events. | In its first quarterly report, each electrical corporation shall detail whether and how each initiative in its WMP: i. affects its threshold values for initiating PSPS events; ii. is expected to reduce the frequency (i.e. number of events) of PSPS events; iii. is expected to reduce the scope (i.e. number of customers impacted) of PSPS events; iv. is expected to reduce the duration of PSPS events; and v. supports its directional vision for necessity of PSPS, as outlined in Section 4.4 of its WMP | SDG&E Q3 2020 Report on 2020 WMP (Ex SDG&E-T2-ALJ-01) | Link | 27-38 | SDG&E Supplemental Filing Addressing 2020 WMP Qtr Insufficiencies (Ex SDG&E-T2-ALJ-03) | Link | 29-37 | Yes | Action Statement on SDG&E 2021 Wildfire Mitigation Plan Update | Link | Appendix - 5
WMP 2020 | All IOUs | WSD-002, Appendix A | Class B | Link | A5 | Guidance 5 – Aggregation of initiatives into programs | In their 2020 WMP submissions, electrical corporations often combine various initiatives into broader programs and report cost, risk and other related data at the program level. This aggregation of initiatives and bundled reporting creates several issues. First, because cost data is typically reported across programs and not individual initiatives, it is not possible for the WSD to evaluate the efficacy of each initiative. Second, when initiatives are bundled and reported together as programs, it prevents the WSD from being able to assess which initiatives are effectively reducing utility wildfire risk. Consequently, this creates the challenge that ineffective elements of broad programs cannot be determined and future considerations of initiatives within programs can only be done collectively. | In its first quarterly report, each electrical corporation shall: i. break out its programs outlined in section 5.3 into individual initiatives; ii. report its spend on each individual initiative; iii. describe the effectiveness of each initiative at reducing ignition probability or wildfire consequence; iv. list all data and metrics used to evaluate effectiveness described in (iii), including the threshold values used to differentiate between effective and ineffective initiatives; and v. provide the information required for each initiative in section 5.3 of the Guidelines. | SDG&E Q3 2020 Report on 2020 WMP (Ex SDG&E-T2-ALJ-01) | Link | 39 | SDG&E Supplemental Filing Addressing 2020 WMP Qtr Insufficiencies (Ex SDG&E-T2-ALJ-03) | Link | 38 | Yes | Action Statement on SDG&E 2021 Wildfire Mitigation Plan Update | Link | Appendix - 5
WMP 2020 | All IOUs | WSD-002, Appendix A | Class B | Link | A6 | Guidance 6 – Failure to disaggregate WMP initiatives from standard operations | While WMPs are designed to outline and detail filer’s plans and initiatives for mitigating wildfire risk, many existing programs also provide wildfire risk reduction benefits. For example, General Order 165 requires annual patrol inspections and detailed inspections every five years for electrical infrastructure. These programs and initiatives are often referenced in 2020 WMPs as “supporting,” “routine,” “enabling,” “standard,” or “foundational” work. For these types of programs, in most cases, electrical corporations do not report cost or risk reduction data, as the work is considered part of their electric operations and it is indicated that this information is not tracked independently. Several electrical corporations state that their programs for inspecting and maintaining crossarms, poles, transformers, transmission towers and similar infrastructure, which also reduce wildfire risk, are embedded within standard maintenance programs litigated in GRCs. Consequently, it is difficult to determine whether and how these programs incrementally impact wildfire risk reduction or if related WMP initiatives are redundant and unnecessary. While utilities may not have historically considered the costs and effectiveness of such programs and initiatives, given that numerous WMP initiatives have apparent overlap or potential redundancy, it is imperative that utilities provide such data to validate the need for and effectiveness of additional programs. It is not clear how electrical corporations are tracking their WMP activities in memorandum accounts if they do not budget for them by type of initiative. The Commission will scrutinize electrical corporations’ memorandum accounts for WMP carefully, and if all costs are simply lumped together or included in general operations and maintenance accounts, electrical corporations risk failing to provide entitlement to cost recovery. | In its first quarterly report, each electrical corporation shall: i. clearly identify each initiative in Section 5.3 of its WMP as “Standard Operations” or “Augmented Wildfire Operations;” ii. report WMP required data for all Standard Operations and Augmented Wildfire Operations; iii. confirm that it is budgeting and accounting for WMP activity of each initiative; and iv. include a “ledger” of all subaccounts that show a breakdown by initiative. | N/A | N/A | N/A | SDG&E Q3 2020 Report on 2020 WMP (Ex SDG&E-T2-ALJ-01) | Link | 40-41 | Yes | Action Statement on SDG&E 2021 Wildfire Mitigation Plan Update | Link | Appendix - 5
WMP 2020 | All IOUs | WSD-002, Appendix A | Class B | Link | A7 | Guidance 7 – Lack of detail on effectiveness of “enhanced” inspection programs | Utilities engage in numerous ‘enhanced’ inspection programs, but it is unclear if such ‘enhanced’ programs are incrementally effective over routine patrol and detailed inspections, particularly if patrol and detail inspections are scheduled based on risk rather than GO 95 minimums. | In its first quarterly report, each electrical corporation shall detail: i. the incremental quantifiable risk identified by such ‘enhanced’ inspection programs; ii. whether it addresses the findings uncovered by ‘enhanced’ programs differently than findings discovered through existing inspections; and iii. a detailed cost-benefit analysis of combining elements of such ‘enhanced’ inspections into existing inspection programs. | SDG&E Q3 2020 Report on 2020 WMP (Ex SDG&E-T2-ALJ-01) | Link | 42-45 | SDG&E Supplemental Filing Addressing 2020 WMP Qtr Insufficiencies (Ex SDG&E-T2-ALJ-03) | Link | 39-41 | Yes | Action Statement on SDG&E 2021 Wildfire Mitigation Plan Update | Link | Appendix - 5
WMP 2020 | All IOUs | WSD-002, Appendix A | Class C | Link | A8 | Guidance 8 - (Class C) Prevalence of equivocating language – failure of commitment. | While there have been many improvements and advancements reflected in 2020 WMPs, a key concern remains regarding discussion of WMP objectives and the prevalent use of “equivocating language” to avoid making measurable, quantifiable, and verifiable commitments. While electrical corporations make promises to quantifiably reduce PSPS impacts and the frequency of near misses and ignitions, other promises are far less specific. Terms such as, “track,” “assess,” “evaluate,” and “evolve” are repeated hundreds of times throughout the 2020 WMPs. Without sufficient details, none of these terms provide the WSD or the public with a measurable, quantifiable, and verifiable goal against which electrical corporations could be held. | In its 2021 WMP update, each electrical corporation shall: i. include objectives for each of its initiatives that are measurable, quantifiable, and verifiable by the WSD; ii. provide targets and timelines for all strategies, plans, and approaches to wildfire mitigation that are measurable, quantifiable and verifiable by the WSD; and iii. dispense with empty rhetoric and not use terms that are ambiguous, misleading, or otherwise have the result of diluting commitments. Continued use of equivocating language may result in denial of future WMPs. | SDG&E 2020‐2022 WMP Update - 2021 (Ex SDG&E-T2-01R-B) | Link | 110,115 | SDG&E 2020‐2022 WMP Update - 2022 Update (Ex SDG&E-T2-01R-c) | Link | 144150 | Yes | OEIS Final Decision on SDG&E’s WMP 2022 Update | Link | 20-21
WMP 2020 | All IOUs | WSD-002, Appendix A | Class B | Link | A9 | Guidance 9 – Insufficient discussion of pilot programs | Electrical corporations do not describe how they will evaluate and expand the use of successfully piloted technology or which piloted technology has proven ineffective. To ensure pilots that are successful result in expansion, if warranted and justified with quantitative data, electrical corporations must evaluate each pilot or demonstration and describe how it will expand use of successful pilots. | In its quarterly report, each electrical corporation shall detail: i. all pilot programs or demonstrations identified in its WMP; ii. status of the pilot, including where pilots have been initiated and whether the pilot is progressing toward broader adoption; iii. results of the pilot, including quantitative performance metrics and quantitative risk reduction benefits; and ii.iv. how the electrical corporation remedies ignitions or faults revealed during the pilot on a schedule that promptly mitigates the risk of such ignition or fault, and incorporates such mitigation into its operational practices; and iv.v. a proposal for how to expand use of the technology if it reduces ignition risk materially. | SDG&E Q3 2020 Report on 2020 WMP (Ex SDG&E-T2-ALJ-01) | Link | 46-54 | SDG&E Supplemental Filing Addressing 2020 WMP Qtr Insufficiencies (Ex SDG&E-T2-ALJ-03) | Link | 42-47 | Yes | Action Statement on SDG&E 2021 Wildfire Mitigation Plan Update | Link | Appendix - 6
WMP 2020 | All IOUs | WSD-002, Appendix A | Class B | Link | A10 | Guidance 10 – Data issues general | Although the availability of data, including GIS data, provides unprecedented insight into utility infrastructure and operations, inconsistencies and gaps in the data present a number of challenges and hurdles. As it relates to GIS data, electrical corporation submissions often had inconsistent file formats and naming conventions, contained little to no metadata, were incomplete or missing many data attributes and utilized varying schema. These deficiencies rendered cross-utility comparisons impossible without substantive, resource- and timeconsuming manipulation of the data. Additional data challenges included varying interpretations of WMP Guideline data requirements, leading to inconsistency of data submitted. | Electrical corporations shall ensure that all future data submissions to the WSD adhere to the forthcoming data taxonomy and schema currently being developed by the WSD. Additionally, each electrical corporation shall file a quarterly report detailing: i. locations where grid hardening, vegetation management, and asset inspections were completed over the prior reporting period, clearly identifying each initiative and supported with GIS data, ii. the type of hardening, vegetation management and asset inspection work done, and the number of circuit miles covered, supported with GIS data iii. the analysis that led it to target that specific area and hardening, vegetation management or asset inspection initiative, and iv. hardening, vegetation management, and asset inspection work scheduled for the following reporting period, with the detail in (i) – (iii). | SDG&E Q3 2020 Report on 2020 WMP (Ex SDG&E-T2-ALJ-01) | Link | 55-56 | SDG&E Q3 2020 Report on 2020 WMP (Ex SDG&E-T2-ALJ-01) | Link | 55-56 | Yes | Action Statement on SDG&E 2021 Wildfire Mitigation Plan Update | Link | Appendix - 6
WMP 2020 | All IOUs | WSD-002, Appendix A | Class B | Link | A11 | Guidance 11 – Lack of detail on plans to address personnel | Electrical corporations do not explain in detail the range of activities that they are undertakingto recruit and train personnel to grow the overall pool of talent in areas of personnel shortage. | In its first quarterly report, each electrical corporation shall detail: i. a listing and description of its programs for recruitment and training of personnel, including for vegetation management; ii. a description of its strategy for direct recruiting and indirect recruiting via contractors and subcontractors; and iii. its metrics to track the effectiveness of its recruiting programs, including metrics to track the percentage of recruits that are newly trained, percentage from out of state, and the percentage that were working for another California utility immediately prior to being hired | SDG&E Q3 2020 Report on 2020 WMP (Ex SDG&E-T2-ALJ-01) | Link | 57-60 | SDG&E Supplemental Filing Addressing 2020 WMP Qtr Insufficiencies (Ex SDG&E-T2-ALJ-03) | Link | 48 | Yes | Action Statement on SDG&E 2021 Wildfire Mitigation Plan Update | Link | Appendix - 7
WMP 2020 | All IOUs | WSD-002, Appendix A | Class B | Link | A12 | Guidance 12 – Lack of detail of long-term planning | Electrical corporations do not provide sufficient detail regarding long-term wildfire mitigation plans and how the initiatives in their WMPs align with and support those long-term plans. | In their first quarterly report, each electrical corporations shall detail: i. its expected state of wildfire mitigation in 10 years, including 1) a description of wildfire mitigation capabilities in 10 years, 2) a description of its grid architecture, lines, and equipment; ii. a year-by-year timeline for reaching these goals; iii. a list of activities that will be required to achieve this end goal; and iv. a description of how the electrical corporation’s three -year WMP is a step on the way to this 10-year goal. | SDG&E Q3 2020 Report on 2020 WMP (Ex SDG&E-T2-ALJ-01) | Link | 61-95 | SDG&E Supplemental Filing Addressing 2020 WMP Qtr Insufficiencies (Ex SDG&E-T2-ALJ-03) | Link | 49-52 | Yes | Action Statement on SDG&E 2021 Wildfire Mitigation Plan Update | Link | Appendix - 7
WMP 2020 | SDG&E | WSD Resolution 005 Ratifying Action on SDG&E's 2020 WMP per PUC Sec 8386 (Appendix A) | Class B | Link | A1 | SDGE-1 – Higher number of ignitions related to balloon contact | Although SDG&E has relatively low volume of ignitions (annual average over five-year reporting period of 23, compared to 440 for PG&E and 106 for SCE), over the past five years, SDG&E reports a high percentage (18%) of ignitions related to balloon contact when normalized for overhead circuit miles. Compared to PG&E, SDG&E reports more than three times the rate of such balloon contact ignitions. However, SDG&E’s percentage of balloon contact ignitions as a fraction of total ignitions is similarto SCE's, which seems to indicate that this issue is more concentrated in southern California. Considering the fact that SDG&E has substantially less overhead circuitry, as compared to peer utilities, the higher incidence of balloon caused ignitions potentially correlates to an increased risk from this ignition driver in SDG&E's service territory. However, beyond some targeted covered conductor installation and undergrounding and covered conductor initiatives, SDG&E's WMP lacks detail on which initiatives it is implementing to reduce the risk of balloon contact ignitions. | In its first quarterly report, SDG&E shall: i. list and describe the actions it is taking to study the occurrence and potential consequence of metallic balloon caused ignitions in its service territory; ii. efforts it is taking to mitigate the occurrence of such ignitions in the future; iii. the status of the action and efforts identified in (i) and (ii) above, including timelines for completion; iv. the specific initiatives in its 2020 WMP that aim to reduce the risk of balloon caused ignitions; and v. its goals, targets and quantitative measures for evaluating effectiveness of the initiatives identified in (iv) at reducing the risk of balloon caused ignitions. | SDG&E Q3 2020 Report on 2020 WMP (Ex SDG&E-T2-ALJ-01) | Link | 96-103 | SDG&E Supplemental Filing Addressing 2020 WMP Qtr Insufficiencies (Ex SDG&E-T2-ALJ-03) | Link | 53 | Yes | Action Statement on SDG&E 2021 Wildfire Mitigation Plan Update | Link | Appendix - 1
WMP 2020 | SDG&E | WSD-005, Appendix A | Class B | Link | A2 | SDGE-2 – Higher number of ignitions related to vehicle contact | Although SDG&E has relatively low volume of ignitions (annual average over five-year reporting period of 23, compared to 440 for PG&E and 106 for SCE), over the past five years, SDG&E reports approximately twice the rate of ignitions related to vehicle contact compared to PG&E and SCE, when normalized for overhead circuit miles. Considering the fact that SDG&E has substantially less overhead circuitry, as compared to peer utilities, the higher incidence of vehicle contact ignitions potentially correlates to an increased risk from this ignition driver in SDG&E's service territory. However, beyond undergrounding, SDG&E's WMP lacks detail on which initiatives it is implementing to reduce the risk of vehicle contact ignitions. | In its first quarterly report, SDG&E shall: i. list and describe the actions it is taking to study the occurrence and potential consequence of vehicle contact caused ignitions in its service territory; ii. efforts it is taking to mitigate the occurrence of such ignitions in the future; iii. the status of the action and efforts identified in (i) and (ii) above, including timelines for completion; iv. the specific initiatives in its 2020 WMP that aim to reduce the risk of vehicle contact caused ignitions; and v. its goals, targets and quantitative measures for evaluating effectiveness of the initiatives identified in (iv) at reducing the risk of vehicle contact caused ignitions. | SDG&E Q3 2020 Report on 2020 WMP (Ex SDG&E-T2-ALJ-01) | Link | 104-107 | SDG&E Supplemental Filing Addressing 2020 WMP Qtr Insufficiencies (Ex SDG&E-T2-ALJ-03) | Link | 54-56 | Yes | Action Statement on SDG&E 2021 Wildfire Mitigation Plan Update | Link | Appendix - 1
WMP 2020 | SDG&E | WSD-005, Appendix A | Class B | Link | A3 | SDGE-3 – Incorporate lessons learned into updates of its risk models | In Section 5.3.1.1 of its WMP, SDG&E fails to explain how it plans to incorporate lessons learned into updates of its risk models. For instance, the model does not currently factor in spot fires or emergency resources | In its first quarterly report, SDG&E shall describe: i. how it plans to incorporate learnings into its risk models, including a specific timeline for implementation; ii. changes or updates to its risk models identified after 2020 WMP submission; and iii. the status of implementing the changes and updates identified in (ii) above, including the expected timeframe for completion. | SDG&E Q3 2020 Report on 2020 WMP (Ex SDG&E-T2-ALJ-01) | Link | 108-109 | SDG&E Supplemental Filing Addressing 2020 WMP Qtr Insufficiencies (Ex SDG&E-T2-ALJ-03) | Link | 57-59 | Yes | Action Statement on SDG&E 2021 Wildfire Mitigation Plan Update | Link | Appendix - 2
WMP 2020 | SDG&E | WSD-005, Appendix A | Class B | Link | A3 | SDGE-4 – Detail on strategic undergrounding pilots | In addressing its undergrounding efforts, SDG&E states it will determine a need to strategically underground lines through pilots that establish a baseline for project scope, cost and schedule, but does not provide sufficient detail on how it will report and share its findings. | In its first quarterly report, SDG&E shall: i. detail its plans to report and share the findings of its undergrounding pilotinitiatives; ii. outline what data it plans to collect and report for project scope, cost and schedule of these projects, and iii. explain how it intends to track and measure the effectiveness of these projects in comparisonto other WMP initiatives | SDG&E Q3 2020 Report on 2020 WMP (Ex SDG&E-T2-ALJ-01) | Link | 110-114 | SDG&E Supplemental Filing Addressing 2020 WMP Qtr Insufficiencies (Ex SDG&E-T2-ALJ-03); See also Ex. SDG&E-T2-13) | Link | 60-65 | Yes | Action Statement on SDG&E 2021 Wildfire Mitigation Plan Update; See also OEIS Approval of SDG&E 2023 WMP at ACI 23-6; OEIS Appoval of SDG&E 2025 WMP Update at 17-20. | Link | Appendix - 2
WMP 2020 | SDG&E | WSD-005, Appendix A | Class B | Link | A4 | SDGE-5 – Detail on need for regulatory assistance | SDG&E acknowledges potential easement and line extension barriers (from main road to house) related to undergrounding efforts, and requests regulatory assistance to alleviate barriers. However, SDG&E does not provide specific detail regarding the type of regulatory assistance needed, the required timeframe for such actions, or its plans for obtaining the needed assistance from regulators | In its first quarterly report, SDG&E shall: i. list and describe all regulatory barriers to implementation of its undergroundinginitiatives, ii. detail its proposals for specific regulatory changes needed to eliminate the barriers identified in (i) above; and iii. describe its efforts and actions over the past 3 years to collaborate with regulators and other entities responsible for implementing the regulatory changes identified in (ii) above, including status and expected timeline for implementation | SDG&E Q3 2020 Report on 2020 WMP (Ex SDG&E-T2-ALJ-01) | Link | 115 | SDG&E Supplemental Filing Addressing 2020 WMP Qtr Insufficiencies (Ex SDG&E-T2-ALJ-03) | Link | 115 | N/A - Resolved | Action Statement on SDG&E 2021 Wildfire Mitigation Plan Update | Link | Appendix - 2
WMP 2020 | SDG&E | WSD-005, Appendix A | Class B | Link | A5 | SDGE-6 – Detail on plans for reinforcing transmission lines | SDG&E’s WMP lacks sufficient detail to demonstrate the efficacy of its plans for reinforcing transmission lines – to have at least one hardened line into every transmission substation in the HFTD by 2020 and to harden 66 miles within a three-year period | In its first quarterly report, SDG&E shall: i. detail how it plans to measure and report the efficacy of its plans to reinforce transmission lines and, specifically, to have at least one hardened line into every transmission substation in the HFTD by 2020 and to harden 66 miles within the three-year plan period; ii. list and describe the specific actions and initiatives it plans to implement to achieve this plan for its transmission lines; and iii. the status and timeline for completion of all actions and initiatives identified in (ii)above. | SDG&E Q3 2020 Report on 2020 WMP (Ex SDG&E-T2-ALJ-01) | Link | 116-117 | SDG&E Supplemental Filing Addressing 2020 WMP Qtr Insufficiencies (Ex SDG&E-T2-ALJ-03) | Link | 66 | Yes | Action Statement on SDG&E 2021 Wildfire Mitigation Plan Update | Link | Appendix - 2
WMP 2020 | SDG&E | WSD-005, Appendix A | Class B | Link | A5 | SDGE-7 – Potential redundancies in VM activities | The scope and magnitude of its vegetation management activities raised concerns about potential redundancies. SDG&E seems to provide potentially redundant programs and measures, and greater evaluation of its “Master Schedule” as mentioned throughout Section 5.3.5 was needed. The Master Schedule, supplied in response to a WSD data request, only displays the schedule for routine vegetation inspections and work | In its first quarterly report, SDG&E shall: i. describe how it assesses its vegetation management processes to determine effectiveness; and ii. provide additional evaluation on how inspections overlap with one another both in timing and scope, including evaluation of effectiveness in terms of number and quality of findings per inspection. For example, if not many findings are being made, then SDG&E should provide an assessment of whether additional efforts are necessary. | SDG&E Q3 2020 Report on 2020 WMP (Ex SDG&E-T2-ALJ-01) | Link | 118-119 | SDG&E Supplemental Filing Addressing 2020 WMP Qtr Insufficiencies (Ex SDG&E-T2-ALJ-03) | Link | 67 | Yes | Action Statement on SDG&E 2021 Wildfire Mitigation Plan Update | Link | Appendix - 2
WMP 2020 | SDG&E | WSD-005, Appendix A | Class B | Link | A6 | SDGE-8 – Consideration of environmental impacts, local community input | SDG&E does not provide sufficient detail regarding how it measures and accounts for the potential environmental impacts related to its vegetation management work or how it incorporates input from local stakeholders in planning and executing its vegetation management work. | In its first quarterly report, SDG&E shall describe: i. how it measures and accounts for the potential environmental impacts related to its vegetation management work; and ii. how it incorporates input from local stakeholders in planning and executing its vegetation management work. | SDG&E Q3 2020 Report on 2020 WMP (Ex SDG&E-T2-ALJ-01) | Link | 120 | SDG&E 2020‐2022 WMP Update - 2021 (Ex SDG&E-T2-01R-B) | Link | 265 | Yes | OEIS Final Decision on SDG&E’s WMP 2022 Update | Link | 61
WMP 2020 | SDG&E | WSD-005, Appendix A | Class B | Link | A6 | SDGE-9 – Explain how investments in undergrounding reduce planned VM spend | SDG&E indicates in its WMP plans for significant investment in undergrounding. We anticipate that increased underground infrastructure will result in cost savings from reduced or eliminated need for vegetation management for underground infrastructure. However, SDG&E's WMP reports no changes in vegetation management costs over the plan period (i.e. 2020-2022) and lacks detail on how its planned investment in undergrounding initiatives correlates to cost savings in other initiatives, such as vegetation management. | In its first quarterly report, SDG&E shall describe: i. whether and how it takes ancillary cost savings into account when evaluating the effectiveness of undergrounding initiatives; and ii. how SDG&E plans to account for realized cost savings through a reduced need for certain vegetation management activities, resulting from its undergrounding investments. | SDG&E Q3 2020 Report on 2020 WMP (Ex SDG&E-T2-ALJ-01) | Link | 121 | SDG&E Supplemental Filing Addressing 2020 WMP Qtr Insufficiencies (Ex SDG&E-T2-ALJ-03) | Link | 70 | Yes | Action Statement on SDG&E 2021 Wildfire Mitigation Plan Update | Link | Appendix - 2
WMP 2020 | SDG&E | WSD-005, Appendix A | Class C | Link | A7 | SDGE-10(Class C) Use of outside entities for fuel reduction | SDG&E was asked to describe whether outside entities are conducting fuel reduction projects and how this work relates to the effectiveness of the overall vegetation management program. | In its annual update, SDG&E shall detail: i. whether fuel reduction projects via outside entities are being completed, and ii. how they tie into the overall vegetation management program in terms ofeffectiveness | N/A | N/A | N/A | SDG&E 2020‐2022 WMP Update - 2021 (Ex SDG&E-T2-01R-B) | Link | 267 | Yes | Action Statement on SDG&E 2021 Wildfire Mitigation Plan Update | Link | Appendix - 3
WMP 2020 | SDG&E | WSD-005, Appendix A | Class B | Link | A7 | SDGE-11 – Details on VM around substations | In Section 5.3.5, SDG&E's WMP lacks detail regarding its vegetation management efforts for substations beyond maintaining conductor clearance. | In its first quarterly report, SDG&E shall: i. describe how it plans fuels reduction work around its substations; and ii. whether and how it maintains defensible space around its substations. | N/A | N/A | N/A | SDG&E Q3 2020 Report on 2020 WMP (Ex SDG&E-T2-ALJ-01) | Link | 122 | Yes | Action Statement on SDG&E 2021 Wildfire Mitigation Plan Update | Link | Appendix - 3
WMP 2020 | SDG&E | WSD-005, Appendix A | Class B | Link | A8 | SDGE-12 – Details of quality assurance, quality control | SDG&E's WMP describes a quality assurance and quality control efforts designed to evaluate and ensure the effectiveness of its vegetation management and inspection activities. However, SDG&E's WMP lacks sufficient detail regarding how these quality assurance and quality control efforts measure and evaluate the effectiveness of vegetation management and inspection activities. | In its first quarterly report, SDG&E shall: i. describe the process and measures for how its quality assurance and quality control (QA/QC) efforts evaluate the effectiveness of vegetation management and inspection activities, ii. list and describe all QA/QC audits performed, the timing of the audits, and the quantitative results of such audits, and iii. list and describe all changes implemented as a result of QA/QC audit findings. | SDG&E Q3 2020 Report on 2020 WMP (Ex SDG&E-T2-ALJ-01) | Link | 123-124 | SDG&E 2020‐2022 WMP Update - 2021 (Ex SDG&E-T2-01R-B) | Link | 279 | Yes | OEIS Final Decision on SDG&E’s WMP 2022 Update | Link | Appendix A - Page A2 & A3 (Table A-1)
WMP 2020 | SDG&E | WSD-005, Appendix A | Class A | Link | A9 | SDGE-13: Lack of Risk Reduction or Other Supporting Data for Increased Time-of-Trim Clearances | • SDG&E’s research plan for a study of the effectiveness of extended vegetation clearances is incomplete and ineffective. • SDG&E provides minimal details on its methodology, and presents a rudimentary explanation of what data will be collected and how it will be compared, in contrast to submissions from other utilities. | o Action SDGE-4: SDG&E shall provide a detailed plan for how it intends to analyze and use extended vegetation clearance data, including specific statistical methods it expects to use, how it will control for environmental variables (e.g. wind, soil, elevation, and tree species), and how it will approach the collection and reporting of required data. o Action SDGE-5: SDG&E along with PG&E and SCE shall submit a joint, unified plan that reflects collaborative efforts and contains uniform definitions, methodology, timeline, data standards, and assumptions. | SDG&E 2020 WMP Remedial Compliance Plan (Ex SDG&E-T2-ALJ-02); See also Ex. SDG&E-T2-01R-B; Ex. SDG&E-T2-01R-C. | Link | 5 | SDG&E 2020‐2022 WMP Update - 2022 Update (Ex SDG&E-T2-01R-c) | Link | Detailed Progress Report on Key Areas of Improvement (7-11) | Yes | OEIS Final Decision on SDG&E’s WMP 2022 Update; Note: original deficiency folded into condition SDGE-21-04 | Link | Appendix A - Page A2 & A3 (Table A-1)
WMP 2020 | SDG&E | WSD-005, Appendix A | Class B | Link | A10 | SDGE-14 – Granularity of “at-risk species” Lacks detail to identify the tree species SDG&E considers “at risk” | SDG&E identifies five types of "at-risk" trees - eucalyptus, palm, oak, pine, and sycamore. However, SDG&E identifies these trees by their genus, and based on additional review, the WSD has discovered that not all tree species within a genus are considered "at-risk" trees. As such, SDG&E's WMP lacks sufficient detail to identify the tree species it considers "at-risk" and subject to its enhanced vegetation management programs. | In its first quarterly report, SDG&E shall detail the following: i. all tree species within the genera identified in its list of "at-risk"trees, ii. the measures, properties and characteristics it considers in identifying "at-risk" trees, and iii. the threshold values of the measures, properties and characteristics identified in (ii) above that result in a species being defined as "at-risk." | SDG&E Q3 2020 Report on 2020 WMP (Ex SDG&E-T2-ALJ-01); See also Ex. SDG&E-T2-01R-B, Ex. SDG&E-T2-01R-C. | Link | 129-132 | SDG&E 2020‐2022 WMP Update - 2022 Update (Ex SDG&E-T2-01R-c) | Link | Detailed Progress Report on Key Areas of Improvement (7-18) | Yes | OEIS Final Decision on SDG&E’s WMP 2022 Update; Note original deficiency folded into conditions SDGE-21-04 through SDGE-21-06 | Link | Appendix A - Page A2 & A3 (Table A-1)
WMP 2020 | SDG&E | WSD-005, Appendix A | Class B | Link | A10 | SDGE-15 – Details of centralized data repository | SDG&E indicates efforts to create a centralized data repository, however, its WMP lacks sufficient detail of the data to be included. | In its first quarterly report, SDG&E shall: i. list and describe all data it plans to provide in its centralized repository; ii. list and describe the sources and treatment of all data identified in (i) above; and iii. describe the frequency it plans to update all data identified in (i) above. | SDG&E Q3 2020 Report on 2020 WMP (Ex SDG&E-T2-ALJ-01) | Link | 133-134 | SDG&E Supplemental Filing Addressing 2020 WMP Qtr Insufficiencies (Ex SDG&E-T2-ALJ-03) | Link | 76-77 | Yes | Action Statement on SDG&E 2021 Wildfire Mitigation Plan Update | Link | Section 10 - Appendix - 4
WMP 2020 | SDG&E | WSD-005, Appendix A | Class B | Link | A11 | SDGE-16 – Details of cooperative fuel reduction work | A large portion of SDG&E’s HFTD area falls within federal lands. As such, it is imperative that SDG&E maintain close coordination and working relationships with the U.S. Forest Service (USFS), who is responsible for managing federal lands. SDG&E identifies specific ways in which it coordinates with the USFS, which appear sufficient for receiving permits for fuel reduction, but SDG&E does not address the resources needed to collaborate on fuel reductionefforts and establish formal agreements. | In its first quarterly report, SDG&E shall describe: i. whether it plans to collaborate with the USFS on fuel reduction programs in its service territory; ii. what programs or agreements, if any, it has in place with the USFS for fuel reduction programs; iii. the timeline for implementing initiatives identified in (i) and (ii); iv. how it plans to identify the resources needed to collaborate with the USFS on fuel reduction; and v. the status of reaching any formal agreements on fuel reduction efforts. | SDG&E Q3 2020 Report on 2020 WMP (Ex SDG&E-T2-ALJ-01) | Link | 135 | SDG&E Supplemental Filing Addressing 2020 WMP Qtr Insufficiencies (Ex SDG&E-T2-ALJ-03) | Link | 78 | Yes | Action Statement on SDG&E 2021 Wildfire Mitigation Plan Update | Link | Section 10 - Appendix - 4
WMP 2021 | All IOUs | WSD Resolution 019 Ratifying Action on SDG&E’s 2021 WMP Update Per PUC Sec 8386 (Appendix A) | Areas for improvement & remedies | Link | Section 6.3 | SDGE-21-01: Inadequate transparency in accounting for ignition sources in risk modelling and mitigation selection | SDG&E identifies vehicle contact and balloon contact as the first and second highest ignition risks but does not explain how that affects its risk models or mitigation selection. | SDG&E must fully explain: 1. How third-party ignition sources feed into SDG&E’s risk models; 2. How ignition sources impact 3. SDG&E’s mitigation selection process, including: a. How SDG&E prioritizes ignition sources; b. If SDG&E treats third-party ignition sources that are not under c. SDG&E’s direct control differently than other ignition sources, and if so, how d. How SDG&E targets its mitigations efforts to reduce ignitions that are more likely to result in catastrophic wildfire conditions. | N/A | N/A | N/A | SDG&E 2021 WMP Action Statement Supplemental - Nov 1 2021 (Ex SDG&E-T2-ALJ-04) | Link | 6 | Yes | OEIS Final Decision on SDG&E’s WMP 2022 Update | Link | Appendix A - Page A2 & A3 (Table A-1)
WMP 2021 | All IOUs | WSD-019, Appendix A | Areas for improvement & remedies | Link | Section 6.3 | SDGE-21-02: Lack of consistency in approach to wildfire risk modeling across utilities | The utilities do not have a consistent approach to wildfire risk modeling. For example, in their wildfire risk models, utilities use different types of data, use their individual data sets in different ways, and use different third-party vendors. The WSD recognizes that the utilities have differing service territory characteristics, differing data availability, and are at different stages in developing their wildfire risk models. However, the utilities face similar enough circumstances that there should be some level of consistency in statewide approaches to wildfire risk modeling. | The utilities must collaborate through a working group facilitated by Energy Safety to develop a more consistent statewide approach to wildfire risk modeling. After the WSD completes its evaluation of all the utilities’ 2021 WMP Updates, it will provide additional detail on the specifics of this working group. A working group to address wildfire risk modeling will allow for: 1. Collaboration among the utilities; 2. Stakeholder and academic expert input; and 3. Increased transparency. | N/A | N/A | N/A | SDG&E 2021 WMP Action Statement Supplemental - Nov 1 2021 (Ex SDG&E-T2-ALJ-04) | Link | 7 | Yes | OEIS Final Decision on SDG&E’s WMP 2022 Update | Link | Appendix A - Page A2 & A3 (Table A-1)
WMP 2021 | All IOUs | WSD-019, Appendix A | Areas for improvement & remedies | Link | Section 6.3 | SDGE-21-03: Limited evidence to support the effectiveness of covered conductor | The rationale to support the selection of covered conductor as a preferred initiative to mitigate wildfire risk lacks consistency among the utilities, leading some utilities to potentially expedite covered conductor deployment without first demonstrating a full understanding of its long-term risk reduction and cost-effectiveness. The utilities’ current covered conductor pilot efforts are limited in scope and therefore fail to provide a full basis for understanding how covered conductor will perform in the field. Additionally, utilities justify covered conductor installation by alluding to reduced PSPS risk but fail to provide adequate comparison to other initiatives’ ability to reduce PSPS risk. | The utilities must coordinate to develop a consistent approach to evaluating the long-term risk reduction and cost-effectiveness of covered conductor deployment, including: 1. The effectiveness of covered conductor in the field in comparison to alternative initiatives. 2. How covered conductor installation compares to other initiatives in its potential to reduce PSPS risk. | N/A | N/A | N/A | SDG&E 2021 WMP Action Statement Supplemental - Nov 1 2021 (Ex SDG&E-T2-ALJ-04) | Link | 8-12 | Yes | OEIS Final Decision on SDG&E’s WMP 2022 Update | Link | Appendix A - Page A2 & A3 (Table A-1)
WMP 2021 | All IOUs | WSD-019, Appendix A | Areas for improvement & remedies | Link | Section 6.3 | SDGE-21-04: Inadequate joint plan to study the effectiveness of enhanced clearances | RCP Action-SDGE-4 (Class A) required SDG&E, PG&E, and SCE to “submit a joint, unified plan” to begin a study of the effectiveness of extended vegetation clearances. SDG&E submitted its plan to study the effectiveness of extended vegetation clearance as part of its 2021 WMP Update. SDG&E, PG&E, and SCE presented the “joint, unified” plan to the WSD on February 18, 2021. While it was apparent the three large utilities had discussed a unified approach, each utility presented differing analyses that would be performed to measure the effectiveness of enhanced clearances. This presentation’s content was not included in the February 26, 2021, “Supplemental Filing Addressing 2020 Wildfire Mitigation Plan Quarterly Report Insufficiencies.” The WSD acknowledges the complexity of this issue; any study performed assessing the effectiveness of enhanced clearances will take years of data collection and rigorous analysis. | SDG&E, PG&E, and SCE will participate in a multi-year vegetation clearance study. The WSD will confirm the details of this study in due course. The objectives of this study are to: 1. Establish uniform data collection standards. 2. Create a cross-utility database of tree-caused risk events (i.e., outages and ignitions caused by vegetation contact). 3. Incorporate biotic and abiotic factors into the determination of outage and ignition risk caused by vegetation contact. 4. Assess the effectiveness of enhanced clearances. n preparation for this study and the eventual analysis, SDG&E must collect the relevant data; the required data are currently defined by the WSD Geographic Information System (GIS Data Reporting Standard for California Electrical Corporations - V2). Table 2 below outlines the feature classes which the WSD believes will be most relevant to the study. Additional requirements related to this study may be included in the Action Statements for PG&E and SCE’s 2021 WMP Updates. The WSD will also be updating the GIS Reporting Standards in 2021, which may include additional data attributes for vegetation-related risk events. | N/A | N/A | N/A | SDG&E 2021 WMP Action Statement Supplemental - Nov 1 2021 (Ex SDG&E-T2-ALJ-04) | Link | 13-14 | Yes | OEIS Final Decision on SDG&E’s WMP 2022 Update | Link | Appendix A - Page A2 & A3 (Table A-1)
WMP 2021 | All IOUs | WSD-019, Appendix A | Areas for improvement & remedies | Link | Section 6.3 | SDGE-21-05: Incomplete identification of vegetation species and record keeping | SDG&E reports that it targets trees based on characteristics of the species. SDG&E targets “eucalyptus, palm, oak, pine, and sycamore.” However, these are not tree species, but tree genera. SDG&E needs to ensure proper identification of trees to the species level. | 1. Use scientific names in its reporting (as opposed to common names). This change will be reflected in the upcoming updates to the WSD GIS Reporting Standard. 2. Add genus and species designation input capabilities into its systems which track vegetation (e.g., vegetation inventory system and vegetation-caused outage reports). 3. If the tree’s species designation is unknown (i.e., if the inspector knows the tree as “Quercus” but is unsure whether the tree is, for example, Quercus kelloggii, Quercus lobata, or Quercus agrifolia), it must be recorded as such. Instead of simply “Quercus,” use “Quercus sp.” If referencing multiple species within a genus use “spp.” (e.g., Quercus spp.).32 4. Require its vegetation management (VM) and outage reporting personnel to use the unknown “sp.” designation only as a last resort by including this requirement in its standard operating protocols and training programs for such work. 5. Notwithstanding (4), identify the genus and species of a tree that has caused an outage33 or ignition34 in the Quarterly Data Reports (in these cases, an unknown “sp.” designation is not acceptable). 6. Teach tree species identification skills in its VM personnel training programs, both in initial and continuing education. 7. Where possible SDG&E must remedy any unknown species designations made in the field by the time SDG&E submits each Quarterly Data Report, by, for example, allowing inspectors to upload pictures of tree-identifying characteristics and having a qualified individual identify the species using the inspector’s report. | N/A | N/A | N/A | SDG&E 2021 WMP Action Statement Supplemental - Nov 1 2021 (Ex SDG&E-T2-ALJ-04) | Link | 15-16 | Yes | OEIS Final Decision on SDG&E’s WMP 2022 Update | Link | Appendix A - Page A2 & A3 (Table A-1)
WMP 2021 | SDG&E | WSD-019, Appendix A | Areas for improvement & remedies | Link | Section 6.3 | SDGE-21-06: Limited evidence of quantitative analysis to identify “at-risk” species | Mussey Grade Road Alliance (MGRA) analyzed SDG&E’s vegetation-caused outage data to determine the outages per 1000 trees per year by tree genus. MGRA found that palm, cypress, and century plant constituted the highest risk with >1 outage per 1000 trees per year. These data are inconsistent with SDG&E’s statement that it “targeted species identified as a higher risk due to growth potential, failure characteristics and relative outage frequency. These species include eucalyptus, sycamore, oak,pine, and palm.” Only palms are common to both lists. Additionally, QR Action-SDGE-46 (Class B), from Jan. 8, 2021, required SDG&E to “define quantitative threshold values […] for the criteria used to define a tree as ‘at-risk.’”SDG&E responded to this requirement stating, “evaluation is based more on qualitative factors rather than quantitative.” SDG&E must use quantitative data to inform its “at-risk” species targeting; qualitative evaluation of a tree’s risk does not adequately address the quantitative risk of ignition or outage. | In Section 7.3.5.15 (or equivalent) of its 2022 WMP Update, SDG&E must: 1. Describe its methodologies for determining what species it considers “at-risk.” 2. Explain in complete detail why discrepancies exist between the genera with the highest number of outages per 1000 trees per year and SDG&E’s “targeted species identified as a higher risk due to growth potential, failure characteristics and relative outage frequency.” 3. Define quantitative threshold values (whether a standard value, a range of values, or an example of a typical value) for the criteria used to define a tree as “at-risk.” | N/A | N/A | N/A | SDG&E 2021 WMP Action Statement Supplemental - Nov 1 2021 (Ex SDG&E-T2-ALJ-04) | Link | 17-20 | Yes | OEIS Final Decision on SDG&E’s WMP 2022 Update | Link | Appendix A - Page A2 & A3 (Table A-1)
WMP 2021 | All IOUs | WSD-019, Appendix A | Areas for improvement & remedies | Link | Section 6.3 | SDGE-21-07: Need for quantified vegetation management (VM) compliance targets | In Table 12, SDG&E only defines quantitative targets for four of 20 VM initiatives. The WSD is statutorily required to audit SDG&E when a “substantial portion” of SDG&E’s VM work is complete; without quantifiable targets in the WMP and subsequent reporting on those targets in the Quarterly Data Report (QDR) and Quarterly Initiative Update (QIU), the WSD cannot fully realize its statutory obligations. | SDG&E must define quantitative targets for all VM initiatives in Table 12. If quantitative targets are not applicable to an initiative, SDG&E must fully justify this, define goals within that initiative, and include a timeline in which it expects to achieve those goals. | N/A | N/A | N/A | SDG&E 2021 WMP Action Statement Supplemental - Nov 1 2021 (Ex SDG&E-T2-ALJ-04) | Link | 21-22 | Yes | OEIS Final Decision on SDG&E’s WMP 2022 Update | Link | Appendix A - Page A2 & A3 (Table A-1)
WMP 2021 | SDG&E | WSD-019, Appendix A | Areas for improvement & remedies | Link | Section 6.3 | SDGE-21-08: Non-communicative remote-controlled switches | SDG&E experienced several incidents in which non-communicative Supervisory Control and Data Acquisition (SCADA) switches caused customers to be de-energized without notice. SDG&E indicates that it has no plans to alter its existing practices to ensure this issue does not continue in the future. In its WMP Update, SDG&E does not discuss any plans to take system-level proactive steps to validate that existing SCADA switches remain fully functional or to ensure that newly installed SCADA switches are fully functional. | 1. Discuss its plans to take systemlevel proactive steps to validate that existing SCADA switches remain fully functional. 2. Discuss its plans to ensure that newly installed SCADA switches are fully functional. 3. Describe the steps it is taking to increase and improve inspectionsand testing of SCADA switches. | N/A | N/A | N/A | SDG&E 2021 WMP Action Statement Supplemental - Nov 1 2021 (Ex SDG&E-T2-ALJ-04) | Link | 23 | Yes | OEIS Final Decision on SDG&E’s WMP 2022 Update | Link | Appendix A - Page A2 & A3 (Table A-1)
WMP 2021 | SDG&E | WSD-019, Appendix A | Areas for improvement & remedies | Link | Section 6.3 | SDGE-21-09: Inadequate transparency associated with SDG&E’s decision-making process | SDG&E does not clearly explain its initiative selection process or how RSE estimates impact the process. For example, SDG&E does not quantitively justify the selection of undergrounding compared to other mitigation alternatives. RSE estimates provide a quantitative pathway to assess the relative risk reductionbenefit provided by mitigation initiatives and inform the initiative selection process. | 1. Elaborate on its decision-making process to include a thorough overview of its initiative selection procedure. The overview must show the rankings of the relative decision-making factors (e.g., planning and execution lead times, resource constraints, etc.) and pinpoint where quantifiable risk reductions and RSE estimates are considered in the initiative selection process. The WSD recommends a cascading, dynamic “if-then” style flowchart to effectively demonstrate this prioritization process and satisfy this requirement. 2. Using the newly developed decision-making overview, demonstrate that its undergrounding projects are a reasonable and effective use of resources to achieve risk reduction compared to other mitigation alternatives. | N/A | N/A | N/A | SDG&E 2021 WMP Action Statement Supplemental - Nov 1 2021 (Ex SDG&E-T2-ALJ-04) | Link | 24 | Yes | OEIS Final Decision on SDG&E’s WMP 2022 Update | Link | Appendix A - Page A2 & A3 (Table A-1)
WMP 2021 | SDG&E | WSD-019, Appendix A | Areas for improvement & remedies | Link | Section 6.3 | SDGE-21-10: Insufficient detail regarding prioritization of HFTD in undergrounding and covered conductor mitigation efforts | Stakeholders expressed concerns that SDG&E is not adequately targeting its covered conductor installations and undergrounding efforts to high-risk circuits in its HFTD areas.46 It can be more cost-effective to bundle projects in proximate geographic areas47 than to perform mitigation initiatives strictly from the highest priority circuit segment to the lowest. Additionally, a strictly hierarchical strategy would not necessarily reduce PSPS events in the near term. It is therefore theoretically possible that a strategy of directing 100% of mitigation efforts to HFTD areas may not be the most reasonable and cost-effective strategy for reducing wildfire risk and PSPS events. However, SDG&E does not provide sufficient detail regarding its strategy for determining workflow to fully assess SDG&E is sufficiently prioritizing HFTD areas in its undergrounding and covered conductor mitigation efforts. SDG&E must effectively demonstrate that its mitigation efforts are focused on efficiently reducing wildfire risk and PSPS events. | SDG&E must fully demonstrate that its undergrounding and covered conductor mitigation efforts are focused on efficiently reducing wildfire risk and PSPS events, including a description of how SDG&E determines the order in which circuit segments are scheduled for mitigation. | N/A | N/A | N/A | SDG&E 2021 WMP Action Statement Supplemental - Nov 1 2021 (Ex SDG&E-T2-ALJ-04) | Link | 25 | Yes | OEIS Final Decision on SDG&E’s WMP 2022 Update | Link | Appendix A - Page A2 & A3 (Table A-1)
WMP 2021 | All IOUs | WSD-019, Appendix A | Areas for improvement & remedies | Link | Section 6.3 | SDGE-21-11: RSE values vary across utilities | The WSD is concerned by the stark variances in RSE estimates, sometimes on several orders of magnitude, for the same initiatives calculated by different utilities. For example, PGE’s RSE for covered conductor installation was 4.08,48 SDGE’s RSE was 76.73,49 and SCE’s RSE was 4,192.50 These drastic differences reveal that there are significant discrepancies between the utilities’ inputs and assumptions, which further support the need for exploration and alignment of these calculations. | The utilities51 must collaborate through a working group facilitated by Energy Safety52 to develop a more standardized approach to the inputs and assumptions used for RSE calculations. After the WSD completes its evaluation of the 2021 WMP Updates, it will provide additional detail on the specifics of this working group. | N/A | N/A | N/A | SDG&E 2021 WMP Action Statement Supplemental - Nov 1 2021 (Ex SDG&E-T2-ALJ-04) | Link | 26 | Yes | OEIS Final Decision on SDG&E’s WMP 2022 Update | Link | Appendix A - Page A2 & A3 (Table A-1)
WMP 2022 | All IOUs | OEIS Final Decision on SDG&E’s WMP 2022 Update | Areas for Continued Improvement & Required Progress | Link | 108 | SDGE-22-01. Prioritized List of Wildfire Risks and Drivers | SDG&E’s prioritized list of wildfire risks and drivers (2022 WMP Update Table 4-6) weighs the risk drivers by average outage multiplied by ignition rate; it does not account for the likelihood of the ignition to cause a catastrophic wildfire. | SDG&E must further refine its prioritized list of wildfire risks and drivers. It must do so by weighting each risk driver by likelihood of causing a catastrophic wildfire (e.g., does this ignition tend to happen in high wildfire risk areas identified by SDG&E’s risk models, including the HFTD). | N/A | N/A | N/A | SDG&E 2023-2025 WMP - October 2023 (Ex SDG&E-T2-ALJ-05) | Link | Appendix D - 1-2 | Yes | Resolution SPD-16 Ratifying Action of OEIS on SDG&E’s 2023-2025 WMP Per PUC 8386 | Link | Appendix B - A10
WMP 2022 | All IOUs | OEIS Final Decision on SDG&E’s WMP 2022 Update | Areas for Continued Improvement & Required Progress | Link | 108 | SDGE-22-02. Collaboration and Research in Best Practices in Relation to Climate Change Impacts and Wildfire Risk and Consequence Modeling. | SDG&E and the other large IOUs are currently pursuing their own efforts at integrating the potential impacts of climate change in their risk and consequence modeling. They are not actively collaborating with each other on these efforts nor taking advantage of the existing climate change modeling expertise of state agencies and academic institutions | SDG&E must participate in an Energy Safety-led scoping meeting to discuss how utilities can best learn from each other, external agencies, and outside experts. | N/A | N/A | N/A | SDG&E 2023-2025 WMP - October 2023 (Ex SDG&E-T2-ALJ-05) | Link | Appendix D - 3 | Yes | SPD-016 | Link | Appendix B - A10
WMP 2022 | SDG&E | OEIS Final Decision on SDG&E’s WMP 2022 Update | Areas for Continued Improvement & Required Progress | Link | 109 | SDGE-22-03. Utility Arborist Training Initiatives. | SDG&E does not provide details on the scope of Utility Arborist training initiatives it is developing or supporting. | SDG&E must provide more details on utility vegetation management workforce training initiatives it is developing and/or supporting. Details to include are as follows: 1. The number of people entering classes using the Utility Arborist Trainee curriculum at California community colleges and/or other training programs developed and/or supported by SDG&E. 2. The number completing the classes or other training programs. 3. The number of those completing the classes or other training programs subsequently joining the utility vegetation management workforce. 4. Any additional details on how SDG&E is addressing utility vegetation management labor constraints. | N/A | N/A | N/A | SDG&E 2023-2025 WMP - October 2023 (Ex SDG&E-T2-ALJ-05) | Link | Appendix D - 4-5 | Yes | SPD-016 | Link | Appendix B - A10
WMP 2022 | All IOUs | OEIS Final Decision on SDG&E’s WMP 2022 Update | Areas for Continued Improvement & Required Progress | Link | 109 | SDGE-22-04. Inclusion of Community Vulnerability in Consequence Modeling. | SDG&E does not currently include the impacts of wildfire on communities, such as community vulnerability, within consequence modeling | SDG&E must participate in an Energy Safety-led scoping meeting to discuss how to best learn from each other, external agencies and outside experts | N/A | N/A | N/A | SDG&E 2023-2025 WMP - October 2023 (Ex SDG&E-T2-ALJ-05) | Link | Appendix D - 6 | Yes | SPD-016 | Link | Appendix B - A10
WMP 2022 | All IOUs | OEIS Final Decision on SDG&E’s WMP 2022 Update | Areas for Continued Improvement & Required Progress | Link | 110 | SDGE-22-05. Fire Suppression Considerations. | SDG&E’s fire spread modeling does not currently factor in fire suppression effects (e.g., fire department efforts). | SDG&E must work with other utilities to evaluate how to best account for, quantify, and model suppression effects on wildfire spread. Further guidance will be determined and covered during the risk model working group meetings established by Energy Safety’s 2021 WMP Action Statements. | N/A | N/A | N/A | SDG&E 2023-2025 WMP - October 2023 (Ex SDG&E-T2-ALJ-05) | Link | Appendix D - 7 | Yes | SPD-016 | Link | Appendix B - A10
WMP 2022 | All IOUs | OEIS Final Decision on SDG&E’s WMP 2022 Update | Areas for Continued Improvement & Required Progress | Link | 110 | SDGE-22-06. Eight-Hour Fire Spread Simulations. | SDG&E’s eight-hour fire spread simulations may be impacting the accuracy of its wildfire spread consequence modeling | 1. SDG&E must benchmark against other utilities to account for catastrophic fire risk that occurs more than eight hours post-ignition and provide a summary of lessons learned in its 2023 WMP. Further guidance may be determined and covered within the risk model working group established by the 2021 WMP Action Statements. 2. SDG&E must include a description of resulting changes to its wildfire spread consequence modeling or anticipated changes and a timeline for implementation. | N/A | N/A | N/A | SDG&E 2023-2025 WMP - October 2023 (Ex SDG&E-T2-ALJ-05) | Link | Appendix D - 8 | Yes | SPD-016 | Link | Appendix B - A10
WMP 2022 | SDG&E | OEIS Final Decision on SDG&E’s WMP 2022 Update | Areas for Continued Improvement & Required Progress | Link | 111 | SDGE-22-07. Risk Prioritization for Mitigation Measures. | SDG&E only calculated the cumulative top risk coverage estimates based on risk model output for covered conductor and undergrounding | SDG&E must provide an update on its progress using risk model output to inform its initiative plans based on highest risk areas, including determination of top risk percentages, for all initiatives, including covered conductor and undergrounding. | N/A | N/A | N/A | SDG&E 2023-2025 WMP - October 2023 (Ex SDG&E-T2-ALJ-05) | Link | Appendix D - 9 | Yes | OEIS Final Decision on SDG&E’s WMP 2025 Update (ACI SDGE-23-06) | Link | Appendix B - A8 to A10 (Table A-1)
WMP 2022 | SDG&E | OEIS Final Decision on SDG&E’s WMP 2022 Update | Areas for Continued Improvement & Required Progress | Link | 111 | SDGE-22-08. Evaluation of Wildfire Risk Outside of the HFTD. | SDG&E has yet to evaluate the potential need for adjustment of the HFTD. | • SDG&E must analyze its service territory to determine if there are additional higher wildfire risk areas outside of the HFTD boundaries and include in its 2023 WMP its findings and a description of the analysis performed, including factors considered, and include any territory newly classified by SDG&E as high risk within the treatment area for its mitigation initiatives. • If it identifies any new areas of higher wildfire risk, SDG&E must provide a process outlining the formal steps necessary to have those areas considered for recognition in the CPUC-defined HFTD | N/A | N/A | N/A | SDG&E 2023-2025 WMP - October 2023 (Ex SDG&E-T2-ALJ-05) | Link | Appendix D - 10 | Yes | SPD-016 | Link | Appendix B - A11
WMP 2022 | SDG&E | OEIS Final Decision on SDG&E’s WMP 2022 Update | Areas for Continued Improvement & Required Progress | Link | 111 | SDGE-22-09. Evaluation of Wind Gust Effects on Vegetation-Related Failures. | SDG&E does not currently account for wind gust effects within its vegetation probability of failure (PoF) model | 1. Provide a description of any analysis it has completed to evaluate the effects of wind gust effects on vegetation failures (including factors considered, weighing of various factors, and wind studies used) and provide a description of any additional analysis needed to evaluate wind gust effects on vegetation-related failures. 2. Provide an update on any changes made to its PoF model as a result of its analysis of wind gust effects on vegetation failures. 3. Provide a timeline for any future analyses on wind gust effects, as applicable, including reasoning for the need of future analysis, and cadence for performance of future analysis. 4. Provide a timeline for any future changes to its model related to wind gust effects | N/A | N/A | N/A | SDG&E 2023-2025 WMP - October 2023 (Ex SDG&E-T2-ALJ-05) | Link | Appendix D - 11-12 | Yes | SPD-016 | Link | Appendix B - A11
WMP 2022 | All IOUs | OEIS Final Decision on SDG&E’s WMP 2022 Update | Areas for Continued Improvement & Required Progress | Link | 112 | SDGE-22-10. Wildfire Consequence Modeling Improvements. | SDG&E does not use its wildfire consequence modeling as a tool to model potential ignitions in near real-time as faults/outages occur in the HFTD | SDG&E must discuss how it explored the use of its wildfire consequence modeling and/or developed processes to locate, prioritize, and respond to the locations of faults/outages in the HFTD as they happen. | N/A | N/A | N/A | SDG&E 2023-2025 WMP - October 2023 (Ex SDG&E-T2-ALJ-05) | Link | Appendix D - 13 | Yes | SPD-016 | Link | Appendix B - A11
WMP 2022 | All IOUs | OEIS Final Decision on SDG&E’s WMP 2022 Update | Areas for Continued Improvement & Required Progress | Link | 112 | SDGE-22-11. Applying Joint Lessons Learned Concerning Covered Conductor. | SDG&E has not yet provided goals and timelines for implementing lessons learned from the covered conductor effectiveness joint study. | Provide a concrete list of goals with planned dates of implementation for any lessons learned in the covered conductor effectiveness joint study. Provide a table indicating which WMP sections include changes (compared to its 2021 and 2022 Updates) as a result of the covered conductor effectiveness joint study. This should include, but not be limited to: a. Changes made to covered conductor effectiveness calculations. b. Changes made to initiative selection based on effectiveness and benchmarking across alternatives. c. Inclusion of rapid earth fault current limiter (REFCL), open phase detection (OPD), early fault detection (EFD), and distribution fault anticipation (DFA) as alternatives, including for PSPS considerations. d. Changes made to cost impacts and drivers. e. An update on data sharing across utilities on measured effectiveness of covered conductor in-field and pilot results, including collective evaluation. | N/A | N/A | N/A | SDG&E 2023-2025 WMP - October 2023 (Ex SDG&E-T2-ALJ-05) | Link | Appendix D - 14 | Yes | SPD-016 | Link | Appendix B - A11
WMP 2022 | All IOUs | OEIS Final Decision on SDG&E’s WMP 2022 Update | Areas for Continued Improvement & Required Progress | Link | 113 | SDGE-22-12. Covered Conductor Inspection and Maintenance. | SDG&E lacks specific directives for inspection procedures regarding covered conductor inspection and maintenance. | All electrical corporations (not including independent transmission operators) must work to share and determine best practices for inspecting and maintaining covered conductor, including either augmenting existing practices or developing new programs. This should be considered as a continuation of the covered conductor study established by Energy Safety’s 2021 WMP Action Statements. The study will continue to be utility-led, with the expectation for Energy Safety to be included as a participant. A report on progress on this continuation of the covered conductor effectiveness joint study will be expected in the 2023 WMPs. | N/A | N/A | N/A | SDG&E 2023-2025 WMP - October 2023 (Ex SDG&E-T2-ALJ-05) | Link | Appendix D - 15 | Yes | OEIS Decision Approving SDG&E's 2025 WMP Update (ACI SDGE-23-12) | Link | Appendix B - A8 to A10 (Table A-1)
WMP 2022 | All IOUs | OEIS Final Decision on SDG&E’s WMP 2022 Update | Areas for Continued Improvement & Required Progress | Link | 113 | SDGE-22-13. New Technologies Evaluation and Implementation. | SDG&E is not moving forward with its REFCL pilot and does not provide a plan for exploring new technologies that could increase effectiveness against ignition or wildfire risk. | All electrical corporations (not including independent transmission operators) must collaborate to evaluate the effectiveness of new technologies that support grid hardening and situational awareness such as REFCL and DFA/EFD, particularly in combination with other initiatives. Utilities must also share practices and evaluate implementation strategies for these new technologies. This should be considered as a continuation of the covered conductor effectiveness joint study established by Energy Safety’s 2021 WMP Action Statements. The scope of this study should now be expanded to cover grid hardening overall. The study will continue to be utility-led, with the expectation for Energy Safety to be included as a participant. A report on progress on this expansion of the covered conductor effectiveness joint study will be expected in the 2023 WMPs. | N/A | N/A | N/A | SDG&E 2023-2025 WMP - October 2023 (Ex SDG&E-T2-ALJ-05) | Link | Appendix D - 16 | Yes | OEIS Decision Approving SDG&E's 2025 WMP Update (ACI SDGE-23-09; SDGE-23-08 is ongoing) | Link | Appendix B - A8 to A10 (Table A-1)
WMP 2022 | SDG&E | OEIS Final Decision on SDG&E’s WMP 2022 Update | Areas for Continued Improvement & Required Progress | Link | 114 | SDGE-22-14. Grid Hardening Decision-Making Process Transparency. | SDG&E’s description of how it selects mitigation initiatives based on risk factors lacks detail, such as how its listed considerations affect initiative selection. | 1. A description of its analysis of how it selects mitigation initiatives based on risk factors evident in certain locations. This should include how SDG&E selects mitigation initiatives to optimize risk reduction for specific ignition risks. 2. Details on how each consideration listed in Figure 7-4 row 3 “Desktop Feasibility” in SDG&E’s 2022 Update is weighted, and how each consideration affects SDG&E’s initiative selection for grid hardening. | N/A | N/A | N/A | SDG&E 2023-2025 WMP - October 2023 (Ex SDG&E-T2-ALJ-05) | Link | Appendix D - 17-19 | Yes | OEIS Decision Approving SDG&E's 2025 WMP Update (ACI SDGE-23-06) | Link | Appendix B - A8 to A10 (Table A-1)
WMP 2022 | SDG&E | OEIS Final Decision on SDG&E’s WMP 2022 Update | Areas for Continued Improvement & Required Progress | Link | 114 | SDGE-22-15. Undergrounding Risk-Spend Efficiency Demonstration. | SDG&E plans on ramping up future undergrounding efforts without adequately demonstrating costeffectiveness based on specific ignition risks. | SDG&E must provide a description of its decision-making process demonstrating risk/cost benefit analysis as it pertains to future undergrounding installations. | N/A | N/A | N/A | SDG&E 2023-2025 WMP - October 2023 (Ex SDG&E-T2-ALJ-05) | Link | Appendix D - 20-21 | Yes | OEIS Decision Approving SDG&E's 2025 WMP Update ( ACI SDGE-23-06) | Link | Appendix B - A8 to A10 (Table A-1)
WMP 2022 | SDG&E | OEIS Final Decision on SDG&E’s WMP 2022 Update | Areas for Continued Improvement & Required Progress | Link | 115 | SDGE-22-16. Enabling Circuits with Advanced Protection. | SDG&E has not been meeting its targets for enabling circuits with advanced protection. | SDG&E must explain how it will meet its current and future targets for enabling circuits with advanced protection and provide a detailed description of that plan in its 2023 WMP. | N/A | N/A | N/A | SDG&E 2023-2025 WMP - October 2023 (Ex SDG&E-T2-ALJ-05) | Link | Appendix D - 22 | Yes | SPD-016 | Link | Appendix B - A12
WMP 2022 | SDG&E | OEIS Final Decision on SDG&E’s WMP 2022 Update | Areas for Continued Improvement & Required Progress | Link | 115 | SDGE-22-17. Further Development of Integrating Risk-Informed Decision Making for Inspection Scheduling and Planning | While SDG&E has some risk-informed prioritization for cyclical schedules (e.g., every three years) based on Tier 2 and Tier 3 designations, SDG&E has not yet implemented risk modeling-informed prioritization for its inspections | G&E must provide a concrete timeline detailing when SDG&E plans to implement risk modelinginformed prioritization for each of its inspection types. | N/A | N/A | N/A | SDG&E 2023-2025 WMP - October 2023 (Ex SDG&E-T2-ALJ-05) | Link | Appendix D - 23 | Yes | SPD-016 | Link | Appendix B - A12
WMP 2022 | SDG&E | OEIS Final Decision on SDG&E’s WMP 2022 Update | Areas for Continued Improvement & Required Progress | Link | 115 | SDGE-22-18. Evaluation and Interpretation of “Other” Equipment Failures. | Within Tables 7.1 and 7.2 (2022 Update), many of SDG&E’s equipment failures are grouped in a category defined as “other,” with some causes seemingly falling under other existing categories, or represented as “null.” | 1. A review of the categories that fall under “other” in order to ensure the categories accurately reflect the causes of equipment failures. 2. A clear justification for why causes are categorized as “other,” including an explanation for why “weather related” causes are listed as such. 3. A breakout of the events that fall under “other.” | N/A | N/A | N/A | SDG&E 2023-2025 WMP - October 2023 (Ex SDG&E-T2-ALJ-05) | Link | Appendix D - 24 | Yes | SPD-016 | Link | Appendix B - A12
WMP 2022 | SDG&E | OEIS Final Decision on SDG&E’s WMP 2022 Update | Areas for Continued Improvement & Required Progress | Link | 116 | SDGE-22-19. Plan to Address Missing Asset Data. | Less than one percent of SDG&E’s data on installation dates for older assets is missing, but SDG&E lacks a proactive plan to address the missing data | 1. Provide a plan, including a timeline, to obtain and address the missing installation dates within asset data. This includes developing a plan to determine missing installation dates and fill estimated installation dates into asset databases where possible. a. Include an explanation for instances where installation dates cannot be estimated. 2. Evaluate whether using installation dates would increase predictability within the PoI and evaluate any additional causes for limitations on data quality | N/A | N/A | N/A | SDG&E 2023-2025 WMP - October 2023 (Ex SDG&E-T2-ALJ-05) | Link | Appendix D - 25 | Yes | SPD-016 | Link | Appendix B - A12
WMP 2022 | All IOUs | OEIS Final Decision on SDG&E’s WMP 2022 Update | Areas for Continued Improvement & Required Progress | Link | 116 | SDGE-22-20. Progression of Effectiveness of Enhanced Clearances Joint Study. | The 2021 Action Statements required the large IOUs to conduct a study assessing the effectiveness of enhanced clearances. Progress has been made in the study; however, the study must continue to progress. | SDG&E, along with PG&E and SCE, must (1) standardize the data collection process for the cross-utility database of tree-caused risk events, (2) determine where and in what form the database will exist, (3) examine, to the best of their ability, whether the correlation between enhanced clearances and the lower number of tree-caused outage events may be attributable to other factors beyond clearances, such as the management of hazard trees and the installation of covered conductor. | N/A | N/A | N/A | SDG&E 2023-2025 WMP - October 2023 (Ex SDG&E-T2-ALJ-05) | Link | Appendix D - 26 | Yes | SPD-016 | Link | Appendix B - A12
WMP 2022 | SDG&E | OEIS Final Decision on SDG&E’s WMP 2022 Update | Areas for Continued Improvement & Required Progress | Link | 117 | SDGE-22-21. Consideration of Alternatives to Fuels Treatment Activity. | SDG&E’s practice of removing dead or dying fine fuels within a 50-foot radius of selected poles is not a long-term solution to this particular wildfire mitigation challenge | 1. SDG&E must present an analysis of alternatives to its fuels treatment activity including consideration of, but not limited to, undergrounding, REFCL, and pole replacement (e.g., with steel). SDG&E must provide a discussion of its progress in quantifying the additional risk reduction in its 2023 WMP. 2. SDG&E must quantify the additional risk reduction achieved by removing dead or dying fine fuels within a 50-foot radius as compared to the Public Resources Code Section 4292 standard | N/A | N/A | N/A | SDG&E 2023-2025 WMP - October 2023 (Ex SDG&E-T2-ALJ-05) | Link | Appendix D - 27 | Yes | SPD-016 | Link | Appendix B - A13
WMP 2022 | All IOUs | OEIS Final Decision on SDG&E’s WMP 2022 Update | Areas for Continued Improvement & Required Progress | Link | 117 | SDGE-22-22. Participation in Vegetation Management Best Management Practices Scoping Meeting. | Vegetation management processes and protocols for the reduction of wildfire risk are not uniform across electrical corporations. | SDG&E and all other electrical corporations (not including independent transmission operators) must participate in an Energy Safety-led scoping meeting to discuss how utilities can best learn from each other and future topics to explore regarding vegetation management best management practices for wildfire risk reduction. They must also participate in any follow-on activities to this meeting. This vegetation management best management practices scoping meeting may result in additional meetings or workshops or the formation of a working group. Energy Safety will provide additional details on the specifics of this scoping meeting in due course. | N/A | N/A | N/A | SDG&E 2023-2025 WMP - October 2023 (Ex SDG&E-T2-ALJ-05) | Link | Appendix D - 28 | Yes | SPD-016 | Link | Appendix B - A13
WMP 2022 | All IOUs | OEIS Final Decision on SDG&E’s WMP 2022 Update | Areas for Continued Improvement & Required Progress | Link | 117 | SDGE-22-23. PSPS Wind Threshold Change Evaluations | SDG&E has not yet evaluated PSPS threshold changes as a result of installing covered conductor. | 1. Coordinate with other utilities to understand the impacts of installing covered conductor and associated changes that could be made to PSPS thresholds as a result. 2. Provide a summary of key findings, including any changes implemented to SDG&E’s PSPS procedures or practices. 3. Provide any studies completed by third-parties on wind speed thresholds for covered conductor, or, if not yet completed, a timeline for completion. 4. Provide a description and associated justification of any modifications to PSPS wind speed thresholds since the 2022 Update. | N/A | N/A | N/A | SDG&E 2023-2025 WMP - October 2023 (Ex SDG&E-T2-ALJ-05) | Link | Appendix D - 29 | Yes | SPD-016 | Link | Appendix B - A13
WMP 2022 | SDG&E | OEIS Final Decision on SDG&E’s WMP 2022 Update | Areas for Continued Improvement & Required Progress | Link | 118 | SDGE-22-24. Replacing Protective Devices for Sensitivity Setting Capabilities. | SDG&E does not have a plan to proactively replace old field devices to include protective device sensitivity setting capabilities. | SDG&E must evaluate whether it should replace field devices with sensitivity setting capabilities. SDG&E must include in this evaluation a survey of existing coverage and determination of which areas could benefit from replacements. The evaluation should assess the extent to which replacements for increased sensitivity settings would reduce ignition risk. If SDG&E determines that field device replacement would decrease ignition risk, SDG&E must create and implement a plan to do so. If SDG&E determines that replacement of field devices would not effectively decrease ignition risk, SDG&E must explain why it would not. | SDG&E 2023-2025 WMP - October 2023 (Ex SDG&E-T2-ALJ-05) | Link | 30 | SDG&E 2025 WMP Update - July 2024 (Ex SDG&E-T2-ALJ-06) | Link | 101-102 | Yes | OEIS Decision Approving SDG&E's 2025 WMP Update (ACI SDGE-23-15) | Link | Appendix B - A8 to A10 (Table A-1)
WMP 2022 | SDG&E | OEIS Final Decision on SDG&E’s WMP 2022 Update | Areas for Continued Improvement & Required Progress | Link | 119 | SDGE-22-25. Validation of Vegetation Risk Index (VRI). | SDG&E states that it does not conduct any standard verification or validation on the Vegetation Risk Index (VRI) because “this is not a predictive model but rather a qualitative index.” Regardless of the nature of the index, if it is being used to drive decisions about PSPS as claimed, there should be evidence that there is in fact some relationship between the output and results (in this case, that the ratings of low/medium/high are correlated with increasing rates of vegetation-related outages) | 1. Evaluate the VRI output and report on the results of that effort. 2. Evaluate post-PSPS event data and compare to the VRI model to check for validity of output. 3. Adjust the model as needed based on lessons learned or provide a timeline and plan for associated adjustments. | N/A | N/A | N/A | SDG&E 2023-2025 WMP - October 2023 (Ex SDG&E-T2-ALJ-05) | Link | Appendix D - 31 | Yes | SPD-016 | Link | Appendix B - A13
WMP 2022 | SDG&E | OEIS Final Decision on SDG&E’s WMP 2022 Update | Areas for Continued Improvement & Required Progress | Link | 119 | SDGE-22-26. Validation of Wildfire Risk Reduction Model (WRRM). | SDG&E describes the validation of its WRRM as consisting only of visual verification by comparison using GIS software to determine that the results of the model “coincide with known conditions around the service territory.” As described in its 2022 Update Section 4.5.1.3, the WRRM incorporates 10 separate data elements, many of which could be validated in a more robust fashion to determine sources and magnitude of uncertainty in the model | SDG&E must determine which inputs to its WRRM can be more rigorously validated, conduct such validation, or provide a plan including a timeline to conduct such validation, and report on the results of that effort. | N/A | N/A | N/A | SDG&E 2023-2025 WMP - October 2023 (Ex SDG&E-T2-ALJ-05) | Link | Appendix D - 32 | Yes | SPD-016 | Link | Appendix B - A13
WMP 2022 | SDG&E | OEIS Final Decision on SDG&E’s WMP 2022 Update | Areas for Continued Improvement & Required Progress | Link | 119 | SDGE-22-27. Improvements to Capital Allocation Methodology. | SDG&E’s progress on the Maturity Survey for capability 41 under the Resource Allocation Methodology Section H.V “Portfolio-wide initiative allocation methodology” is limited by question H.V. that asks “to what extent does the utility allocate capital to initiatives based on [RSE]?” Based on SDG&E’s response to this question, the utility anticipates no progress on this question in 2022 | SDG&E must provide a timeline with attainable benchmarks for using accurate RSE estimates to determine capital allocation at a portfolio level | N/A | N/A | N/A | SDG&E 2023-2025 WMP - October 2023 (Ex SDG&E-T2-ALJ-05) | Link | Appendix D - 33 | Yes | SPD-016 | Link | Appendix B - A14
WMP 2022 | All IOUs | OEIS Final Decision on SDG&E’s WMP 2022 Update | Areas for Continued Improvement & Required Progress | Link | 120 | SDGE-22-28. Improvements to the RSE Verification Process. | SDG&E does not currently, nor does it plan to, verify its RSE estimates with independent experts or other utilities in California | SDG&E must provide a timeline with attainable benchmarks to verify its RSE estimates with independent experts or other utilities in California | SDG&E 2023-2025 WMP - October 2023 (Ex SDG&E-T2-ALJ-05) | Link | 34 | SDG&E 2025 WMP Update - July 2024 (Ex SDG&E-T2-ALJ-06) | Link | 45-50 | Yes | OEIS Decision Approving SDG&E's 2025 WMP Update (ACI SDGE-23-03) | Link | Appendix B - A8 to A10 (Table A-1)
WMP 2022 | SDG&E | OEIS Final Decision on SDG&E’s WMP 2022 Update | Areas for Continued Improvement & Required Progress | Link | 120 | SDGE-22-29. Mitigation Plan for Frequently De-Energized Circuits. | SDG&E does not go far enough in its plans to reduce the future risk of PSPS on its most frequently deenergized circuits, identified in Table 8.6-1 (2022 Update | SDG&E must demonstrate that it is planning to achieve a greater level of PSPS risk reduction on the frequently de-energized circuits identified in Table 8.6-1. This must include a greater percentage of risk reduction, a higher percentage of customers who will no longer be de-energized, and a greater percentage of circuit miles mitigated | N/A | N/A | N/A | SDG&E 2023-2025 WMP - October 2023 (Ex SDG&E-T2-ALJ-05) | Link | Appendix D - 35 | Yes | SPD-016 | Link | Appendix B - A14
WMP 2022 | SDG&E | OEIS Final Decision on SDG&E’s WMP 2022 Update | Areas for Continued Improvement & Required Progress | Link | 121 | SDGE-22-30. Improvements to the WiNGS-Ops and WiNGS-Planning Models. | SDG&E indicates it is planning enhancements to its WiNGS-Ops model in 2022. Additionally, SDG&E indicates that the WiNGS-Planning model does not include customers impacted by sectionalizing and resiliency programs | SDG&E must provide a progress report on the performance of WiNGS-Ops as used in its 2022 PSPS decision-making process, including successes, issues encountered, and lessons learned. 1. In particular, SDG&E must include in its report the progress it made prior to September 1, 2022, in incorporating WiNGS-Ops in the PSPS decision-making process. 2. SDG&E must also report any progress it made on incorporating PSPS risk reduction quantification to include customers impacted by sectionalizing and resiliency programs through the WiNGS-Planning model. | N/A | N/A | N/A | SDG&E 2025 WMP Update - July 2024 (Ex SDG&E-T2-ALJ-06) | Link | 65-84 | Ongoing | OEIS Decision Approving SDG&E's 2025 WMP Update; SDG&E must respond to this revised area for continued improvement in its 2026-2028 Base WMP | Link | Appendix B - A8 to A10 (Table A-1)

## To Do
1) Populate external links for Addresss in column (green) -Will/Kari - Complete
2) Add Page Numbers - Complete
3) Look at 'No' and add any relevant ACIs - Complete
4) Address 2019 16 Orders - Complete
5) Narrative along w/ the spreadsheet - Complete
6) Add to the Exhibit; documents missing - Will
7) Presentation of the materials - Will
8) Themes - Nisha/Lana - Complete
9) SDGE vs. IOUs - Nisha - Complete
10) Page # for approvals - Juan/Holly Complete
11)Deficiences noted by intervenors - Will Complete